## Lobby and Admin AHU Data Table
Project Name
Date | 2023-01-24
Altitude (ft) | 0
Barometric Pressure (in. Hg) | 29.9213
Atmospheric Pressure (psia) | 14.6959
Point Name | Airflow | Condition | Airflow UOM | Dry Bulb (°F) | Wet Bulb (°F) | Relative Humidity (%) | Humidity Ratio (gr/lb) | Humidity Ratio (lb/lb) | Specific Volume (cu.ft./lb) | Enthalpy (Btu/lb) | Dew Point (°F) | Density (lb/cu.ft.) | Vapor Pressure (in. Hg) | Absolute Humidity (gr/cu.ft.)
0.4% Cooling Design | 1000 | Standard | cfm | 90.3 | 67.6 | 30.5356 | 65.0601 | 0.0092943 | 14.0665 | 31.9059 | 55.18 | 0.071752 | 0.43878 | 4.6252
Space Condition | 1000 | Standard | cfm | 72 | 60.0747 | 50 | 58.6084 | 0.0083726 | 13.5786 | 26.431 | 52.37 | 0.074262 | 0.39589 | 4.3162
Return Air | 1000 | Standard | cfm | 75 | 61.1559 | 45.2014 | 58.6078 | 0.0083725 | 13.6553 | 27.1621 | 52.37 | 0.073845 | 0.39589 | 4.292
Cooling Coil EA | 2000 | Standard | cfm | 81 | 63.8 | 38.7023 | 61.2037 | 0.0087434 | 13.8166 | 29.0312 | 53.53 | 0.07301 | 0.41312 | 4.4297
Mixed Air | 1000 | Standard | cfm | 81.1261 | 63.8394 | 38.5343 | 61.1887 | 0.0087412 | 13.8198 | 29.0596 | 53.52 | 0.072993 | 0.41297 | 4.4276
Point Name | Process Name | Total Energy (tons) | Total Energy (Btu/hr) | Sensible Energy (Btu/hr) | Latent Energy (Btu/hr) | Sensible Heat Ratio | Moisture Difference (lb/hr) | Moisture Difference (gal/hr) | Start Point Name | Second Point Name
0.4% Cooling Design | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Space Condition | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Return Air | Connect States | 0.27408 | 3289 | 3290 | -1 | 1.0003 | -0.00036164 | -4.3331e-05 | Space Condition
Cooling Coil EA | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mixed Air | Air Mixing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.4% Cooling Design | Return Air