## Head Estimate
Item | Low End Head, ft.w.c. | High End Head, ft.w.c. | Lineal feet of pipe | Low end friction rate, ft.w.c. per 100 linear feet of pipe | High end friction rate, ft.w.c. per 100 linear feet of pipe
Pipe | 2.9388 | 6.32 | 158 | 1.86 | 4
Fittings | 1.4694 | 6.32
Chiller tube bundle | 10 | 10
| 14.4082 | 22.64
Design value | 40 | 40
Wasted head at design flow | 25.5918 | 17.36

## System Curve
Known point | 1100 | gpm | Known point | 1100 | gpm
| 40 | ft.w.c |  | 28 | ft.w.c
|  |  | Extra pressure drop at TDV - | 12
Flow Rate, gpm | Head, ft.w.c. |  | Flow Rate, gpm | Head, ft.w.c.
1400 | 64.7934 |  | 1400 | 45.3554
1200 | 47.6033 |  | 1200 | 33.3223
1100 | 40 | Given | 1100 | 28 | Given
800 | 21.157 |  | 800 | 14.8099
600 | 11.9008 |  | 600 | 8.3306
400 | 5.2893 |  | 400 | 3.7025
300 | 2.9752 |  | 300 | 2.0826
200 | 1.3223 |  | 200 | 0.92562
150 | 0.7438 |  | 150 | 0.52066
100 | 0.33058 |  | 100 | 0.2314
75 | 0.18595 |  | 75 | 0.13017
50 | 0.082645 |  | 50 | 0.057851
25 | 0.020661 |  | 25 | 0.014463
0 | 0 |  | 0 | 0
Projected Impeller Line
Wide Open Operating Point
System Curve Plotted from Square Law
Estimated Head Requirement at Design Flow; a.k.a. the Optimization Target
Design Point