## Scratch
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Docment dimensions and other parameters in the cells with the dark yellow highlight. Take photographs and make sketches to supplement the test data and document the physical configuration of the mixed air plenum. Document the system diagram for the plenum on the results tab in the graph paper area provided. Note that if you manipulate the text boxes and lines that are already there, the data on this tab will automatically fill in and follow them.
In the test matrix, nsert the filter height and width in inches into the blue boxes for all rows and columns. The area of each filter will be calculated in the indvidual filter elements and totaled below. Enter the velocity reading and temperature observed in the yellow area. The flow rate associated with each filter element and the flow times temperature parameter will be calculated. Average velocities, total flow, average temperature and mass weighted average temperature (the true average temperature from a conservation of mass and energy standpoint) are caculated where indicated below.
Note that you need to adjusted the number of rows and columns you actually use in your filter bank modely by adjusting the values in the purple highlighted cells tif you are interested in that information. For the other calculated values, as long as the input cells (blue and yellow boxes) for rows and columns with out filters are left blank, the result will be correct.
Note that you will need to click into a cell below the yellow area and arrow key up to enter data because the yellow is created with an autoshape overlayed on the cell to higlight it. I did that so that you could use the cell formating to higlight the filter elements that are being used for the particular unit you are working on and still have the data entry cells higlighted.
If you enter the average outdoor air temperature and return air temperature that existed during the test into the orange highlighted squares, the average outdoor air flow during the test will be calculated based on conservation of mass and energy.
100% Mixed air flow x Mixed air temperature = (Outdoor air % x Outdoor temperature) + ((100-Outdoor air %)x(Return temperature))
Solving for Outdoor Air %:
Outdoor air % = (MAT- RAT)/(OAT - RAT)
The equation used is included on the tab "Mixed Air Temp Callcs". The greater the difference between the outdoor and return temperatures, the more accurate the result. To understand this consider what would happen if both the outdoor air temperature and the return air temperaure were the same value.
Ideally, you should use the same temperature sensor for measureing the outdoor air temperature and return air temperature as you used for the filter face temperatures. But if you forget to take the other two temperatures, you may be able to get a reasonable estimate of the outdoor air flow by checking trends in the control system for return air temperatures at the time of your test or by making a reasonable assumption about the return temperature. For example, it would be reasonable to assume the return temperature was about the same as the typical space temperature in the facility.
For outdoor temperature, you may be able to find trend information in the control system. Or you could use historical data from a nearby weather station that can be found in sources like the National Weather Service or Weather Underground.
The EXAMPLE tabs contain the data and results used to assess a filter bank at Le Conte Annex on the UC Berkeley Campus.

## Instructions
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Developed by David Sellers, Senior Engineer, Facility Dynamics Engineering
Revision History
Rev. | Date |  | Revision
1 | 2018-02-05 20:34 |  | Origianal version of the spreadsheet, which was developed using my Filter Face Velocity spreadsheet as a starting point (basically, the grid on the "Test Data" tab.
Instructions
1 | This spreadsheet is intended to support performing a temperature and velocity traverse of a mixed air plenum. This process is typically used to:
| a | Identify hot and cold spots in a plenum which could lead to frozen coils or nuisance freezestat trips.
| b | Identify temperature patterns in a plenum to assist in the placement of the sensing elements for freezestats and averaging temperature sensors.
| c | Identify velocity and flow patterns in plenums to assess how the average temperature might differ from the true, mass weighted mixed air temperature.
| d | Identify how the temperature and flow patterns shift around as economizer dampers modulate, including the variations in flow that might occur with dampers in different positions.
2 | This spreadsheet could also be applied on the discharge side of coil bank to assess how uniformly flow is distributed through the coil by the piping manifold and coil arrrangement and circuiting.
3 | The spreadsheet uses the filter bank as a measurement grid and is configured for a filter bank that is 14 modules wide and 13 modules high. This module count has no particular significance other than being the size of the unit I was working on when I first started to develop this. If the modules were 24" x24" filters, that means the spreadsheet could support a unit that was in the range of 364,000 cfm.
If you are using it on a larger unit, you could either modify it to add rows (complicated in that you have to modify a bunch of formulas), use multiple forms to cover the plenum, or let each module represent something besides one filter, like every other filter.
Similarly, if you were using it on a coil face, you would have to use some other form of reverence to estsablish the grid. For instance you could mark of even incraments on the coil frame and then tape strings to the marks and run them across the coil to establish the grid. Or, you could "eyeball" things based on other indicators like the seperators between coils, bolts in the coil frame, etc.
Generally speaking, the results of your analysis will be better with more points, but the analysis will take longer since more points mean more data to capture. So, in the field, you need to make an informed decision about how many measurements you will take, perhaps based on some spot measurements.
4 | In terms of taking readings, I typically use my Omega Engineering 4-in-1 instrument (pictured to the right) in a mode that displays velocity from the rotating vane anemometer and temperature from the internal temperature sensor (upper picture). The rotating vane anemometer is the little propeller like part inside the circle. The internal temperature sensor (as well as a relative humidity sensor) is located behind the little grid to the lower left of the anemometer.
If you are interested in the Omega instrument, this link should take you to it.

## Side by Side Comparison
These are screen shots of the test results placed side by side to allow you to compare the results; If you "Paste Special" - "Linked Picture" they will update if you change something.

## Test 1 Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Mixing Plenum Test
Misc. Notes
| Test date - | [5 empty] | Date:
| Project/System Name - | [5 empty] | Project Name:
| Project Number - | [5 empty] | Project Number:
| Test engineer - | [5 empty] | Engineer:
Test start time -
Test end time -
| Average outdoor air temperature during the test - | [7 empty] | °F (Field measurement)
| Average return air teperature during the test - | [7 empty] | °F (Field measurement)
` | Outdoor Air Damper Information
| Target minimum outdoor air percentage - | [7 empty] | Estimate based on design AHU1 flow and related exhaust flow
Outdoor air damper number of sections -
Outdoor air damper number of actuators -
Outdoor air damper typical actuator make and model -
| Outdoor air damper over-all height - | [7 empty] | inches (estimate from drawings and photo)
| Outdoor air damper over-all width - | [7 empty] | inches (estimate from drawings and photo)
| Outdoor air damper nominal face area - | [6 empty] | 0 | sq.ft.
| Outdoor air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [7 empty] | blade | Blade rotation -
Outdoor air damper blade orientation -
Outdoor air damper blade angle during the test -
Outdoor air damper control signal during the test -
` | Return Air Damper Information
Return air damper number of sections -
Return air damper number of actuators -
Return air damper typical actuator make and model -
| Return air damper over-all height - | [7 empty] | inches (estimate from photo)
| Return air damper over-all width - | [7 empty] | inches (estimate from photo)
| Return air damper nominal face area - | [6 empty] | 0 | sq.ft.
| Return air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [7 empty] | blade | Blade rotation -
Return air damper blade orientation -
Return air damper blade angle during the test -
Return air damper control signal during the test -
| Total area for the filter bank (sum of individual element areas) - | [6 empty] | 0 | sq.ft.
| Total flow for the filter bank (sum of individual elements) - | [6 empty] | 0 | cfm
| Average velocity for the filter bank (average of individual elements) - | [6 empty] | #DIV/0! | fpm
| Number of rows used - | [7 empty] | (13 maximum)
| Number of colums use - | [7 empty] | (14 maximum)
| Average temperature (average of individual temperature readings) - | [6 empty] | #DIV/0! | °F
| Mass weighted average temperature (individual temperature readings times related flow divided by total flow) - | [6 empty] | #DIV/0! | °F
| Outdoor air % of mixed air flow during test based on temperatures - | [6 empty] | #DIV/0!
| Average outdoor air flow during the test based on temperatures - | [6 empty] | #DIV/0! | cfm
| Maximum temperature - | [6 empty] | 0 | °F
| Minimum temperature - | [6 empty] | 0 | °F
| Maximum velocity - | [6 empty] | 0 | fpm
| Minimum velocity - | [6 empty] | 0 | fpm
|  | Filter Column Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches
|  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0

## Test 1 Results
Test 1 | [6 empty] | Plenum Picture | Plenum System Diagram (with Test 1 results)
Test Date - | 0
Test Start Time - | 0:00 | [9 empty] | #DIV/0! |  | 0 Section, Square Foot, 0 0 Blade Return Air Damper
Test Finish Time - | 0:00
Outdoor air damper size - | 0 | sq.ft.
Outdoor air damper sections - | 0
Outdoor air damper type - | 0 0 |  |  | Blade
Outdoor air flow - | #DIV/0! | cfm
Outdoor air temperature - | 0 | °F
Outdoor air % of total - | #DIV/0! | (Design target is %)
Return air damper size - | 0 | sq.ft.
Return air damper sections - | 0
Return air damper type - | 0 0 |  |  | Blade | [8 empty] | Filter bank
Return air flow - | #DIV/0! | cfm | [6 empty] | #DIV/0!
Return air temperature - | 0 | °F
Total air flow - | 0 | cfm
Outdoor air damper velocity - | #DIV/0! | fpm ( at measured total flow an 100% OA)
Return air damper velocity - | #DIV/0! | fpm (at measured total flow on MOA)
Mixed air temperature - | #DIV/0! | °F (mass weighted; true mixed air temperature)
| #DIV/0! | °F (average if measurements)
Maximum temperature - | 0 | °F | [9 empty] | #DIV/0!
Minimum temperature - | 0 | °F
Maximum velocity - | 0 | fpm
Minimum velocity - | 0 | fpm
Link to additional photos - | ..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-07 | [8 empty] | 0 Section, Square Foot, 0 0 Blade Outdoor Air Damper
..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-11
Link to field notes - | LeConte Annex
Temperature Profile | Coldest |  | Hottest |  | Minimum | Maximum
Velocity Profile | Slowest |  | Fastest |  | Minimum | Maximum

## Mixed Air Temp Calcs
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2012-04-24 13:41
Project Name: | None
Project Number: | None
Engineer: | David Sellers
Assumptions
1 | Enter appropriate data in the yellow cells in consistent units of measure …
… and read the results in the blue cells.
Note that the Supply Air Flow is the flow out of the mixed air plenum.
Mixed air temperature based on conservation of mass
|  | Mixed air temperature, °F = | (((OAT, °F) x (OA Flow, Cfm)) + ((RAT, °F) x (RA Flow, Cfm))/SA Flow, Cfm
|  | Outdoor air temperature (OAT)= | -20 | °F
|  | Return air temperature (RAT) = | 72 | °F
|  | Supply flow (SA Flow) = | 25000 | cfm
|  | Outdoor air flow (OA Flow) = | 5000 | cfm
|  | RA Flow = | 20000 | cfm
|  | Mixed air temperature = | 53.6 | °F
Outdoor air temperature that gives a specified mixed air temperature based on conservation of mass
|  | Outdoor air temperature, °F = | (((MAT, °F) x (SA Flow, Cfm)) - ((RAT, °F) x (RA Flow, Cfm))/OA Flow, Cfm
|  | Mixed air temperature (MAT) = | 32 | °F
|  | Return air temperature (RAT) = | 75 | °F
|  | Supply flow (SAF) = | 18000 | cfm
|  | Outdoor air flow (OA Flow) = | 9000 | cfm
|  | RA Flow = | 9000 | cfm
|  | Outdoor air temperature (OAT)= | -11 | °F
Outdoor air percentage based on temperatures
|  | Outdoor air % = | (MAT- RAT)/(OAT - RAT)
|  | Mixed air temperature (MAT) = | 64.3 | °F
|  | Return air temperature (RAT) = | 67 | °F
|  | Outdoor air temperature (OAT)= | 52 | °F
|  | Outdoor air % = | 18%
|  | 100% Mixed air flow x Mixed air temperature = | (Outdoor air % x Outdoor temperature) + ((100-Outdoor air %)x(Return temperature))

## Example
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
The tabs that follow this tab are an example of how to use the spreadsheet. The data comes from facility on the UC Berkeley Campus named "Le Conte Annex". The facility is part of the UCB Physics department and houses offices, research labs, and teaching labs. The system we were working with was origianlly a 100% outdoor air system that was retrofitted with an economizer at one point. The image below is a very rough system diagram that I sketched up in the field. The face and bypass coil is a steam coil as are is the coil for the hot deck. There are 4 hot and cold deck ducts, with each duct serving a floor. Mixing dampers are located at the zone served and as of the time I type this, I do not know if they are volume regulating mixing dampers or not. Note that the example was done with an earlier version of this spreadsheet tool, so there are some minor differences between what you will see there and what the current version of the spreadsheet will create.

## Example Side by Side Comparison
These are screen shots of the test results placed side by side to allow you to compare the results; If you "Paste Special" - "Linked Picture" they will update if you change something.

## Example Test 1 Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Mixing Plenum Test
[14 empty] | Misc. Notes |  |  |  | Test 1 % of Design | Test 2 % of Design | Test 3 % of Design
| Test date - | [5 empty] | Date: | 2013-01-04
| Project/System Name - | [5 empty] | Project Name: | Le Conte Annex AHU1 | [6 empty] | AHU1 Design Flow - | 47500 | cfm | 104.1% | 110.8% | 120.2%
| Project Number - | [5 empty] | Project Number: | PEC EBCx Class, Series 8, Session 6b | [6 empty] | AHU1 Exhaust - | 9000 | cfm Total
| Test engineer - | [5 empty] | Engineer: | Maria's Group | [6 empty] | Toilet exhaust - | 4400 | cfm
| Test start time - | [6 empty] | 12:15 | [6 empty] | Room 85 - | 1000 | cfm
| Test end time - | [6 empty] | 13:20 | [6 empty] | Room 87 - | 1000 | cfm
| Average outdoor air temperature during the test - | [6 empty] | 52 | °F (Field measurement) | [5 empty] | Room S-85 - | 1000 | cfm
| Average return air teperature during the test - | [6 empty] | 65.425 | °F (Field measurement) | [5 empty] | Room S-87 - | 1000 | cfm
` | Outdoor Air Damper Information | [13 empty] | Room 186A - | 300 | cfm
| Target minimum outdoor air percentage - | [6 empty] | 18.95% | Estimate based on design AHU1 flow and related exhaust flow | [5 empty] | Room 174 - | 300 | cfm
| Outdoor air damper number of sections - | [6 empty] | 3
| Outdoor air damper number of actuators - | [6 empty] | 1
| Outdoor air damper typical actuator make and model - | [6 empty] | 6" pneumatic, Honeywell?
| Outdoor air damper over-all height - | [6 empty] | 36 | inches (estimate from drawings and photo)
| Outdoor air damper over-all width - | [6 empty] | 126 | inches (estimate from drawings and photo)
| Outdoor air damper nominal face area - | [6 empty] | 31.5 | sq.ft.
| Outdoor air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [6 empty] | Opposed | blade | Blade rotation -
| Outdoor air damper blade orientation - | [6 empty] | Horizontal
| Outdoor air damper blade angle during the test - | [6 empty] | 80° degrees from the horizontal (estimated)
| Outdoor air damper control signal during the test - | [6 empty] | 00 hexadecimal in the Microstar
` | Return Air Damper Information
| Return air damper number of sections - | [6 empty] | 2
| Return air damper number of actuators - | [6 empty] | 2
| Return air damper typical actuator make and model - | [6 empty] | Johnson 6" pneumatic
| Return air damper over-all height - | [6 empty] | 42 | inches (estimate from photo)
| Return air damper over-all width - | [6 empty] | 30 | inches (estimate from photo)
| Return air damper nominal face area - | [6 empty] | 17.5 | sq.ft.
| Return air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [6 empty] | Opposed | blade | Blade rotation -
| Return air damper blade orientation - | [6 empty] | Horizontal
| Return air damper blade angle during the test - | [6 empty] | Not noted
| Return air damper control signal during the test - | [6 empty] | Common signal with the outdoor air damper
| Total area for the filter bank (sum of individual element areas) - | [6 empty] | 97.2222 | sq.ft.
| Total flow for the filter bank (sum of individual elements) - | [6 empty] | 49466.6667 | cfm
| Average velocity for the filter bank (average of individual elements) - | [6 empty] | 508.8 | fpm
| Number of rows used - | [6 empty] | 5 | (13 maximum)
| Number of colums use - | [6 empty] | 7 | (14 maximum)
| Average temperature (average of individual temperature readings) - | [6 empty] | 64.4236 | °F
| Mass weighted average temperature (individual temperature readings times related flow divided by total flow) - | [6 empty] | 64.3338 | °F
| Outdoor air % of mixed air flow during test based on temperatures - | [6 empty] | 8.128%
| Average outdoor air flow during the test based on temperatures - | [6 empty] | 4020.7583 | cfm
| Maximum temperature - | [6 empty] | 66.8 | °F
| Minimum temperature - | [6 empty] | 62.2 | °F
| Maximum velocity - | [6 empty] | 721 | fpm
| Minimum velocity - | [6 empty] | 252 | fpm
Note - Suspect that the field reading of 61.7°F for the filter in the 4th row, fifth column was an error given the pattern around that particular filter (highlighted in dark yellow with a red boarder). Changed it to the average of the fitlers around it.
|  | Filter Column Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches
|  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used
| Filter Row Height, inches | Velocity reading, fpm | 526 | Velocity reading, fpm | 506 | Velocity reading, fpm | 604 | Velocity reading, fpm | 564 | Velocity reading, fpm | 623 | Velocity reading, fpm | 604 | Velocity reading, fpm | 447 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 62.5 | Temperature, °F | 63.8 | Temperature, °F | 63.1 | Temperature, °F | 63.3 | Temperature, °F | 64.2 | Temperature, °F | 64.5 | Temperature, °F | 64.5 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1461.1111 | Flow rate , cfm - | 1405.5556 | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 1730.5556 | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1241.6667 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 91319.4444 | Flow x Temperature | 89674.4444 | Flow x Temperature | 105867.7778 | Flow x Temperature | 99170 | Flow x Temperature | 111101.6667 | Flow x Temperature | 108216.6667 | Flow x Temperature | 80087.5 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 604 | Velocity reading, fpm | 681 | Velocity reading, fpm | 604 | Velocity reading, fpm | 663 | Velocity reading, fpm | 663 | Velocity reading, fpm | 506 | Velocity reading, fpm | 526 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 64 | Temperature, °F | 62.3 | Temperature, °F | 63.5 | Temperature, °F | 64.2 | Temperature, °F | 64.7 | Temperature, °F | 65.3 | Temperature, °F | 64.9 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1891.6667 | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1841.6667 | Flow rate , cfm - | 1841.6667 | Flow rate , cfm - | 1405.5556 | Flow rate , cfm - | 1461.1111 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 107377.7778 | Flow x Temperature | 117850.8333 | Flow x Temperature | 106538.8889 | Flow x Temperature | 118235 | Flow x Temperature | 119155.8333 | Flow x Temperature | 91782.7778 | Flow x Temperature | 94826.1111 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 721 | Velocity reading, fpm | 447 | Velocity reading, fpm | 272 | Velocity reading, fpm | 252 | Velocity reading, fpm | 447 | Velocity reading, fpm | 409 | Velocity reading, fpm | 429 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 62.2 | Temperature, °F | 62.4 | Temperature, °F | 63.8 | Temperature, °F | 65.1 | Temperature, °F | 64.9 | Temperature, °F | 65 | Temperature, °F | 66 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 2002.7778 | Flow rate , cfm - | 1241.6667 | Flow rate , cfm - | 755.5556 | Flow rate , cfm - | 700 | Flow rate , cfm - | 1241.6667 | Flow rate , cfm - | 1136.1111 | Flow rate , cfm - | 1191.6667 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 124572.7778 | Flow x Temperature | 77480 | Flow x Temperature | 48204.4444 | Flow x Temperature | 45570 | Flow x Temperature | 80584.1667 | Flow x Temperature | 73847.2222 | Flow x Temperature | 78650 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 584 | Velocity reading, fpm | 487 | Velocity reading, fpm | 546 | Velocity reading, fpm | 526 | Velocity reading, fpm | 447 | Velocity reading, fpm | 623 | Velocity reading, fpm | 526 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 63.3 | Temperature, °F | 65.7 | Temperature, °F | 63.3 | Temperature, °F | 64 | Temperature, °F | 65.325 | Temperature, °F | 66.8 | Temperature, °F | 66.2 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1352.7778 | Flow rate , cfm - | 1516.6667 | Flow rate , cfm - | 1461.1111 | Flow rate , cfm - | 1241.6667 | Flow rate , cfm - | 1730.5556 | Flow rate , cfm - | 1461.1111 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 102686.6667 | Flow x Temperature | 88877.5 | Flow x Temperature | 96005 | Flow x Temperature | 93511.1111 | Flow x Temperature | 81111.875 | Flow x Temperature | 115601.1111 | Flow x Temperature | 96725.5556 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 429 | Velocity reading, fpm | 389 | Velocity reading, fpm | 405 | Velocity reading, fpm | 405 | Velocity reading, fpm | 546 | Velocity reading, fpm | 350 | Velocity reading, fpm | 447 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 64.7 | Temperature, °F | 64.5 | Temperature, °F | 64.2 | Temperature, °F | 64.4 | Temperature, °F | 65.6 | Temperature, °F | 66.3 | Temperature, °F | 66.3 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1191.6667 | Flow rate , cfm - | 1080.5556 | Flow rate , cfm - | 1125 | Flow rate , cfm - | 1125 | Flow rate , cfm - | 1516.6667 | Flow rate , cfm - | 972.2222 | Flow rate , cfm - | 1241.6667 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 77100.8333 | Flow x Temperature | 69695.8333 | Flow x Temperature | 72225 | Flow x Temperature | 72450 | Flow x Temperature | 99493.3333 | Flow x Temperature | 64458.3333 | Flow x Temperature | 82322.5 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
Docment dimensions and other parameters in the cells with the dark yellow highlight. Take photographs and make sketches to supplement the test data and document the physical configuration of the mixed air plenum. Document the system diagram for the plenum on the results tab in the graph paper area provided. Note that if you manipulate the text boxes and lines that are already there, the data on this tab will automatically fill in and follow them.
In the test matrix, nsert the filter height and width in inches into the blue boxes for all rows and columns. The area of each filter will be calculated in the indvidual filter elements and totaled below. Enter the velocity reading and temperature observed in the yellow area. The flow rate associated with each filter element and the flow times temperature parameter will be calculated. Average velocities, total flow, average temperature and mass weighted average temperature (the true average temperature from a conservation of mass and energy standpoint) are caculated where indicated below.
Note that you need to adjusted the number of rows and columns you actually use in your filter bank modely by adjusting the values in the purple highlighted cells tif you are interested in that information. For the other calculated values, as long as the input cells (blue and yellow boxes) for rows and columns with out filters are left blank, the result will be correct.
Note that you will need to click into a cell below the yellow area and arrow key up to enter data because the yellow is created with an autoshape overlayed on the cell to higlight it. I did that so that you could use the cell formating to higlight the filter elements that are being used for the particular unit you are working on and still have the data entry cells higlighted.
If you enter the average outdoor air temperature and return air temperature that existed during the test into the orange highlighted squares, the average outdoor air flow during the test will be calculated based on conservation of mass and energy.
100% Mixed air flow x Mixed air temperature = (Outdoor air % x Outdoor temperature) + ((100-Outdoor air %)x(Return temperature))
Solving for Outdoor Air %:
Outdoor air % = (MAT- RAT)/(OAT - RAT)
The equation used is included on the tab "Mixed Air Temp Callcs". The greater the difference between the outdoor and return temperatures, the more accurate the result. To understand this consider what would happen if both the outdoor air temperature and the return air temperaure were the same value.
Ideally, you should use the same temperature sensor for measureing the outdoor air temperature and return air temperature as you used for the filter face temperatures. But if you forget to take the other two temperatures, you may be able to get a reasonable estimate of the outdoor air flow by checking trends in the control system for return air temperatures at the time of your test or by making a reasonable assumption about the return temperature. For example, it would be reasonable to assume the return temperature was about the same as the typical space temperature in the facility.
For outdoor temperature, you may be able to find trend information in the control system. Or you could use historical data from a nearby weather station that can be found in sources like the National Weather Service or Weather Underground.
The EXAMPLE tabs contain the data and results used to assess a filter bank at Le Conte Annex on the UC Berkeley Campus.

## Example Test 1 Results
Test 1 |  |  |  |  | Maria's Group | [6 empty] | Plenum Picture | Plenum System Diagram (with Test 1 results)
Test Date - |  |  |  |  | 2013-01-04
Test Start Time - |  |  |  |  | 12:15 | [10 empty] | 45,446 cfm of return air at 65.4°F |  | 2 Section, 18 Square Foot, Horizontal Opposed Blade Return Air Damper
Test Finish Time - |  |  |  |  | 13:20
Outdoor air damper size - |  |  |  |  | 31.5 |  | sq.ft.
Outdoor air damper sections - |  |  |  |  | 3
Outdoor air damper type - |  |  |  |  | Horizontal Opposed |  |  |  | Blade
Outdoor air flow - |  |  |  |  | 4020.7583 |  | cfm
Outdoor air temperature - |  |  |  |  | 52 |  | °F
Outdoor air % of total - |  |  |  |  | 8.128% |  | (Design target is 19%)
Return air damper size - |  |  |  |  | 17.5 |  | sq.ft.
Return air damper sections - |  |  |  |  | 2
Return air damper type - |  |  |  |  | Horizontal Opposed |  |  |  | Blade | [8 empty] | Filter bank
Return air flow - |  |  |  |  | 45445.9083 |  | cfm | [6 empty] | 4,021 of outdoor air at 52.°F
Return air temperature - |  |  |  |  | 65.425 |  | °F
Total air flow - |  |  |  |  | 49466.6667 |  | cfm
Outdoor air damper velocity - |  |  |  |  | 1570.3704 |  | fpm ( at measured total flow an 100% OA)
Return air damper velocity - |  |  |  |  | 2291.0877 |  | fpm (at measured total flow on MOA)
Mixed air temperature - |  |  |  |  | 64.3338 |  | °F (mass weighted; true mixed air temperature)
[5 empty] | 64.4236 |  | °F (average if measurements)
Maximum temperature - |  |  |  |  | 66.8 |  | °F | [9 empty] | 49,467 cfm of mixed air at 64.3 °F
Minimum temperature - |  |  |  |  | 62.2 |  | °F
Maximum velocity - |  |  |  |  | 721 |  | fpm
Minimum velocity - |  |  |  |  | 252 |  | fpm
Link to additional photos - |  |  |  |  | ..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-07 | [9 empty] | 3 Section, 32 Square Foot, Horizontal Opposed Blade Outdoor Air Damper
..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-11
Link to field notes - |  |  |  |  | LeConte Annex
Temperature Profile |  |  |  |  | Coldest |  |  | Hottest |  | Minimum | Maximum
| 20 | 20 | 20 | 20 | 20 | 20 | 20
20 | 62.5 | 63.8 | 63.1 | 63.3 | 64.2 | 64.5 | 64.5
20 | 64 | 62.3 | 63.5 | 64.2 | 64.7 | 65.3 | 64.9
20 | 62.2 | 62.4 | 63.8 | 65.1 | 64.9 | 65 | 66
20 | 63.3 | 65.7 | 63.3 | 64 | 65.325 | 66.8 | 66.2
20 | 64.7 | 64.5 | 64.2 | 64.4 | 65.6 | 66.3 | 66.3
Velocity Profile |  |  |  |  | Slowest |  |  | Fastest |  | Minimum | Maximum
| 20 | 20 | 20 | 20 | 20 | 20 | 20
20 | 526 | 506 | 604 | 564 | 623 | 604 | 447
20 | 604 | 681 | 604 | 663 | 663 | 506 | 526
20 | 721 | 447 | 272 | 252 | 447 | 409 | 429
20 | 584 | 487 | 546 | 526 | 447 | 623 | 526
20 | 429 | 389 | 405 | 405 | 546 | 350 | 447

## Example Test 2 Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Mixing Plenum Test
| Test date - | [5 empty] | Date: | 2013-01-04 | [5 empty] | Misc. Notes
| Project/System Name - | [5 empty] | Project Name: | Le Conte Annex AHU1 | [6 empty] | AHU1 Design Flow - | 47500 | cfm
| Project Number - | [5 empty] | Project Number: | PEC EBCx Class, Series 8, Session 6b | [6 empty] | AHU1 Exhaust - | 9000 | cfm Total
| Test engineer - | [5 empty] | Engineer: | Kathy's Group | [6 empty] | Toilet exhaust - | 4400 | cfm
| Test start time - | [6 empty] | 13:20 | [6 empty] | Room 85 - | 1000 | cfm
| Test end time - | [6 empty] | 14:25 | [6 empty] | Room 87 - | 1000 | cfm
| Average outdoor air temperature during the test - | [6 empty] | 52 | °F (Field measurement) | [5 empty] | Room S-85 - | 1000 | cfm
| Average return air teperature during the test - | [6 empty] | 69.8 | °F (Field measurement) | [5 empty] | Room S-87 - | 1000 | cfm
` | Outdoor Air Damper Information | [13 empty] | Room 186A - | 300 | cfm
| Target minimum outdoor air percentage - | [6 empty] | 18.95% | Estimate based on design AHU1 flow and related exhaust flow | [5 empty] | Room 174 - | 300 | cfm
| Outdoor air damper number of sections - | [6 empty] | 3
| Outdoor air damper number of actuators - | [6 empty] | 1
| Outdoor air damper typical actuator make and model - | [6 empty] | 6" pneumatic, Honeywell?
| Outdoor air damper over-all height - | [6 empty] | 36 | inches (estimate from drawings and photo)
| Outdoor air damper over-all width - | [6 empty] | 126 | inches (estimate from drawings and photo)
| Outdoor air damper nominal face area - | [6 empty] | 31.5 | sq.ft.
| Outdoor air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [6 empty] | Opposed | blade | Blade rotation -
| Outdoor air damper blade orientation - | [6 empty] | Horizontal
| Outdoor air damper blade angle during the test - | [6 empty] | 60° degrees from the horizontal (estimated)
| Outdoor air damper control signal during the test - | [6 empty] | 10 hexadecimal in the Microstar
` | Return Air Damper Information
| Return air damper number of sections - | [6 empty] | 2
| Return air damper number of actuators - | [6 empty] | 2
| Return air damper typical actuator make and model - | [6 empty] | Johnson 6" pneumatic
| Return air damper over-all height - | [6 empty] | 42 | inches (estimate from photo)
| Return air damper over-all width - | [6 empty] | 30 | inches (estimate from photo)
| Return air damper nominal face area - | [6 empty] | 17.5 | sq.ft.
| Return air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [6 empty] | Opposed | blade | Blade rotation -
| Return air damper blade orientation - | [6 empty] | Horizontal
| Return air damper blade angle during the test - | [6 empty] | Not noted
| Return air damper control signal during the test - | [6 empty] | Common signal with the outdoor air damper
| Total area for the filter bank (sum of individual element areas) - | [6 empty] | 97.2222 | sq.ft.
| Total flow for the filter bank (sum of individual elements) - | [6 empty] | 52638.8889 | cfm
| Average velocity for the filter bank (average of individual elements) - | [6 empty] | 541.4286 | fpm
| Number of rows used - | [6 empty] | 5 | (13 maximum)
| Number of colums use - | [6 empty] | 7 | (14 maximum)
| Average temperature (average of individual temperature readings) - | [6 empty] | 64.28 | °F
| Mass weighted average temperature (individual temperature readings times related flow divided by total flow) - | [6 empty] | 64.2965 | °F
| Outdoor air % of mixed air flow during test based on temperatures - | [6 empty] | 30.92%
| Average outdoor air flow during the test based on temperatures - | [6 empty] | 16275.2185 | cfm
| Maximum temperature - | [6 empty] | 69.9 | °F
| Minimum temperature - | [6 empty] | 60 | °F
| Maximum velocity - | [6 empty] | 701 | fpm
| Minimum velocity - | [6 empty] | 350 | fpm
|  | Filter Column Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches
|  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used
| Filter Row Height, inches | Velocity reading, fpm | 584 | Velocity reading, fpm | 409 | Velocity reading, fpm | 584 | Velocity reading, fpm | 584 | Velocity reading, fpm | 623 | Velocity reading, fpm | 526 | Velocity reading, fpm | 506 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 60.9 | Temperature, °F | 60.8 | Temperature, °F | 63.5 | Temperature, °F | 64.7 | Temperature, °F | 64.9 | Temperature, °F | 65.4 | Temperature, °F | 66.9 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1136.1111 | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1730.5556 | Flow rate , cfm - | 1461.1111 | Flow rate , cfm - | 1405.5556 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 98793.3333 | Flow x Temperature | 69075.5556 | Flow x Temperature | 103011.1111 | Flow x Temperature | 104957.7778 | Flow x Temperature | 112313.0556 | Flow x Temperature | 95556.6667 | Flow x Temperature | 94031.6667 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 623 | Velocity reading, fpm | 567 | Velocity reading, fpm | 604 | Velocity reading, fpm | 564 | Velocity reading, fpm | 584 | Velocity reading, fpm | 650 | Velocity reading, fpm | 526 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 60.2 | Temperature, °F | 61.8 | Temperature, °F | 63.3 | Temperature, °F | 64.7 | Temperature, °F | 64.4 | Temperature, °F | 65.9 | Temperature, °F | 66.5 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1730.5556 | Flow rate , cfm - | 1575 | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1805.5556 | Flow rate , cfm - | 1461.1111 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 104179.4444 | Flow x Temperature | 97335 | Flow x Temperature | 106203.3333 | Flow x Temperature | 101363.3333 | Flow x Temperature | 104471.1111 | Flow x Temperature | 118986.1111 | Flow x Temperature | 97163.8889 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 604 | Velocity reading, fpm | 584 | Velocity reading, fpm | 506 | Velocity reading, fpm | 389 | Velocity reading, fpm | 506 | Velocity reading, fpm | 584 | Velocity reading, fpm | 701 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 60.8 | Temperature, °F | 61.5 | Temperature, °F | 64 | Temperature, °F | 65.1 | Temperature, °F | 69.9 | Temperature, °F | 66.3 | Temperature, °F | 66.5 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1405.5556 | Flow rate , cfm - | 1080.5556 | Flow rate , cfm - | 1405.5556 | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1947.2222 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 102008.8889 | Flow x Temperature | 99766.6667 | Flow x Temperature | 89955.5556 | Flow x Temperature | 70344.1667 | Flow x Temperature | 98248.3333 | Flow x Temperature | 107553.3333 | Flow x Temperature | 129490.2778 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 564 | Velocity reading, fpm | 564 | Velocity reading, fpm | 564 | Velocity reading, fpm | 564 | Velocity reading, fpm | 370 | Velocity reading, fpm | 584 | Velocity reading, fpm | 564 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 60 | Temperature, °F | 60.9 | Temperature, °F | 64 | Temperature, °F | 64.9 | Temperature, °F | 66.2 | Temperature, °F | 66.7 | Temperature, °F | 66.7 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 1027.7778 | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 94000 | Flow x Temperature | 95410 | Flow x Temperature | 100266.6667 | Flow x Temperature | 101676.6667 | Flow x Temperature | 68038.8889 | Flow x Temperature | 108202.2222 | Flow x Temperature | 104496.6667 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 429 | Velocity reading, fpm | 350 | Velocity reading, fpm | 467 | Velocity reading, fpm | 487 | Velocity reading, fpm | 584 | Velocity reading, fpm | 564 | Velocity reading, fpm | 487 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 60 | Temperature, °F | 61.7 | Temperature, °F | 64.4 | Temperature, °F | 65.4 | Temperature, °F | 66.7 | Temperature, °F | 67.1 | Temperature, °F | 67.1 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1191.6667 | Flow rate , cfm - | 972.2222 | Flow rate , cfm - | 1297.2222 | Flow rate , cfm - | 1352.7778 | Flow rate , cfm - | 1622.2222 | Flow rate , cfm - | 1566.6667 | Flow rate , cfm - | 1352.7778 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 71500 | Flow x Temperature | 59986.1111 | Flow x Temperature | 83541.1111 | Flow x Temperature | 88471.6667 | Flow x Temperature | 108202.2222 | Flow x Temperature | 105123.3333 | Flow x Temperature | 90771.3889 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
Docment dimensions and other parameters in the cells with the dark yellow highlight. Take photographs and make sketches to supplement the test data and document the physical configuration of the mixed air plenum. Document the system diagram for the plenum on the results tab in the graph paper area provided. Note that if you manipulate the text boxes and lines that are already there, the data on this tab will automatically fill in and follow them.
In the test matrix, nsert the filter height and width in inches into the blue boxes for all rows and columns. The area of each filter will be calculated in the indvidual filter elements and totaled below. Enter the velocity reading and temperature observed in the yellow area. The flow rate associated with each filter element and the flow times temperature parameter will be calculated. Average velocities, total flow, average temperature and mass weighted average temperature (the true average temperature from a conservation of mass and energy standpoint) are caculated where indicated below.
Note that you need to adjusted the number of rows and columns you actually use in your filter bank modely by adjusting the values in the purple highlighted cells tif you are interested in that information. For the other calculated values, as long as the input cells (blue and yellow boxes) for rows and columns with out filters are left blank, the result will be correct.
Note that you will need to click into a cell below the yellow area and arrow key up to enter data because the yellow is created with an autoshape overlayed on the cell to higlight it. I did that so that you could use the cell formating to higlight the filter elements that are being used for the particular unit you are working on and still have the data entry cells higlighted.
If you enter the average outdoor air temperature and return air temperature that existed during the test into the orange highlighted squares, the average outdoor air flow during the test will be calculated based on conservation of mass and energy.
100% Mixed air flow x Mixed air temperature = (Outdoor air % x Outdoor temperature) + ((100-Outdoor air %)x(Return temperature))
Solving for Outdoor Air %:
Outdoor air % = (MAT- RAT)/(OAT - RAT)
The equation used is included on the tab "Mixed Air Temp Callcs". The greater the difference between the outdoor and return temperatures, the more accurate the result. To understand this consider what would happen if both the outdoor air temperature and the return air temperaure were the same value.
Ideally, you should use the same temperature sensor for measureing the outdoor air temperature and return air temperature as you used for the filter face temperatures. But if you forget to take the other two temperatures, you may be able to get a reasonable estimate of the outdoor air flow by checking trends in the control system for return air temperatures at the time of your test or by making a reasonable assumption about the return temperature. For example, it would be reasonable to assume the return temperature was about the same as the typical space temperature in the facility.
For outdoor temperature, you may be able to find trend information in the control system. Or you could use historical data from a nearby weather station that can be found in sources like the National Weather Service or Weather Underground.
The EXAMPLE tabs contain the data and results used to assess a filter bank at Le Conte Annex on the UC Berkeley Campus.

## Example Test 2 Results
Test 2 |  |  |  |  | Kathy's Group | [6 empty] | Plenum Picture | Plenum System Diagram (with Test 2 results)
Test Date - |  |  |  |  | 2013-01-04
Test Start Time - |  |  |  |  | 13:20 | [10 empty] | 36,364 cfm of return air at 69.8°F |  | 2 Section, 18 Square Foot, Horizontal Opposed Blade Return Air Damper
Test Finish Time - |  |  |  |  | 14:25
Outdoor air damper size - |  |  |  |  | 31.5 |  | sq.ft.
Outdoor air damper sections - |  |  |  |  | 3
Outdoor air damper type - |  |  |  |  | Horizontal Opposed |  |  |  | Blade
Outdoor air flow - |  |  |  |  | 16275.2185 |  | cfm
Outdoor air temperature - |  |  |  |  | 52 |  | °F
Outdoor air % of total - |  |  |  |  | 30.92% |  | (Design target is 19%)
Return air damper size - |  |  |  |  | 17.5 |  | sq.ft.
Return air damper sections - |  |  |  |  | 2
Return air damper type - |  |  |  |  | Horizontal Opposed |  |  |  | Blade | [8 empty] | Filter bank
Return air flow - |  |  |  |  | 36363.6704 |  | cfm | [6 empty] | 16,275 of outdoor air at 52.°F
Return air temperature - |  |  |  |  | 69.8 |  | °F
Total air flow - |  |  |  |  | 52638.8889 |  | cfm
Outdoor air damper velocity - |  |  |  |  | 1671.0758 |  | fpm ( at measured total flow an 100% OA)
Return air damper velocity - |  |  |  |  | 2438.0117 |  | fpm (at measured total flow on MOA)
Mixed air temperature - |  |  |  |  | 64.2965 |  | °F (mass weighted; true mixed air temperature)
[5 empty] | 64.28 |  | °F (average if measurements)
Maximum temperature - |  |  |  |  | 69.9 |  | °F | [9 empty] | 52,639 cfm of mixed air at 64.3 °F
Minimum temperature - |  |  |  |  | 60 |  | °F
Maximum velocity - |  |  |  |  | 701 |  | fpm
Minimum velocity - |  |  |  |  | 350 |  | fpm
Link to additional photos - |  |  |  |  | ..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-07 | [9 empty] | 3 Section, 32 Square Foot, Horizontal Opposed Blade Outdoor Air Damper
..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-11
Link to field notes - |  |  |  |  | ..\LeConte Annex
Temperature Profile |  |  |  |  | Coldest |  |  | Hottest |  | Minimum | Maximum
| 20 | 20 | 20 | 20 | 20 | 20 | 20
20 | 60.9 | 60.8 | 63.5 | 64.7 | 64.9 | 65.4 | 66.9
20 | 60.2 | 61.8 | 63.3 | 64.7 | 64.4 | 65.9 | 66.5
20 | 60.8 | 61.5 | 64 | 65.1 | 69.9 | 66.3 | 66.5
20 | 60 | 60.9 | 64 | 64.9 | 66.2 | 66.7 | 66.7
20 | 60 | 61.7 | 64.4 | 65.4 | 66.7 | 67.1 | 67.1
Velocity Profile |  |  |  |  | Slowest |  |  | Fastest |  | Minimum | Maximum
| 20 | 20 | 20 | 20 | 20 | 20 | 20
20 | 584 | 409 | 584 | 584 | 623 | 526 | 506
20 | 623 | 567 | 604 | 564 | 584 | 650 | 526
20 | 604 | 584 | 506 | 389 | 506 | 584 | 701
20 | 564 | 564 | 564 | 564 | 370 | 584 | 564
20 | 429 | 350 | 467 | 487 | 584 | 564 | 487

## Example Test 3 Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Mixing Plenum Test
| Test date - | [5 empty] | Date: | 2013-01-04 | [5 empty] | Misc. Notes
| Project/System Name - | [5 empty] | Project Name: | Le Conte Annex AHU1 | [6 empty] | AHU1 Design Flow - | 47500 | cfm
| Project Number - | [5 empty] | Project Number: | PEC EBCx Class, Series 8, Session 6b | [6 empty] | AHU1 Exhaust - | 9000 | cfm Total
| Test engineer - | [5 empty] | Engineer: | Dan's Group | [6 empty] | Toilet exhaust - | 4400 | cfm
| Test start time - | [6 empty] | 14:25 | [6 empty] | Room 85 - | 1000 | cfm
| Test end time - | [6 empty] | 15:30 | [6 empty] | Room 87 - | 1000 | cfm
| Average outdoor air temperature during the test - | [6 empty] | 52 | °F (Field measurement) | [5 empty] | Room S-85 - | 1000 | cfm
| Average return air teperature during the test - | [6 empty] | 69.8 | °F (Field measurement) | [5 empty] | Room S-87 - | 1000 | cfm
` | Outdoor Air Damper Information | [13 empty] | Room 186A - | 300 | cfm
| Target minimum outdoor air percentage - | [6 empty] | 18.95% | Estimate based on design AHU1 flow and related exhaust flow | [5 empty] | Room 174 - | 300 | cfm
| Outdoor air damper number of sections - | [6 empty] | 3
| Outdoor air damper number of actuators - | [6 empty] | 1
| Outdoor air damper typical actuator make and model - | [6 empty] | 6" pneumatic, Honeywell?
| Outdoor air damper over-all height - | [6 empty] | 36 | inches (estimate from drawings and photo)
| Outdoor air damper over-all width - | [6 empty] | 126 | inches (estimate from drawings and photo)
| Outdoor air damper nominal face area - | [6 empty] | 31.5 | sq.ft.
| Outdoor air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [6 empty] | Opposed | blade | Blade rotation -
| Outdoor air damper blade orientation - | [6 empty] | Horizontal
| Outdoor air damper blade angle during the test - | [6 empty] | 30° degrees from the horizontal (estimated)
| Outdoor air damper control signal during the test - | [6 empty] | 80 hexadecimal in the Microstar
` | Return Air Damper Information
| Return air damper number of sections - | [6 empty] | 2
| Return air damper number of actuators - | [6 empty] | 2
| Return air damper typical actuator make and model - | [6 empty] | Johnson 6" pneumatic
| Return air damper over-all height - | [6 empty] | 42 | inches (estimate from photo)
| Return air damper over-all width - | [6 empty] | 30 | inches (estimate from photo)
| Return air damper nominal face area - | [6 empty] | 17.5 | sq.ft.
| Return air damper blade type (opposed or parallel; if parallel note how the blades direct air as they close) - | [6 empty] | Opposed | blade | Blade rotation -
| Return air damper blade orientation - | [6 empty] | Horizontal
| Return air damper blade angle during the test - | [6 empty] | Not noted
| Return air damper control signal during the test - | [6 empty] | Common signal with the outdoor air damper
| Total area for the filter bank (sum of individual element areas) - | [6 empty] | 97.2222 | sq.ft.
| Total flow for the filter bank (sum of individual elements) - | [6 empty] | 57113.8889 | cfm
| Average velocity for the filter bank (average of individual elements) - | [6 empty] | 587.4571 | fpm
| Number of rows used - | [6 empty] | 5 | (13 maximum)
| Number of colums use - | [6 empty] | 7 | (14 maximum)
| Average temperature (average of individual temperature readings) - | [6 empty] | 55.3257 | °F
| Mass weighted average temperature (individual temperature readings times related flow divided by total flow) - | [6 empty] | 55.0759 | °F
| Outdoor air % of mixed air flow during test based on temperatures - | [6 empty] | 82.72%
| Average outdoor air flow during the test based on temperatures - | [6 empty] | 47244.4444 | cfm
| Maximum temperature - | [6 empty] | 59.3 | °F
| Minimum temperature - | [6 empty] | 51.8 | °F
| Maximum velocity - | [6 empty] | 945 | fpm
| Minimum velocity - | [6 empty] | 272 | fpm
|  | Filter Column Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches |  | Filter Row Width, inches
|  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used |  | Not Used
| Filter Row Height, inches | Velocity reading, fpm | 331 | Velocity reading, fpm | 350 | Velocity reading, fpm | 272 | Velocity reading, fpm | 643 | Velocity reading, fpm | 779 | Velocity reading, fpm | 643 | Velocity reading, fpm | 632 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 57.5 | Temperature, °F | 57.3 | Temperature, °F | 57 | Temperature, °F | 55.4 | Temperature, °F | 53.9 | Temperature, °F | 52.7 | Temperature, °F | 52.5 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 919.4444 | Flow rate , cfm - | 972.2222 | Flow rate , cfm - | 755.5556 | Flow rate , cfm - | 1786.1111 | Flow rate , cfm - | 2163.8889 | Flow rate , cfm - | 1786.1111 | Flow rate , cfm - | 1755.5556 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 52868.0556 | Flow x Temperature | 55708.3333 | Flow x Temperature | 43066.6667 | Flow x Temperature | 98950.5556 | Flow x Temperature | 116633.6111 | Flow x Temperature | 94128.0556 | Flow x Temperature | 92166.6667 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 350 | Velocity reading, fpm | 292 | Velocity reading, fpm | 370 | Velocity reading, fpm | 741 | Velocity reading, fpm | 945 | Velocity reading, fpm | 799 | Velocity reading, fpm | 653 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 57.5 | Temperature, °F | 57.9 | Temperature, °F | 57 | Temperature, °F | 55.9 | Temperature, °F | 53.9 | Temperature, °F | 52.7 | Temperature, °F | 52.1 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 972.2222 | Flow rate , cfm - | 811.1111 | Flow rate , cfm - | 1027.7778 | Flow rate , cfm - | 2058.3333 | Flow rate , cfm - | 2625 | Flow rate , cfm - | 2219.4444 | Flow rate , cfm - | 1813.8889 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 55902.7778 | Flow x Temperature | 46963.3333 | Flow x Temperature | 58583.3333 | Flow x Temperature | 115060.8333 | Flow x Temperature | 141487.5 | Flow x Temperature | 116964.7222 | Flow x Temperature | 94503.6111 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 800 | Velocity reading, fpm | 604 | Velocity reading, fpm | 429 | Velocity reading, fpm | 760 | Velocity reading, fpm | 858 | Velocity reading, fpm | 643 | Velocity reading, fpm | 701 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 58.4 | Temperature, °F | 58.1 | Temperature, °F | 57 | Temperature, °F | 57.9 | Temperature, °F | 54.1 | Temperature, °F | 52.5 | Temperature, °F | 52.5 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 2222.2222 | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1191.6667 | Flow rate , cfm - | 2111.1111 | Flow rate , cfm - | 2383.3333 | Flow rate , cfm - | 1786.1111 | Flow rate , cfm - | 1947.2222 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 129777.7778 | Flow x Temperature | 97478.8889 | Flow x Temperature | 67925 | Flow x Temperature | 122233.3333 | Flow x Temperature | 128938.3333 | Flow x Temperature | 93770.8333 | Flow x Temperature | 102229.1667 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 681 | Velocity reading, fpm | 487 | Velocity reading, fpm | 604 | Velocity reading, fpm | 663 | Velocity reading, fpm | 741 | Velocity reading, fpm | 663 | Velocity reading, fpm | 604 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 58.8 | Temperature, °F | 57.9 | Temperature, °F | 58.1 | Temperature, °F | 55.4 | Temperature, °F | 53.7 | Temperature, °F | 52.5 | Temperature, °F | 51.8 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1891.6667 | Flow rate , cfm - | 1352.7778 | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 1841.6667 | Flow rate , cfm - | 2058.3333 | Flow rate , cfm - | 1841.6667 | Flow rate , cfm - | 1677.7778 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 111230 | Flow x Temperature | 78325.8333 | Flow x Temperature | 97478.8889 | Flow x Temperature | 102028.3333 | Flow x Temperature | 110532.5 | Flow x Temperature | 96687.5 | Flow x Temperature | 86908.8889 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm | 467 | Velocity reading, fpm | 487 | Velocity reading, fpm | 623 | Velocity reading, fpm | 389 | Velocity reading, fpm | 447 | Velocity reading, fpm | 487 | Velocity reading, fpm | 623 | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| 20 | Temperature, °F | 59.3 | Temperature, °F | 57.3 | Temperature, °F | 55.7 | Temperature, °F | 54.3 | Temperature, °F | 52.7 | Temperature, °F | 52.3 | Temperature, °F | 52.8 | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 2.7778 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 1297.2222 | Flow rate , cfm - | 1352.7778 | Flow rate , cfm - | 1730.5556 | Flow rate , cfm - | 1080.5556 | Flow rate , cfm - | 1241.6667 | Flow rate , cfm - | 1352.7778 | Flow rate , cfm - | 1730.5556 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 76925.2778 | Flow x Temperature | 77514.1667 | Flow x Temperature | 96391.9444 | Flow x Temperature | 58674.1667 | Flow x Temperature | 65435.8333 | Flow x Temperature | 70750.2778 | Flow x Temperature | 91373.3333 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
| Filter Row Height, inches | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm |  | Velocity reading, fpm
| Not Used | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F |  | Temperature, °F
|  | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0 | Filter area, sq.ft. | 0
|  | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0 | Flow rate , cfm - | 0
|  | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0 | Flow x Temperature | 0
Docment dimensions and other parameters in the cells with the dark yellow highlight. Take photographs and make sketches to supplement the test data and document the physical configuration of the mixed air plenum. Document the system diagram for the plenum on the results tab in the graph paper area provided. Note that if you manipulate the text boxes and lines that are already there, the data on this tab will automatically fill in and follow them.
In the test matrix, nsert the filter height and width in inches into the blue boxes for all rows and columns. The area of each filter will be calculated in the indvidual filter elements and totaled below. Enter the velocity reading and temperature observed in the yellow area. The flow rate associated with each filter element and the flow times temperature parameter will be calculated. Average velocities, total flow, average temperature and mass weighted average temperature (the true average temperature from a conservation of mass and energy standpoint) are caculated where indicated below.
Note that you need to adjusted the number of rows and columns you actually use in your filter bank modely by adjusting the values in the purple highlighted cells tif you are interested in that information. For the other calculated values, as long as the input cells (blue and yellow boxes) for rows and columns with out filters are left blank, the result will be correct.
Note that you will need to click into a cell below the yellow area and arrow key up to enter data because the yellow is created with an autoshape overlayed on the cell to higlight it. I did that so that you could use the cell formating to higlight the filter elements that are being used for the particular unit you are working on and still have the data entry cells higlighted.
If you enter the average outdoor air temperature and return air temperature that existed during the test into the orange highlighted squares, the average outdoor air flow during the test will be calculated based on conservation of mass and energy.
100% Mixed air flow x Mixed air temperature = (Outdoor air % x Outdoor temperature) + ((100-Outdoor air %)x(Return temperature))
Solving for Outdoor Air %:
Outdoor air % = (MAT- RAT)/(OAT - RAT)
The equation used is included on the tab "Mixed Air Temp Callcs". The greater the difference between the outdoor and return temperatures, the more accurate the result. To understand this consider what would happen if both the outdoor air temperature and the return air temperaure were the same value.
Ideally, you should use the same temperature sensor for measureing the outdoor air temperature and return air temperature as you used for the filter face temperatures. But if you forget to take the other two temperatures, you may be able to get a reasonable estimate of the outdoor air flow by checking trends in the control system for return air temperatures at the time of your test or by making a reasonable assumption about the return temperature. For example, it would be reasonable to assume the return temperature was about the same as the typical space temperature in the facility.
For outdoor temperature, you may be able to find trend information in the control system. Or you could use historical data from a nearby weather station that can be found in sources like the National Weather Service or Weather Underground.
The EXAMPLE tabs contain the data and results used to assess a filter bank at Le Conte Annex on the UC Berkeley Campus.

## Example Test 3 Results
Test 3 |  |  |  |  | Dan's Group | [6 empty] | Plenum Picture | Plenum System Diagram (with Test 3 results)
Test Date - |  |  |  |  | 2013-01-04
Test Start Time - |  |  |  |  | 14:25 | [10 empty] | 9,869 cfm of return air at 69.8°F |  | 2 Section, 18 Square Foot, Horizontal Opposed Blade Return Air Damper
Test Finish Time - |  |  |  |  | 15:30
Outdoor air damper size - |  |  |  |  | 31.5 |  | sq.ft.
Outdoor air damper sections - |  |  |  |  | 3
Outdoor air damper type - |  |  |  |  | Horizontal Opposed |  |  |  | Blade
Outdoor air flow - |  |  |  |  | 47244.4444 |  | cfm
Outdoor air temperature - |  |  |  |  | 52 |  | °F
Outdoor air % of total - |  |  |  |  | 82.72% |  | (Design target is 19%)
Return air damper size - |  |  |  |  | 17.5 |  | sq.ft.
Return air damper sections - |  |  |  |  | 2
Return air damper type - |  |  |  |  | Horizontal Opposed |  |  |  | Blade | [8 empty] | Filter bank
Return air flow - |  |  |  |  | 9869.4444 |  | cfm | [6 empty] | 47,244 of outdoor air at 52.°F
Return air temperature - |  |  |  |  | 69.8 |  | °F
Total air flow - |  |  |  |  | 57113.8889 |  | cfm
Outdoor air damper velocity - |  |  |  |  | 1813.1393 |  | fpm ( at measured total flow an 100% OA)
Return air damper velocity - |  |  |  |  | 2645.2749 |  | fpm (at measured total flow on MOA)
Mixed air temperature - |  |  |  |  | 55.0759 |  | °F (mass weighted; true mixed air temperature)
[5 empty] | 55.3257 |  | °F (average if measurements)
Maximum temperature - |  |  |  |  | 59.3 |  | °F | [9 empty] | 57,114 cfm of mixed air at 55.1 °F
Minimum temperature - |  |  |  |  | 51.8 |  | °F
Maximum velocity - |  |  |  |  | 945 |  | fpm
Minimum velocity - |  |  |  |  | 272 |  | fpm
Link to additional photos - |  |  |  |  | ..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-07 | [9 empty] | 3 Section, 32 Square Foot, Horizontal Opposed Blade Outdoor Air Damper
..\..\..\..\..\Technical Pictures\UCB - Le Conte Annex\2013-01-11
Link to field notes - |  |  |  |  | ..\LeConte Annex
Temperature Profile |  |  |  |  | Coldest |  |  | Hottest |  | Minimum | Maximum
| 20 | 20 | 20 | 20 | 20 | 20 | 20
20 | 57.5 | 57.3 | 57 | 55.4 | 53.9 | 52.7 | 52.5
20 | 57.5 | 57.9 | 57 | 55.9 | 53.9 | 52.7 | 52.1
20 | 58.4 | 58.1 | 57 | 57.9 | 54.1 | 52.5 | 52.5
20 | 58.8 | 57.9 | 58.1 | 55.4 | 53.7 | 52.5 | 51.8
20 | 59.3 | 57.3 | 55.7 | 54.3 | 52.7 | 52.3 | 52.8
Velocity Profile |  |  |  |  | Slowest |  |  | Fastest |  | Minimum | Maximum
| 20 | 20 | 20 | 20 | 20 | 20 | 20
20 | 331 | 350 | 272 | 643 | 779 | 643 | 632
20 | 350 | 292 | 370 | 741 | 945 | 799 | 653
20 | 800 | 604 | 429 | 760 | 858 | 643 | 701
20 | 681 | 487 | 604 | 663 | 741 | 663 | 604
20 | 467 | 487 | 623 | 389 | 447 | 487 | 623