## Monitoring Plan
[5 empty] | N.W. Satellite Office |  | Home Office
[5 empty] | 8560 North Buchanan Avenue |  | 6760 Alexander Bell Drive, Suite 200
[5 empty] | Portland, Oregon 97203 |  | Columbia, MD 21046
[5 empty] | Phone: (503) 286-1494 |  | Phone: (410) 290-0900
[5 empty] | Email: DSellers@FacilityDynamics.com |  | www.FacilityDynamics.com
Data Logging/Trending Monitoring Plan |  |  |  |  | Notice: We have provided this spreadsheet for educational purposes. We are fine with you using it as a starting point for your own spreadsheet performing a similar function or even using it as is. But you are using it at your own risk and neither FDE nor I can be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head. You can check our copyright and permissions page for more information in this regard at http://www.av8rdas.com/copyright-and-permissions.html.
Project Name
Project Number
Engineer/Technician
Date |  |  | 2017-09-25 14:06 |  | (Copy the date cells and then paste them back using "Paste Values" to lock the date)
General Notes:
1 | For situations where sensors are installed to measure temperatures in the same system, before deploying the logger, connect all sensors and launch the logger. Then put all of the sensors inside the tube in roll of toilet paper and plug the ends of the tube. Log data for 15-30 minutes to establishi the accuracy of the sensors relative to each other.
2 | For sensors measuring amps on VFD equipped motors, install the sensor upstream of the VFD. The current and voltage coming out of the VFD will be distorted relative to how the sensor/logger combination is set up to measure, so readings at a downstream location will not be accurate or meaningful.
3 | When installing sensors in a thermometer will, if possible, fill the well with water (use glycol or something that won't freeze if the well is outside). If you can't fill the well with water, then plug the opening after the sensor is installed to prevent air migration into the well, which will throw the reading off.
4 | For sensors installed in a hole drilled in a duct, once the sensor is in place, tape over the hole and sensor cable with duct tape or something similar to prevent the sensor from falling out and to seal the opening so air does not flow in and distort the reading.
5
Logger Serial Number (EMS indicates control system trend) | System | Point (use full point name for EMS Points) | Sensor | Sampling Time | Sensor Location | Logger Location | Link to Screenshots of deployed location of sensors and Logger | Notes | Data Off-loaded (Lable a column with the date of the offload and then change the fill color of the square associated with the logger if you have the data)
[7 empty] | Link to Screenshot of Launch |  | Insert Date Here | Insert Date Here | Insert Date Here | Insert Date Here | Insert Date Here | Insert Date Here | Insert Date Here | Insert Date Here
[7 empty] | Sensor 1 | Note 2
Sensor 2
Sensor 3
Sensor 4
Logger
Sensor 1
Sensor 2
Sensor 3
Sensor 4
Logger
[7 empty] | Sensor 1 | Note 4, 5, 6
Sensor 2
[7 empty] | Sensor 3 | Note 7
Sensor 4
Logger
[7 empty] | Sensor 1 | Note 8
Sensor 2
Sensor 3
Sensor 4
Logger
[7 empty] | Sensor 1 | Note 8
Sensor 2
Sensor 3
Sensor 4
Logger
[7 empty] | Sensor 1 | Note 8
Sensor 2
Sensor 3
Sensor 4
Logger
[7 empty] | Sensor 1 | Note 8
Sensor 2
Sensor 3
Sensor 4
Logger
[7 empty] | Sensor 1 | Note 4, 5, 8
Sensor 2
Sensor 3
Sensor 4
Logger
Sensor 1
Sensor 2
Sensor 3
Sensor 4
Logger
Sensor 1
Sensor 2
Sensor 3
Sensor 4
Logger
Sensor 1
Sensor 2
Sensor 3
Sensor 4
Logger
Sensor 1
Sensor 2
Sensor 3
Sensor 4
Logger
Sensor 1
Sensor 2
Sensor 3
Sensor 4
Logger
Sensor 1
Sensor 2
Sensor 3
Sensor 4
Logger
Notes
1 | Ideally it would be good for these to be in a well if the operating team is O.K. with taking their thermometers our for a while. Otherwise, under the insulation with heat transfer paste per the blog post.
2 | This should be the one closest to the cooling tower area.
3 | Ditto note 1 regarding wells. If we can't use a well, then put them in heat transfer grease with a sponge or some sort of insulation tie-wrapped over them.
4 | This moniotring plan assumes this chiller does not run, which is how they were running the plant when I was there. If that has changed then we need to revise the plan a bit.
5 | Even thought this chiller is not operating, when I was there, its auxilliary equipment was, which is the point of collecting this data. The axuilliary energy can be saved and in addition, because of the configuraiton of the plant header, I suspect some loads ares not seeing cold chilled water
6 | When I was there, the tower for this chiller was down for maintenance and repair and the fans and CW pumps were off, thus I am not monitoring them. If the tower has been repaired and returned to service, we should revisit this decision.
7 | The idea of these two sensors is to log the temperature entering the suction header at each end. I am pretty sure that under certain opeating conditions, one end (the North end) will be warmer than the other and that the warm water will be passed to the distribution system in a manner that causes the loads served by the North riser to see warmer water than the plant is producing. To really understand this you probably need to look at the system diagram and think through what happens as flows to the loads vary relative to the chiller flow rates.
8 | The idea is to document the operating state of the auxilliary equipment associated with each chiller. When I was there, the evidience suggested that the equipment remains in operation even if the machine cycles off. For the motors that these loggers are applied to, if possible, please get a motor current reading. It should be fairly constant given the system configuration.
9 | The reason for picking up the temperature and RH with this logger is that it may tell us something about the stack effect in the building given the locaiton it will likely end up in and since it has those inputs avaialble, I decided to pick them up, just to see.

## Amps from HP
HP to Amps Conversion
Inputs
Motor horsepower - | 30 | From motor nameplate or schedule
Motor voltage - | 480 | From motor nameplate or schedule
Motor power factor - | 0.82 | From motor nameplate or schedule. If not avaialble, its reasonable to assume something like .80 - .85 (larger motors will tend to have higher power factors). Or use the table below. Or use MotorMaster based on a typical selection.
Outputs
Motor kW - | 22.38 | kW
Motor amps - | 32.828 | amps

## Logger Inventory
This is the logger inventory starting with the photos I took when I removed the loggers from the case when they arrived for the Houston class
Some of these did not make it from Houston to Atlanta
Some of the items we bought for Atlanta did not make it to Columbus | [10 empty] | Picture 1 | Picture 2
Item | Count at Houston | Count at Columbus | Count at Columbus after RTU3 | Proposed Use in Columbus |  |  |  |  | Comment | Reference Picture
|  |  |  | Chiller 1 | Chiller 2 | Chiller 3 | CHW System | Running Total
Shuttle and cables | 1 | 1 | 1 |  |  |  |  | 1 | No microjack cable in Columbus | 1, 5
Hoboware | 1 | 1 | 1 |  |  |  |  | 1 |  | 1
CT-C | 3 | 8 | 8 |  |  |  |  | 8 | 100 amp, includes the 5 we bought in Atlanta | 1
U12-011 | 2 | 1 | 2 |  |  |  |  | 2 | Temp+RH, one still out on RTU 3 | 2
U12-06 | 8 | 4 | 6 | 1 | 1 | 1 |  | 3 | 4 External , 2 Still out on RTU3 | 2
U12-013 | 2 | 5 | 5 |  |  |  | 1 | 4 | Temp+RH+2 External | 2
U12-014 | 3 | 0 | 1 |  |  |  |  | 1 | Thermocouple, One still out on RTU3 | 2
CT - A | 6 | 4 | 4 |  |  |  |  | 4 | 20 amp | 3
CT - B | 6 | 3 | 4 |  |  |  |  | 4 | 50 amp | 3
Type K Thermocouple | 3 | 4 | 5 |  |  |  |  | 5 | Includes the 5 we bought in Atlanta | 4, 5
Thermistor, 50 foot cable | 13 | 12 | 12 |  |  |  | 2 | 10 |  | 6, 7
Thermistor, 20 foot cable | 9 | 18 | 19 | 4 | 4 | 2 |  | 9 | Columbus count includes 10 we bought in Atlanta | 8, 9
Misc. mounting hardware | A bunch | Not as much | Not as much |  |  |  |  | N/A
Surface temperature thermistors | 0 | 3 | [5 empty] | 0 | Not sure how we ended up with these
UX-90 Motor On-Off Loggers | 0 | 5 | 5 | 2 | 2 | 1 |  | 0 | Includes the 5 we bought in Atlanta
4-20 ma cables | 0 | 5 | 5 |  |  |  |  | 5 | Includes the 5 we bought in Atlanta
USB Cables | 0 | 5 | 5 |  |  |  |  | 5 | Includes the 5 we bought in Atlanta
UX100 Thermocouple | 0 | 2 | 2 |  |  |  |  | 2 | Includes the 5 we bought in Atlanta
UX100 Temperature and RH | 0 | 5 | 5 |  |  |  |  | 5 | Includes the 5 we bought in Atlanta
Picture 2
Picture 3
Picture 4
Picture 5
Picture 6
Picture 7
Picture 8
Picture 9