## Model Metrics
Notice: Facility Dynamics Engineering has provided this spreadsheet for educational purposes. We are fine with you using it as a starting point for your own spreadsheet performing a similar analysis or even using it as is. But you are using it at your own risk and FDE can not be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head.
Perfect Cooling Load Model Metrics
Outdoor Air, 0.4% Design Condition |  |  | Return Air Condition |  |  | Mixed Air Condition
tdb, °F | twb, °F | h, Btu/lb | tdb, °F | twb, °F | h, Btu/lb | tdb, °F | twb, °F | h, Btu/lb
93.8 | 74.3 | 38.1854 | 73 | 60.3362 | 26.871 | 78.2401 | 64.2539 | 29.6996
Cooling Coil Leaving Air Condition |  |  | Location - |  | Atlanta, Georgia
Leaving Air |  |  | Flow rate - |  | 80000 |  | cfm
tdb, °F | twb, °F | h, Btu/lb | Economizer Limit - |  | 65.7 |  | °F (see chart)
51 | 50.8 | 20.9317 | MOA - |  | 25%
Space Condition |  |  | Relationship
tdb, °F | RH,% | h, Btu/lb
72 | 0.5 | 26.3905
Design Load, 100% OA
Btu/ht |  | Tons
6211316.9663 |  | 517.6097
Design Load, Economizer
3156438.2067 |  | 263.0365
100% load = 100% OA Load
OAT Dry Bulb Economizer High Limit Set Point
Assessment
The technique involves plotting the intersection of a line representing the average climate, derived from bin data, with a line
representing the design space
enthalpy. The dry bulb temperature
at the point of intersection
becomes the setting for
the high limit.

## Perfect Load
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2021-07-11 17:58
Project Name: | Perfect chilled water load concept
Project Number:
Engineer: | David
Assumptions
1 | Atlanta is used as the example for setting the absolute temperatures, but the % load values should be fairly universal
2 | Assumed AHU Flow rate - | 80000 | cfm
3 | Cooling Coil LAT - | 51 | °F tdb
|  | 50.8 | °F twb
| Enthalpy - | 20.9317 | Btu/lb
4 | Return Air - | 73 | °F tdb
|  | 60.3362 | °F twb
| Enthalpy - | 26.871 | Btu/lb
5 | Outdoor Air - | 93.8 | °F tdb
|  | 74.3 | °F twb
| Enthalpy - | 38.1854 | Btu/lb
6 | Mixed air, design day - | 78.2401 | °F tdb
|  | 64.2539 | °F twb
|  | 29.6996 | Btu/lb
7 | MOA % - | 25%
8 | Economizer high limit - | 65.7 | °F tdb (See chart below)
9 | Economizer unit full load - | 3156438.2067 | Btu/hr based on the equation to the right
10 | 100% OA unit full load - | 6211316.9663 | Btu/hr based on the equation to the right
| Condition | Associated OAT, °F | Load |  |  | % Load per °F | Btu/hr per °F | High Limit Point, % Load | Plot Points | Comment
|  |  | Btu/hr | Tons | % Full Load
| Design Heating Condition | 20.7 | 0 | 0 | 0% |  |  | 0% | 0%
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% | 0% | 0 | 0% | 0%
| Economizer High Limit | 65.7 | 2091021.7926 | 174.2518 | 33.66% | 2.29% | 142246.3804 |  | 34.5% | Plot 100% OA Line and then tweak this value to lie on it where it crosses the high limit temperature line.
| Design Cooling Condition - Economizer System, 25% MOA | 93.8 | 3156438.2067 | 263.0365 | 50.82% | 0.6104% | 37915.1749 |  | 50.82% | Ecomizer Equipped System
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% |  |  |  | 0%
| Design Cooling Condition - 100% OA System | 93.8 | 6211316.9663 | 517.6097 | 100% | 2.336% | 145124.2282 |  | 100% | 100% OA System

## Eco HiLim Hi
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2021-07-11 17:58
Project Name: | Perfect chilled water load concept
Project Number:
Engineer: | David
Assumptions
1 | Atlanta is used as the example for setting the absolute temperatures, but the % load values should be fairly universal
2 | Assumed AHU Flow rate - | 80000 | cfm
3 | Cooling Coil LAT - | 51 | °F tdb
|  | 50.8 | °F twb
| Enthalpy - | 20.9317 | Btu/lb
4 | Return Air - | 73 | °F tdb
|  | 60.3362 | °F twb
| Enthalpy - | 26.871 | Btu/lb
5 | Outdoor Air - | 93.8 | °F tdb
|  | 74.3 | °F twb
| Enthalpy - | 38.1854 | Btu/lb
6 | Mixed air, design day - | 78.2401 | °F tdb
|  | 64.2539 | °F twb
|  | 29.6996 | Btu/lb
7 | MOA % - | 25%
8 | Economizer high limit - | 72 | °F tdb (See chart below)
9 | Economizer unit full load - | 3156438.2067 | Btu/hr based on the equation to the right
10 | 100% OA unit full load - | 6211316.9663 | Btu/hr based on the equation to the right
Economizer high limit set to 72 to simulate an inappropriately high setting
| Condition | Associated OAT, °F | Load |  |  | % Load per °F | Btu/hr per °F | High Limit Point, % Load | Plot Points | Comment
|  |  | Btu/hr | Tons | % Full Load
| Design Heating Condition | 20.7 | 0 | 0 | 0% |  |  | 0% | 0%
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% | 0% | 0 | 0% | 0%
| Economizer High Limit | 72 | 2091021.7926 | 174.2518 | 33.66% | 1.603% | 99572.4663 |  | 49% | Plot 100% OA Line and then tweak this value to lie on it.
| Design Cooling Condition - Economizer System, 25% MOA | 93.8 | 3156438.2067 | 263.0365 | 50.82% | 0.7868% | 48872.3126 |  | 50.82% | Ecomizer Equipped System
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% |  |  |  | 0%
| Design Cooling Condition - 100% OA System | 93.8 | 6211316.9663 | 517.6097 | 100% | 2.336% | 145124.2282 |  | 100% | 100% OA System

## Eco HiLim Lo
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2021-07-11 17:58
Project Name: | Perfect chilled water load concept
Project Number:
Engineer: | David
Assumptions
1 | Atlanta is used as the example for setting the absolute temperatures, but the % load values should be fairly universal
2 | Assumed AHU Flow rate - | 80000 | cfm
3 | Cooling Coil LAT - | 51 | °F tdb
|  | 50.8 | °F twb
| Enthalpy - | 20.9317 | Btu/lb
4 | Return Air - | 73 | °F tdb
|  | 60.3362 | °F twb
| Enthalpy - | 26.871 | Btu/lb
5 | Outdoor Air - | 93.8 | °F tdb
|  | 74.3 | °F twb
| Enthalpy - | 38.1854 | Btu/lb
6 | Mixed air, design day - | 78.2401 | °F tdb
|  | 64.2539 | °F twb
|  | 29.6996 | Btu/lb
7 | MOA % - | 25%
8 | Economizer high limit - | 62 | °F tdb (See chart below)
9 | Economizer unit full load - | 3156438.2067 | Btu/hr based on the equation to the right
10 | 100% OA unit full load - | 6211316.9663 | Btu/hr based on the equation to the right
Economizer high limit set to 62 to simulate an inappropriately high setting
| Condition | Associated OAT, °F | Load |  |  | % Load per °F | Btu/hr per °F | High Limit Point, % Load | Plot Points | Comment
|  |  | Btu/hr | Tons | % Full Load
| Design Heating Condition | 20.7 | 0 | 0 | 0% |  |  | 0% | 0%
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% | 0% | 0 | 0% | 0%
| Economizer High Limit | 62 | 2091021.7926 | 174.2518 | 33.66% | 3.06% | 190092.8902 |  | 26% | Plot 100% OA Line and then tweak this value to lie on it.
| Design Cooling Condition - Economizer System, 25% MOA | 93.8 | 3156438.2067 | 263.0365 | 50.82% | 0.5394% | 33503.6608 |  | 50.82% | Ecomizer Equipped System
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% |  |  |  | 0%
| Design Cooling Condition - 100% OA System | 93.8 | 6211316.9663 | 517.6097 | 100% | 2.336% | 145124.2282 |  | 100% | 100% OA System

## Perfect Load PDX
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2021-07-11 17:58
Project Name: | Perfect chilled water load concept
Project Number:
Engineer: | David
Assumptions
1 | Atlanta is used as the example for setting the absolute temperatures, but the % load values should be fairly universal
2 | Assumed AHU Flow rate - | 80000 | cfm
3 | Cooling Coil LAT - | 51 | °F tdb
|  | 50.8 | °F twb
| Enthalpy - | 20.9317 | Btu/lb
4 | Return Air - | 73 | °F tdb
|  | 60.3362 | °F twb
| Enthalpy - | 26.871 | Btu/lb
5 | Outdoor Air - | 91.2 | °F tdb
|  | 67.5 | °F twb
| Enthalpy - | 32.1636 | Btu/lb
6 | Mixed air, design day - | 77.5548 | °F tdb
|  | 62.2308 | °F twb
|  | 28.1942 | Btu/lb
7 | MOA % - | 25%
8 | Economizer high limit - | 72 | °F tdb (See chart below)
9 | Economizer unit full load - | 2614483.311 | Btu/hr based on the equation to the right
10 | 100% OA unit full load - | 4043501.4359 | Btu/hr based on the equation to the right
| Condition | Associated OAT, °F | Load |  |  | % Load per °F | Btu/hr per °F | High Limit Point, % Load | Plot Points | Comment
|  |  | Btu/hr | Tons | % Full Load
| Design Heating Condition | 23.9 | 0 | 0 | 0% |  |  | 0% | 0%
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% | 0% | 0 | 0% | 0%
| Economizer High Limit | 72 | 2091021.7926 | 174.2518 | 33.66% | 1.603% | 99572.4663 |  | 34% | Plot 100% OA Line and then tweak this value to lie on it.
| Design Cooling Condition - Economizer System, 25% MOA | 91.2 | 2614483.311 | 217.8736 | 42.09% | 0.4389% | 27263.6251 |  | 42.09% | Ecomizer Equipped System
| Design Cooling Coil LAT | 51 | 0 | 0 | 0% |  |  |  | 0%
| Design Cooling Condition - 100% OA System | 91.2 | 4043501.4359 | 336.9585 | 65.1% | 1.619% | 100584.6205 |  | 65.1% | 100% OA System
| Design Cooling Condition - 100% OA System - Atlanta | 93.8 | 6211316.9663 | 517.6097 | 100% | 2.336% | 145124.2282 |  |  | This is used for the 100% load reference to be consistent with the Atlanta Graphs

## Mixed Air Temp Calcs
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2012-04-24 13:41
Project Name: | None
Project Number: | None
Engineer: | David Sellers
Assumptions
1 | Enter appropriate data in the yellow cells in consistent units of measure …
… and read the results in the blue cells.
Note that the Supply Air Flow is the flow out of the mixed air plenum.
2 | These equations are derived from the steady flow energy equation, conservation of mass, the assumption that
for an HVAC system, air can be treated as an ideal gas, and the assumption that for an HVAC system, the constant
| pressure specific heat of air can be assumed to be constant . See this blog post for more info. |  |  |  | Av8rDAS.Wordpress.Com - Economizers - The Physics of a Mixed Air Plenum
3 | Supply air temperature and mixed air temperature are used interchangably; the supply air temperature is the temperature leaving the mixing process.
4 | Any calculation involving mixed air/supply air temperature assumes complete mixing of the two air streams feeding into the process.
Steady Flow Energy Equation
On a Rate Basis, Given the Assumptions Listed in 2 Above, the Steady Flow Energy Equation can be Reduced to this Relationship
Outdoor percentage based on outdoor air, return air, and supply air temperature
|  | Mixed air temperature (MAT) = | 51 | °F
|  | Return air temperature (RAT) = | 75 | °F
|  | Outdoor air temperature (OAT)= | 12 | °F
|  | Supply flow (SAF) = | 20000 | cfm
|  | Outdoor air flow (OA Flow) = | 7619.0476 | cfm
|  | Outdoor air percentage = | 38.1%
|  | RA Flow = | 12380.9524 | cfm
Outdoor air temperature that results in a 32°F mixed air temperature
This is simply a special case with the mixed air temperature set to 32°F
|  | Mixed air temperature (MAT) = | 32 | °F
|  | Return air temperature (RAT) = | 73 | °F
|  | Supply flow (SAF) = | 20000 | cfm
|  | Outdoor air flow (OA Flow) = | 15000 | cfm
|  | Outdoor air percentage = | 75%
|  | RA Flow = | 5000 | cfm
|  | Outdoor air temperature (OAT)= | 18.3333 | °F
Outdoor air temperature that results in a specific mixed air temperature of interest
This is simply a more general case of the preceeding equation
|  | Design mixed air temperature (MAT) = | 51 | °F
|  | Return air temperature (RAT) = | 73 | °F
|  | Supply flow (SAF) = | 20000 | cfm
|  | Outdoor air flow (OA Flow) = | 10000 | cfm
|  | Outdoor air percentage = | 50%
|  | RA Flow = | 10000 | cfm
|  | Outdoor air temperature (OAT)= | 29 | °F
Mixed air temperature created by a known outdoor air percentage, a known outdoor air temperature, and a known return air temperature
|  | Return air temperature (RAT) = | 73 | °F
|  | Outdoor air temperature (OAT)= | 93.8 | °F
|  | Supply flow (SAF) = | 20000 | cfm
|  | Outdoor air flow (OA Flow) = | 10000 | cfm
|  | Outdoor air percentage = | 50%
|  | RA Flow = | 10000 | cfm
|  | Mixed air temperature (MAT) = | 83.4 | °F

## Weather Data Source
This spreadsheet is used as the weather data source by the other load profile spreadsheets. The idea is that if you keep this in the same directory as the other spreadsheets, then you only have to load weather data here. Formulas in the other spreadsheets will reference this, including any copies you make if you are using one spreadsheet per system. To use the spreadsheet, paste the appropriate data into the columns higlighted in yellow below. The data that is there currently is an example that was created using the data export you get from the Akton Psych Chart Climate Data module (or any of the professional versions of Hands Down Software's product that include the climate data module). But you could also populate the data fields from other data sources if you did not have a professional version of one of Hands Down Software's prodcuts. For instance, you could use the legacy NREL TMY2 and TMY3 data files to fill in the wet bulb and dew point columns and then add the free kW Engineering Get Psyched plug-in to Excel and use its functions to calculate the other metrics. You could also use one of the satellite data based TMY files that NREL and other sources now provide via their free tools. Or, you could use ASOS data if you wanted to see what the patterns in the model would look like for a specific climate year rather than a normalized climate year. Note that if you use ASOS data and the year you are referencing is a leap year, you will need to insert a row in this file and in the load profile files at the appropriate location to accomodate the additional day. You may also need to make an adjustment for daylight savings time so that there are not two rows with the same date and time in the ASOS file. Inserting a row is different from adding a row at the bottom because if you insert the row, formulas that reference this sheet and graphs and charts that reverence the entire date range in the load profile will automatically expand to include the day. If you add it, you will need to edit the data selections in all charts and the formulas that reference this sheet to pick it up. One you insert the row in the load profile spreadsheet, you just need to copy and paste the formulas from the row above it into the new row to get it to populate.
Akton Psych Chart
http://www.aktonassoc.com/
PG&E Psych Chart; this is a Hands Down Software based chart that is provided as a free version but can be upgraded to the Pro version for $60.
https://av8rdas.wordpress.com/2016/11/06/a-free-electronic-psych-chart-and-how-to-use-it-to-plot-basic-hvac-processes/
NREL Legacy TMY2 and TMY3 Data
https://nsrdb.nrel.gov/data-sets/archives.html
NREL Satellite Based TMY Data
https://nsrdb.nrel.gov/
European Commission Photovoltaic Geographicak Information System
https://re.jrc.ec.europa.eu/pvg_tools/en/
Automated Surface Observation System (ASOS) Data
http://mesonet.agron.iastate.edu/request/download.phtml?network=OR_ASOS | [10 empty] | Count
Country: USA |  |  |  | 46.2 | 25 |  | 18.46 |  |  |  | 178 | Max
State: GEORGIA |  |  |  | 64 | 64 |  | 29.87 |  |  |  |  | Min
City: ATLANTA_HARTSFIELD_INTL_AP
Altitude: 1010 ft.
Month | Day | Hour | Dry Bulb | Wet Bulb | Dew Point | Humidity Ratio | Enthalpy | Density | Vapor Pressure | Specific Volume
|  |  | °F | °F | °F | gr/lb | btu/lb | lb/cu.ft. | in. HG | cu.ft./lb
January | 1 | 12AM to 1AM | 54 | 49.6 | 46 | 47.9 | 20.37 | 0.0742 | 0.31 | 13.57 | 1
January | 1 | 1AM to 2AM | 55 | 50.1 | 46 | 47.9 | 20.64 | 0.074 | 0.31 | 13.6 | 1
January | 1 | 2AM to 3AM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
January | 1 | 3AM to 4AM | 53.1 | 50.2 | 48 | 51.6 | 20.74 | 0.0743 | 0.34 | 13.56 | 1
January | 1 | 4AM to 5AM | 53.1 | 50.2 | 48 | 51.6 | 20.74 | 0.0743 | 0.34 | 13.56 | 1
January | 1 | 5AM to 6AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
January | 1 | 6AM to 7AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
January | 1 | 7AM to 8AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
January | 1 | 8AM to 9AM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
January | 1 | 9AM to 10AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
January | 1 | 10AM to 11AM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
January | 1 | 11AM to 12PM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
January | 1 | 12PM to 1PM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
January | 1 | 1PM to 2PM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
January | 1 | 2PM to 3PM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
January | 1 | 3PM to 4PM | 48 | 47.4 | 46.9 | 49.6 | 19.19 | 0.075 | 0.32 | 13.42 | 1
January | 1 | 4PM to 5PM | 45 | 44.5 | 44.1 | 44.4 | 17.65 | 0.0755 | 0.29 | 13.33 | 1
January | 1 | 5PM to 6PM | 44.1 | 43.5 | 43 | 42.5 | 17.15 | 0.0757 | 0.28 | 13.3 | 1
January | 1 | 6PM to 7PM | 44.1 | 43.1 | 42.1 | 41.1 | 16.92 | 0.0757 | 0.27 | 13.29 | 1
January | 1 | 7PM to 8PM | 44.1 | 43.1 | 42.1 | 41.1 | 16.92 | 0.0757 | 0.27 | 13.29 | 1
January | 1 | 8PM to 9PM | 43 | 42 | 41 | 39.4 | 16.4 | 0.0758 | 0.26 | 13.26 | 1
January | 1 | 9PM to 10PM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
January | 1 | 10PM to 11PM | 41 | 39.6 | 37.9 | 34.9 | 15.23 | 0.0762 | 0.23 | 13.19 | 1
January | 1 | 11PM to 12AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
January | 2 | 12AM to 1AM | 39 | 38.1 | 37 | 33.7 | 14.56 | 0.0765 | 0.22 | 13.14 | 1
January | 2 | 1AM to 2AM | 39 | 38.1 | 37 | 33.7 | 14.56 | 0.0765 | 0.22 | 13.14 | 1
January | 2 | 2AM to 3AM | 39 | 37.6 | 36 | 32.3 | 14.34 | 0.0765 | 0.21 | 13.13 | 1
January | 2 | 3AM to 4AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
January | 2 | 4AM to 5AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
January | 2 | 5AM to 6AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
January | 2 | 6AM to 7AM | 37.9 | 36.2 | 34 | 29.8 | 13.7 | 0.0767 | 0.2 | 13.1 | 1
January | 2 | 7AM to 8AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
January | 2 | 8AM to 9AM | 39 | 37.6 | 36 | 32.3 | 14.34 | 0.0765 | 0.21 | 13.13 | 1
January | 2 | 9AM to 10AM | 42.1 | 39.7 | 37 | 33.7 | 15.3 | 0.076 | 0.22 | 13.22 | 1
January | 2 | 10AM to 11AM | 44.1 | 41.1 | 37.9 | 34.9 | 15.97 | 0.0757 | 0.23 | 13.27 | 1
January | 2 | 11AM to 12PM | 45 | 41.2 | 37 | 33.7 | 16 | 0.0756 | 0.22 | 13.29 | 1
January | 2 | 12PM to 1PM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
January | 2 | 1PM to 2PM | 48 | 41.1 | 33.1 | 28.8 | 15.97 | 0.0752 | 0.19 | 13.36 | 1
January | 2 | 2PM to 3PM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
January | 2 | 3PM to 4PM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
January | 2 | 4PM to 5PM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
January | 2 | 5PM to 6PM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
January | 2 | 6PM to 7PM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
January | 2 | 7PM to 8PM | 44.1 | 39.5 | 34 | 29.8 | 15.18 | 0.0757 | 0.2 | 13.26 | 1
January | 2 | 8PM to 9PM | 43 | 38.5 | 33.1 | 28.8 | 14.76 | 0.0759 | 0.19 | 13.23 | 1
January | 2 | 9PM to 10PM | 43 | 38.1 | 32 | 27.5 | 14.57 | 0.0759 | 0.18 | 13.22 | 1
January | 2 | 10PM to 11PM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
January | 2 | 11PM to 12AM | 41 | 37.1 | 32 | 27.5 | 14.09 | 0.0762 | 0.18 | 13.17 | 1
January | 3 | 12AM to 1AM | 41 | 37.1 | 32 | 27.5 | 14.09 | 0.0762 | 0.18 | 13.17 | 1
January | 3 | 1AM to 2AM | 41 | 37.5 | 33.1 | 28.8 | 14.28 | 0.0762 | 0.19 | 13.17 | 1
January | 3 | 2AM to 3AM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
January | 3 | 3AM to 4AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
January | 3 | 4AM to 5AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
January | 3 | 5AM to 6AM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
January | 3 | 6AM to 7AM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
January | 3 | 7AM to 8AM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
January | 3 | 8AM to 9AM | 35.1 | 34.2 | 33.1 | 28.8 | 12.84 | 0.0771 | 0.19 | 13.02 | 1
January | 3 | 9AM to 10AM | 35.1 | 34.2 | 33.1 | 28.8 | 12.84 | 0.0771 | 0.19 | 13.02 | 1
January | 3 | 10AM to 11AM | 35.1 | 34.6 | 34 | 29.8 | 13 | 0.0771 | 0.2 | 13.02 | 1
January | 3 | 11AM to 12PM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
January | 3 | 12PM to 1PM | 36 | 35.6 | 35.1 | 31.1 | 13.43 | 0.077 | 0.2 | 13.05 | 1
January | 3 | 1PM to 2PM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
January | 3 | 2PM to 3PM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
January | 3 | 3PM to 4PM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
January | 3 | 4PM to 5PM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
January | 3 | 5PM to 6PM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
January | 3 | 6PM to 7PM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
January | 3 | 7PM to 8PM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
January | 3 | 8PM to 9PM | 37.9 | 37.5 | 37 | 33.7 | 14.3 | 0.0767 | 0.22 | 13.11 | 1
January | 3 | 9PM to 10PM | 39 | 38.1 | 37 | 33.7 | 14.56 | 0.0765 | 0.22 | 13.14 | 1
January | 3 | 10PM to 11PM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
January | 3 | 11PM to 12AM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
January | 4 | 12AM to 1AM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
January | 4 | 1AM to 2AM | 39 | 39 | 39 | 36.4 | 14.98 | 0.0765 | 0.24 | 13.15 | 1
January | 4 | 2AM to 3AM | 39 | 39 | 39 | 36.4 | 14.98 | 0.0765 | 0.24 | 13.15 | 1
January | 4 | 3AM to 4AM | 39 | 39 | 39 | 36.4 | 14.98 | 0.0765 | 0.24 | 13.15 | 1
January | 4 | 4AM to 5AM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
January | 4 | 5AM to 6AM | 39 | 38.1 | 37 | 33.7 | 14.56 | 0.0765 | 0.22 | 13.14 | 1
January | 4 | 6AM to 7AM | 39 | 37.6 | 36 | 32.3 | 14.34 | 0.0765 | 0.21 | 13.13 | 1
January | 4 | 7AM to 8AM | 39 | 36.8 | 34 | 29.8 | 13.96 | 0.0765 | 0.2 | 13.13 | 1
January | 4 | 8AM to 9AM | 37.9 | 35.4 | 32 | 27.5 | 13.35 | 0.0767 | 0.18 | 13.09 | 1
January | 4 | 9AM to 10AM | 39 | 36 | 32 | 27.5 | 13.61 | 0.0765 | 0.18 | 13.12 | 1
January | 4 | 10AM to 11AM | 39.9 | 35.6 | 30 | 25.1 | 13.46 | 0.0764 | 0.16 | 13.14 | 1
January | 4 | 11AM to 12PM | 41 | 35.8 | 28.9 | 23.9 | 13.53 | 0.0762 | 0.16 | 13.16 | 1
January | 4 | 12PM to 1PM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
January | 4 | 1PM to 2PM | 44.1 | 37.5 | 28.9 | 23.9 | 14.27 | 0.0758 | 0.16 | 13.24 | 1
January | 4 | 2PM to 3PM | 44.1 | 37.1 | 28 | 22.9 | 14.11 | 0.0758 | 0.15 | 13.24 | 1
January | 4 | 3PM to 4PM | 43 | 36.1 | 27 | 21.8 | 13.68 | 0.076 | 0.14 | 13.21 | 1
January | 4 | 4PM to 5PM | 42.1 | 35.3 | 26.1 | 20.9 | 13.32 | 0.0761 | 0.14 | 13.18 | 1
January | 4 | 5PM to 6PM | 41 | 34.7 | 26.1 | 20.9 | 13.06 | 0.0763 | 0.14 | 13.15 | 1
January | 4 | 6PM to 7PM | 39.9 | 34.4 | 27 | 21.8 | 12.94 | 0.0764 | 0.14 | 13.13 | 1
January | 4 | 7PM to 8PM | 37.9 | 33 | 26.1 | 20.9 | 12.32 | 0.0767 | 0.14 | 13.07 | 1
January | 4 | 8PM to 9PM | 37 | 31 | 23 | 18.1 | 11.67 | 0.0769 | 0.12 | 13.04 | 1
January | 4 | 9PM to 10PM | 36 | 30.8 | 24.1 | 19 | 11.56 | 0.0771 | 0.12 | 13.01 | 1
January | 4 | 10PM to 11PM | 35.1 | 30.3 | 24.1 | 19 | 11.34 | 0.0772 | 0.12 | 12.99 | 1
January | 4 | 11PM to 12AM | 34 | 27.8 | 18 | 14.2 | 10.34 | 0.0774 | 0.09 | 12.95 | 1
January | 5 | 12AM to 1AM | 33.1 | 27.9 | 19.9 | 15.6 | 10.34 | 0.0775 | 0.1 | 12.93 | 1
January | 5 | 1AM to 2AM | 30.9 | 25.8 | 17.1 | 13.6 | 9.51 | 0.0779 | 0.09 | 12.86 | 1
January | 5 | 2AM to 3AM | 30 | 24.7 | 15.1 | 12.3 | 9.1 | 0.078 | 0.08 | 12.84 | 1
January | 5 | 3AM to 4AM | 28.9 | 23.5 | 12.9 | 11.1 | 8.65 | 0.0782 | 0.07 | 12.81 | 1
January | 5 | 4AM to 5AM | 28 | 22.3 | 10 | 9.6 | 8.2 | 0.0784 | 0.06 | 12.78 | 1
January | 5 | 5AM to 6AM | 28 | 22.3 | 10 | 9.6 | 8.2 | 0.0784 | 0.06 | 12.78 | 1
January | 5 | 6AM to 7AM | 27 | 21.4 | 9 | 9.1 | 7.86 | 0.0785 | 0.06 | 12.75 | 1
January | 5 | 7AM to 8AM | 27 | 20.6 | 5 | 7.4 | 7.61 | 0.0786 | 0.05 | 12.74 | 1
January | 5 | 8AM to 9AM | 27 | 20.8 | 6.1 | 7.8 | 7.68 | 0.0786 | 0.05 | 12.74 | 1
January | 5 | 9AM to 10AM | 28 | 21 | 3 | 6.7 | 7.76 | 0.0784 | 0.04 | 12.77 | 1
January | 5 | 10AM to 11AM | 30 | 21.8 | 0 | 5.7 | 8.08 | 0.0781 | 0.04 | 12.82 | 1
January | 5 | 11AM to 12PM | 33.1 | 23.7 | 0 | 5.7 | 8.82 | 0.0776 | 0.04 | 12.9 | 1
January | 5 | 12PM to 1PM | 35.1 | 24.9 | 0 | 5.7 | 9.3 | 0.0773 | 0.04 | 12.95 | 1
January | 5 | 1PM to 2PM | 36 | 25.3 | -0.9 | 5.4 | 9.47 | 0.0771 | 0.04 | 12.97 | 1
January | 5 | 2PM to 3PM | 37 | 25.9 | -0.9 | 5.4 | 9.73 | 0.077 | 0.04 | 13 | 1
January | 5 | 3PM to 4PM | 36 | 25.3 | -0.9 | 5.4 | 9.47 | 0.0771 | 0.04 | 12.97 | 1
January | 5 | 4PM to 5PM | 34 | 24.4 | 1 | 6 | 9.09 | 0.0775 | 0.04 | 12.92 | 1
January | 5 | 5PM to 6PM | 32 | 22.9 | -0.9 | 5.4 | 8.52 | 0.0778 | 0.04 | 12.87 | 1
January | 5 | 6PM to 7PM | 30.9 | 22.6 | 1.9 | 6.3 | 8.4 | 0.0779 | 0.04 | 12.84 | 1
January | 5 | 7PM to 8PM | 30 | 21.9 | 1 | 6 | 8.14 | 0.0781 | 0.04 | 12.82 | 1
January | 5 | 8PM to 9PM | 28.9 | 21.3 | 1 | 6 | 7.88 | 0.0783 | 0.04 | 12.79 | 1
January | 5 | 9PM to 10PM | 28 | 21 | 3 | 6.7 | 7.76 | 0.0784 | 0.04 | 12.77 | 1
January | 5 | 10PM to 11PM | 27 | 20.5 | 3.9 | 7 | 7.55 | 0.0786 | 0.05 | 12.74 | 1
January | 5 | 11PM to 12AM | 26.1 | 19.9 | 3.9 | 7 | 7.33 | 0.0787 | 0.05 | 12.72 | 1
January | 6 | 12AM to 1AM | 27 | 20.5 | 3.9 | 7 | 7.55 | 0.0786 | 0.05 | 12.74 | 1
January | 6 | 1AM to 2AM | 26.1 | 19.9 | 3.9 | 7 | 7.33 | 0.0787 | 0.05 | 12.72 | 1
January | 6 | 2AM to 3AM | 26.1 | 19.9 | 3.9 | 7 | 7.33 | 0.0787 | 0.05 | 12.72 | 1
January | 6 | 3AM to 4AM | 26.1 | 20.3 | 6.1 | 7.8 | 7.46 | 0.0787 | 0.05 | 12.72 | 1
January | 6 | 4AM to 5AM | 25 | 19.4 | 5 | 7.4 | 7.13 | 0.0789 | 0.05 | 12.69 | 1
January | 6 | 5AM to 6AM | 24.1 | 18.8 | 5 | 7.4 | 6.92 | 0.079 | 0.05 | 12.67 | 1
January | 6 | 6AM to 7AM | 24.1 | 18.6 | 3.9 | 7 | 6.86 | 0.079 | 0.05 | 12.67 | 1
January | 6 | 7AM to 8AM | 24.1 | 18.2 | 1.9 | 6.3 | 6.75 | 0.079 | 0.04 | 12.66 | 1
January | 6 | 8AM to 9AM | 24.1 | 18.6 | 3.9 | 7 | 6.86 | 0.079 | 0.05 | 12.67 | 1
January | 6 | 9AM to 10AM | 25 | 19 | 3 | 6.7 | 7.02 | 0.0789 | 0.04 | 12.69 | 1
January | 6 | 10AM to 11AM | 26.1 | 19.5 | 1.9 | 6.3 | 7.23 | 0.0787 | 0.04 | 12.72 | 1
January | 6 | 11AM to 12PM | 28 | 21 | 3 | 6.7 | 7.76 | 0.0784 | 0.04 | 12.77 | 1
January | 6 | 12PM to 1PM | 28.9 | 21.6 | 3 | 6.7 | 7.98 | 0.0782 | 0.04 | 12.79 | 1
January | 6 | 1PM to 2PM | 30 | 22.8 | 6.1 | 7.8 | 8.41 | 0.0781 | 0.05 | 12.82 | 1
January | 6 | 2PM to 3PM | 30 | 24.7 | 15.1 | 12.3 | 9.1 | 0.078 | 0.08 | 12.84 | 1
January | 6 | 3PM to 4PM | 30.9 | 26.1 | 18 | 14.2 | 9.6 | 0.0779 | 0.09 | 12.87 | 1
January | 6 | 4PM to 5PM | 30.9 | 26.1 | 18 | 14.2 | 9.6 | 0.0779 | 0.09 | 12.87 | 1
January | 6 | 5PM to 6PM | 30.9 | 25.8 | 17.1 | 13.6 | 9.51 | 0.0779 | 0.09 | 12.86 | 1
January | 6 | 6PM to 7PM | 30 | 24.7 | 15.1 | 12.3 | 9.1 | 0.078 | 0.08 | 12.84 | 1
January | 6 | 7PM to 8PM | 30 | 24.7 | 15.1 | 12.3 | 9.1 | 0.078 | 0.08 | 12.84 | 1
January | 6 | 8PM to 9PM | 30.9 | 24.3 | 10.9 | 10 | 8.96 | 0.0779 | 0.07 | 12.85 | 1
January | 6 | 9PM to 10PM | 30.9 | 24.1 | 10 | 9.6 | 8.89 | 0.0779 | 0.06 | 12.85 | 1
January | 6 | 10PM to 11PM | 30.9 | 24.3 | 10.9 | 10 | 8.96 | 0.0779 | 0.07 | 12.85 | 1
January | 6 | 11PM to 12AM | 32 | 24.9 | 10.9 | 10 | 9.22 | 0.0777 | 0.07 | 12.88 | 1
January | 7 | 12AM to 1AM | 32 | 25.2 | 12 | 10.6 | 9.31 | 0.0777 | 0.07 | 12.88 | 1
January | 7 | 1AM to 2AM | 32 | 24.5 | 9 | 9.1 | 9.08 | 0.0777 | 0.06 | 12.88 | 1
January | 7 | 2AM to 3AM | 32 | 24.3 | 8.1 | 8.7 | 9.01 | 0.0777 | 0.06 | 12.88 | 1
January | 7 | 3AM to 4AM | 30.9 | 23.9 | 9 | 9.1 | 8.82 | 0.0779 | 0.06 | 12.85 | 1
January | 7 | 4AM to 5AM | 30.9 | 24.1 | 10 | 9.6 | 8.89 | 0.0779 | 0.06 | 12.85 | 1
January | 7 | 5AM to 6AM | 30 | 23.3 | 9 | 9.1 | 8.6 | 0.0781 | 0.06 | 12.83 | 1
January | 7 | 6AM to 7AM | 28 | 23.2 | 14 | 11.7 | 8.52 | 0.0784 | 0.08 | 12.78 | 1
January | 7 | 7AM to 8AM | 26.1 | 23.1 | 18 | 14.2 | 8.43 | 0.0787 | 0.09 | 12.74 | 1
January | 7 | 8AM to 9AM | 25 | 23.5 | 21 | 16.4 | 8.51 | 0.0788 | 0.11 | 12.72 | 1
January | 7 | 9AM to 10AM | 25 | 23.8 | 21.9 | 17.1 | 8.63 | 0.0788 | 0.11 | 12.72 | 1
January | 7 | 10AM to 11AM | 25 | 24.2 | 23 | 18.1 | 8.76 | 0.0788 | 0.12 | 12.72 | 1
January | 7 | 11AM to 12PM | 25 | 24.6 | 24.1 | 19 | 8.91 | 0.0788 | 0.12 | 12.72 | 1
January | 7 | 12PM to 1PM | 26.1 | 25.3 | 24.1 | 19 | 9.17 | 0.0786 | 0.12 | 12.75 | 1
January | 7 | 1PM to 2PM | 25 | 24.2 | 23 | 18.1 | 8.76 | 0.0788 | 0.12 | 12.72 | 1
January | 7 | 2PM to 3PM | 25 | 24.2 | 23 | 18.1 | 8.76 | 0.0788 | 0.12 | 12.72 | 1
January | 7 | 3PM to 4PM | 25 | 24.2 | 23 | 18.1 | 8.76 | 0.0788 | 0.12 | 12.72 | 1
January | 7 | 4PM to 5PM | 23 | 22.3 | 21 | 16.4 | 8.04 | 0.0791 | 0.11 | 12.67 | 1
January | 7 | 5PM to 6PM | 23 | 21.9 | 19.9 | 15.6 | 7.91 | 0.0791 | 0.1 | 12.66 | 1
January | 7 | 6PM to 7PM | 21.9 | 20.5 | 18 | 14.2 | 7.43 | 0.0793 | 0.09 | 12.63 | 1
January | 7 | 7PM to 8PM | 21.9 | 20.5 | 18 | 14.2 | 7.43 | 0.0793 | 0.09 | 12.63 | 1
January | 7 | 8PM to 9PM | 21 | 20 | 18 | 14.2 | 7.21 | 0.0795 | 0.09 | 12.61 | 1
January | 7 | 9PM to 10PM | 21 | 20.3 | 19 | 14.9 | 7.33 | 0.0795 | 0.1 | 12.61 | 1
January | 7 | 10PM to 11PM | 21 | 20.3 | 19 | 14.9 | 7.33 | 0.0795 | 0.1 | 12.61 | 1
January | 7 | 11PM to 12AM | 21 | 20.3 | 19 | 14.9 | 7.33 | 0.0795 | 0.1 | 12.61 | 1
January | 8 | 12AM to 1AM | 21 | 20.3 | 19 | 14.9 | 7.33 | 0.0795 | 0.1 | 12.61 | 1
January | 8 | 1AM to 2AM | 21.9 | 21.2 | 19.9 | 15.6 | 7.65 | 0.0793 | 0.1 | 12.63 | 1
January | 8 | 2AM to 3AM | 21.9 | 21.2 | 19.9 | 15.6 | 7.65 | 0.0793 | 0.1 | 12.63 | 1
January | 8 | 3AM to 4AM | 21.9 | 21.2 | 19.9 | 15.6 | 7.65 | 0.0793 | 0.1 | 12.63 | 1
January | 8 | 4AM to 5AM | 21.9 | 21.9 | 21.9 | 17.1 | 7.89 | 0.0793 | 0.11 | 12.64 | 1
January | 8 | 5AM to 6AM | 23 | 22.6 | 21.9 | 17.1 | 8.15 | 0.0791 | 0.11 | 12.67 | 1
January | 8 | 6AM to 7AM | 23 | 22.6 | 21.9 | 17.1 | 8.15 | 0.0791 | 0.11 | 12.67 | 1
January | 8 | 7AM to 8AM | 24.1 | 23.3 | 21.9 | 17.1 | 8.41 | 0.079 | 0.11 | 12.7 | 1
January | 8 | 8AM to 9AM | 24.1 | 23.7 | 23 | 18.1 | 8.55 | 0.079 | 0.12 | 12.7 | 1
January | 8 | 9AM to 10AM | 26.1 | 25.3 | 24.1 | 19 | 9.17 | 0.0786 | 0.12 | 12.75 | 1
January | 8 | 10AM to 11AM | 27 | 25.8 | 24.1 | 19 | 9.39 | 0.0785 | 0.12 | 12.78 | 1
January | 8 | 11AM to 12PM | 28 | 26.8 | 25 | 19.8 | 9.78 | 0.0783 | 0.13 | 12.81 | 1
January | 8 | 12PM to 1PM | 30 | 28.3 | 26.1 | 20.9 | 10.41 | 0.078 | 0.14 | 12.86 | 1
January | 8 | 1PM to 2PM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
January | 8 | 2PM to 3PM | 32 | 30.6 | 28.9 | 23.9 | 11.35 | 0.0776 | 0.16 | 12.92 | 1
January | 8 | 3PM to 4PM | 32 | 30.6 | 28.9 | 23.9 | 11.35 | 0.0776 | 0.16 | 12.92 | 1
January | 8 | 4PM to 5PM | 32 | 29.8 | 27 | 21.8 | 11.03 | 0.0777 | 0.14 | 12.92 | 1
January | 8 | 5PM to 6PM | 30.9 | 29.6 | 28 | 22.9 | 10.94 | 0.0778 | 0.15 | 12.89 | 1
January | 8 | 6PM to 7PM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
January | 8 | 7PM to 8PM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
January | 8 | 8PM to 9PM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
January | 8 | 9PM to 10PM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
January | 8 | 10PM to 11PM | 30.9 | 29.6 | 28 | 22.9 | 10.94 | 0.0778 | 0.15 | 12.89 | 1
January | 8 | 11PM to 12AM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
January | 9 | 12AM to 1AM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
January | 9 | 1AM to 2AM | 30 | 28.3 | 26.1 | 20.9 | 10.41 | 0.078 | 0.14 | 12.86 | 1
January | 9 | 2AM to 3AM | 30 | 28.3 | 26.1 | 20.9 | 10.41 | 0.078 | 0.14 | 12.86 | 1
January | 9 | 3AM to 4AM | 28.9 | 27.7 | 26.1 | 20.9 | 10.15 | 0.0782 | 0.14 | 12.83 | 1
January | 9 | 4AM to 5AM | 28 | 26.4 | 24.1 | 19 | 9.65 | 0.0783 | 0.12 | 12.8 | 1
January | 9 | 5AM to 6AM | 28 | 26.8 | 25 | 19.8 | 9.78 | 0.0783 | 0.13 | 12.81 | 1
January | 9 | 6AM to 7AM | 26.1 | 24.9 | 23 | 18.1 | 9.02 | 0.0786 | 0.12 | 12.75 | 1
January | 9 | 7AM to 8AM | 26.1 | 24.5 | 21.9 | 17.1 | 8.89 | 0.0786 | 0.11 | 12.75 | 1
January | 9 | 8AM to 9AM | 26.1 | 24.9 | 23 | 18.1 | 9.02 | 0.0786 | 0.12 | 12.75 | 1
January | 9 | 9AM to 10AM | 27 | 25.4 | 23 | 18.1 | 9.24 | 0.0785 | 0.12 | 12.77 | 1
January | 9 | 10AM to 11AM | 28 | 26 | 23 | 18.1 | 9.5 | 0.0783 | 0.12 | 12.8 | 1
January | 9 | 11AM to 12PM | 28.9 | 26.5 | 23 | 18.1 | 9.72 | 0.0782 | 0.12 | 12.83 | 1
January | 9 | 12PM to 1PM | 30.9 | 28.1 | 24.1 | 19 | 10.34 | 0.0778 | 0.12 | 12.88 | 1
January | 9 | 1PM to 2PM | 33.1 | 29.3 | 24.1 | 19 | 10.86 | 0.0775 | 0.12 | 12.94 | 1
January | 9 | 2PM to 3PM | 34 | 30.1 | 25 | 19.8 | 11.21 | 0.0774 | 0.13 | 12.96 | 1
January | 9 | 3PM to 4PM | 35.1 | 30 | 23 | 18.1 | 11.2 | 0.0772 | 0.12 | 12.99 | 1
January | 9 | 4PM to 5PM | 35.1 | 30.3 | 24.1 | 19 | 11.34 | 0.0772 | 0.12 | 12.99 | 1
January | 9 | 5PM to 6PM | 34 | 30.1 | 25 | 19.8 | 11.21 | 0.0774 | 0.13 | 12.96 | 1
January | 9 | 6PM to 7PM | 33.1 | 30 | 26.1 | 20.9 | 11.15 | 0.0775 | 0.14 | 12.94 | 1
January | 9 | 7PM to 8PM | 30.9 | 28.4 | 25 | 19.8 | 10.47 | 0.0778 | 0.13 | 12.88 | 1
January | 9 | 8PM to 9PM | 30.9 | 28.1 | 24.1 | 19 | 10.34 | 0.0778 | 0.12 | 12.88 | 1
January | 9 | 9PM to 10PM | 30 | 27.9 | 25 | 19.8 | 10.25 | 0.078 | 0.13 | 12.86 | 1
January | 9 | 10PM to 11PM | 28.9 | 27.3 | 25 | 19.8 | 9.99 | 0.0782 | 0.13 | 12.83 | 1
January | 9 | 11PM to 12AM | 28.9 | 27.3 | 25 | 19.8 | 9.99 | 0.0782 | 0.13 | 12.83 | 1
January | 10 | 12AM to 1AM | 28 | 26.8 | 25 | 19.8 | 9.78 | 0.0783 | 0.13 | 12.81 | 1
January | 10 | 1AM to 2AM | 28 | 26.4 | 24.1 | 19 | 9.65 | 0.0783 | 0.12 | 12.8 | 1
January | 10 | 2AM to 3AM | 28 | 26.4 | 24.1 | 19 | 9.65 | 0.0783 | 0.12 | 12.8 | 1
January | 10 | 3AM to 4AM | 27 | 25.8 | 24.1 | 19 | 9.39 | 0.0785 | 0.12 | 12.78 | 1
January | 10 | 4AM to 5AM | 26.1 | 24.9 | 23 | 18.1 | 9.02 | 0.0786 | 0.12 | 12.75 | 1
January | 10 | 5AM to 6AM | 24.1 | 23.7 | 23 | 18.1 | 8.55 | 0.079 | 0.12 | 12.7 | 1
January | 10 | 6AM to 7AM | 24.1 | 24.1 | 24.1 | 19 | 8.69 | 0.0789 | 0.12 | 12.7 | 1
January | 10 | 7AM to 8AM | 23 | 23 | 23 | 18.1 | 8.29 | 0.0791 | 0.12 | 12.67 | 1
January | 10 | 8AM to 9AM | 24.1 | 24.1 | 24.1 | 19 | 8.69 | 0.0789 | 0.12 | 12.7 | 1
January | 10 | 9AM to 10AM | 26.1 | 25.6 | 25 | 19.8 | 9.3 | 0.0786 | 0.13 | 12.76 | 1
January | 10 | 10AM to 11AM | 28 | 27.2 | 26.1 | 20.9 | 9.93 | 0.0783 | 0.14 | 12.81 | 1
January | 10 | 11AM to 12PM | 34 | 30.8 | 27 | 21.8 | 11.51 | 0.0773 | 0.14 | 12.97 | 1
January | 10 | 12PM to 1PM | 37 | 32.8 | 27 | 21.8 | 12.25 | 0.0769 | 0.14 | 13.05 | 1
January | 10 | 1PM to 2PM | 39 | 34.3 | 28 | 22.9 | 12.9 | 0.0766 | 0.15 | 13.1 | 1
January | 10 | 2PM to 3PM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
January | 10 | 3PM to 4PM | 41 | 35.5 | 28 | 22.9 | 13.38 | 0.0763 | 0.15 | 13.16 | 1
January | 10 | 4PM to 5PM | 39.9 | 35.2 | 28.9 | 23.9 | 13.27 | 0.0764 | 0.16 | 13.13 | 1
January | 10 | 5PM to 6PM | 37 | 33.2 | 28 | 22.9 | 12.42 | 0.0769 | 0.15 | 13.05 | 1
January | 10 | 6PM to 7PM | 35.1 | 32.1 | 28 | 22.9 | 11.94 | 0.0772 | 0.15 | 13 | 1
January | 10 | 7PM to 8PM | 32 | 29.4 | 26.1 | 20.9 | 10.89 | 0.0777 | 0.14 | 12.91 | 1
January | 10 | 8PM to 9PM | 30 | 27.9 | 25 | 19.8 | 10.25 | 0.078 | 0.13 | 12.86 | 1
January | 10 | 9PM to 10PM | 30 | 27.9 | 25 | 19.8 | 10.25 | 0.078 | 0.13 | 12.86 | 1
January | 10 | 10PM to 11PM | 28 | 27.2 | 26.1 | 20.9 | 9.93 | 0.0783 | 0.14 | 12.81 | 1
January | 10 | 11PM to 12AM | 28 | 26.8 | 25 | 19.8 | 9.78 | 0.0783 | 0.13 | 12.81 | 1
January | 11 | 12AM to 1AM | 27 | 26.1 | 25 | 19.8 | 9.51 | 0.0785 | 0.13 | 12.78 | 1
January | 11 | 1AM to 2AM | 26.1 | 25.3 | 24.1 | 19 | 9.17 | 0.0786 | 0.12 | 12.75 | 1
January | 11 | 2AM to 3AM | 27 | 26.1 | 25 | 19.8 | 9.51 | 0.0785 | 0.13 | 12.78 | 1
January | 11 | 3AM to 4AM | 28 | 26 | 23 | 18.1 | 9.5 | 0.0783 | 0.12 | 12.8 | 1
January | 11 | 4AM to 5AM | 27 | 25 | 21.9 | 17.1 | 9.1 | 0.0785 | 0.11 | 12.77 | 1
January | 11 | 5AM to 6AM | 27 | 25.4 | 23 | 18.1 | 9.24 | 0.0785 | 0.12 | 12.77 | 1
January | 11 | 6AM to 7AM | 25 | 23.5 | 21 | 16.4 | 8.51 | 0.0788 | 0.11 | 12.72 | 1
January | 11 | 7AM to 8AM | 26.1 | 24.5 | 21.9 | 17.1 | 8.89 | 0.0786 | 0.11 | 12.75 | 1
January | 11 | 8AM to 9AM | 27 | 25.4 | 23 | 18.1 | 9.24 | 0.0785 | 0.12 | 12.77 | 1
January | 11 | 9AM to 10AM | 32 | 28.3 | 23 | 18.1 | 10.46 | 0.0777 | 0.12 | 12.91 | 1
January | 11 | 10AM to 11AM | 37 | 30.7 | 21.9 | 17.1 | 11.53 | 0.0769 | 0.11 | 13.04 | 1
January | 11 | 11AM to 12PM | 41 | 33.7 | 23 | 18.1 | 12.63 | 0.0763 | 0.12 | 13.14 | 1
January | 11 | 12PM to 1PM | 41 | 34.1 | 24.1 | 19 | 12.77 | 0.0763 | 0.12 | 13.15 | 1
January | 11 | 1PM to 2PM | 44.1 | 35.1 | 21.9 | 17.1 | 13.23 | 0.0758 | 0.11 | 13.22 | 1
January | 11 | 2PM to 3PM | 44.1 | 35.1 | 21.9 | 17.1 | 13.23 | 0.0758 | 0.11 | 13.22 | 1
January | 11 | 3PM to 4PM | 45 | 35.4 | 21 | 16.4 | 13.33 | 0.0757 | 0.11 | 13.24 | 1
January | 11 | 4PM to 5PM | 43 | 34.5 | 21.9 | 17.1 | 12.97 | 0.076 | 0.11 | 13.19 | 1
January | 11 | 5PM to 6PM | 42.1 | 33.7 | 21 | 16.4 | 12.64 | 0.0761 | 0.11 | 13.17 | 1
January | 11 | 6PM to 7PM | 39.9 | 32.5 | 21 | 16.4 | 12.12 | 0.0765 | 0.11 | 13.11 | 1
January | 11 | 7PM to 8PM | 37 | 30.7 | 21.9 | 17.1 | 11.53 | 0.0769 | 0.11 | 13.04 | 1
January | 11 | 8PM to 9PM | 35.1 | 29.3 | 21 | 16.4 | 10.94 | 0.0772 | 0.11 | 12.98 | 1
January | 11 | 9PM to 10PM | 32 | 27.9 | 21.9 | 17.1 | 10.32 | 0.0777 | 0.11 | 12.9 | 1
January | 11 | 10PM to 11PM | 30.9 | 27 | 21 | 16.4 | 9.95 | 0.0779 | 0.11 | 12.87 | 1
January | 11 | 11PM to 12AM | 30 | 26.8 | 21.9 | 17.1 | 9.84 | 0.078 | 0.11 | 12.85 | 1
January | 12 | 12AM to 1AM | 28.9 | 25.9 | 21 | 16.4 | 9.47 | 0.0782 | 0.11 | 12.82 | 1
January | 12 | 1AM to 2AM | 28.9 | 25.9 | 21 | 16.4 | 9.47 | 0.0782 | 0.11 | 12.82 | 1
January | 12 | 2AM to 3AM | 27 | 24.3 | 19.9 | 15.6 | 8.86 | 0.0785 | 0.1 | 12.77 | 1
January | 12 | 3AM to 4AM | 26.1 | 23.8 | 19.9 | 15.6 | 8.65 | 0.0786 | 0.1 | 12.74 | 1
January | 12 | 4AM to 5AM | 26.1 | 23.8 | 19.9 | 15.6 | 8.65 | 0.0786 | 0.1 | 12.74 | 1
January | 12 | 5AM to 6AM | 26.1 | 24.1 | 21 | 16.4 | 8.77 | 0.0786 | 0.11 | 12.75 | 1
January | 12 | 6AM to 7AM | 26.1 | 23.5 | 19 | 14.9 | 8.55 | 0.0787 | 0.1 | 12.74 | 1
January | 12 | 7AM to 8AM | 28 | 25 | 19.9 | 15.6 | 9.12 | 0.0783 | 0.1 | 12.79 | 1
January | 12 | 8AM to 9AM | 28.9 | 25.5 | 19.9 | 15.6 | 9.34 | 0.0782 | 0.1 | 12.82 | 1
January | 12 | 9AM to 10AM | 34 | 28.7 | 21 | 16.4 | 10.68 | 0.0774 | 0.11 | 12.95 | 1
January | 12 | 10AM to 11AM | 37 | 30.4 | 21 | 16.4 | 11.42 | 0.0769 | 0.11 | 13.03 | 1
January | 12 | 11AM to 12PM | 41 | 32.8 | 19.9 | 15.6 | 12.25 | 0.0763 | 0.1 | 13.13 | 1
January | 12 | 12PM to 1PM | 43 | 34.2 | 21 | 16.4 | 12.85 | 0.076 | 0.11 | 13.19 | 1
January | 12 | 1PM to 2PM | 45 | 35.4 | 21 | 16.4 | 13.33 | 0.0757 | 0.11 | 13.24 | 1
January | 12 | 2PM to 3PM | 46.9 | 36.2 | 19.9 | 15.6 | 13.68 | 0.0754 | 0.1 | 13.29 | 1
January | 12 | 3PM to 4PM | 50 | 37.8 | 19.9 | 15.6 | 14.42 | 0.075 | 0.1 | 13.37 | 1
January | 12 | 4PM to 5PM | 48 | 37.6 | 23 | 18.1 | 14.32 | 0.0752 | 0.12 | 13.33 | 1
January | 12 | 5PM to 6PM | 46.9 | 36.7 | 21.9 | 17.1 | 13.92 | 0.0754 | 0.11 | 13.3 | 1
January | 12 | 6PM to 7PM | 43 | 34.8 | 23 | 18.1 | 13.11 | 0.076 | 0.12 | 13.19 | 1
January | 12 | 7PM to 8PM | 44.1 | 35.4 | 23 | 18.1 | 13.37 | 0.0758 | 0.12 | 13.22 | 1
January | 12 | 8PM to 9PM | 43 | 34.5 | 21.9 | 17.1 | 12.97 | 0.076 | 0.11 | 13.19 | 1
January | 12 | 9PM to 10PM | 43 | 35.2 | 24.1 | 19 | 13.25 | 0.076 | 0.12 | 13.2 | 1
January | 12 | 10PM to 11PM | 43 | 35.2 | 24.1 | 19 | 13.25 | 0.076 | 0.12 | 13.2 | 1
January | 12 | 11PM to 12AM | 44.1 | 35.8 | 24.1 | 19 | 13.51 | 0.0758 | 0.12 | 13.23 | 1
January | 13 | 12AM to 1AM | 43 | 35.8 | 26.1 | 20.9 | 13.54 | 0.076 | 0.14 | 13.2 | 1
January | 13 | 1AM to 2AM | 43 | 35.8 | 26.1 | 20.9 | 13.54 | 0.076 | 0.14 | 13.2 | 1
January | 13 | 2AM to 3AM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
January | 13 | 3AM to 4AM | 43 | 36.1 | 27 | 21.8 | 13.68 | 0.076 | 0.14 | 13.21 | 1
January | 13 | 4AM to 5AM | 39.9 | 36.5 | 32 | 27.5 | 13.83 | 0.0764 | 0.18 | 13.14 | 1
January | 13 | 5AM to 6AM | 39 | 36 | 32 | 27.5 | 13.61 | 0.0765 | 0.18 | 13.12 | 1
January | 13 | 6AM to 7AM | 39 | 36 | 32 | 27.5 | 13.61 | 0.0765 | 0.18 | 13.12 | 1
January | 13 | 7AM to 8AM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 13 | 8AM to 9AM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 13 | 9AM to 10AM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
January | 13 | 10AM to 11AM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
January | 13 | 11AM to 12PM | 44.1 | 40.3 | 36 | 32.3 | 15.56 | 0.0757 | 0.21 | 13.27 | 1
January | 13 | 12PM to 1PM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
January | 13 | 1PM to 2PM | 45 | 38.7 | 30.9 | 26.2 | 14.84 | 0.0756 | 0.17 | 13.27 | 1
January | 13 | 2PM to 3PM | 44.1 | 35.1 | 21.9 | 17.1 | 13.23 | 0.0758 | 0.11 | 13.22 | 1
January | 13 | 3PM to 4PM | 43 | 33.9 | 19.9 | 15.6 | 12.72 | 0.076 | 0.1 | 13.19 | 1
January | 13 | 4PM to 5PM | 37.9 | 29.8 | 17.1 | 13.6 | 11.2 | 0.0768 | 0.09 | 13.05 | 1
January | 13 | 5PM to 6PM | 37.9 | 29.8 | 17.1 | 13.6 | 11.2 | 0.0768 | 0.09 | 13.05 | 1
January | 13 | 6PM to 7PM | 35.1 | 28.2 | 17.1 | 13.6 | 10.5 | 0.0772 | 0.09 | 12.97 | 1
January | 13 | 7PM to 8PM | 33.1 | 26.8 | 16 | 12.9 | 9.92 | 0.0775 | 0.08 | 12.92 | 1
January | 13 | 8PM to 9PM | 30.9 | 25.3 | 15.1 | 12.3 | 9.31 | 0.0779 | 0.08 | 12.86 | 1
January | 13 | 9PM to 10PM | 28.9 | 24.3 | 16 | 12.9 | 8.92 | 0.0782 | 0.08 | 12.81 | 1
January | 13 | 10PM to 11PM | 28 | 23.5 | 15.1 | 12.3 | 8.62 | 0.0784 | 0.08 | 12.79 | 1
January | 13 | 11PM to 12AM | 26.1 | 22.3 | 15.1 | 12.3 | 8.14 | 0.0787 | 0.08 | 12.73 | 1
January | 14 | 12AM to 1AM | 25 | 21.6 | 15.1 | 12.3 | 7.88 | 0.0788 | 0.08 | 12.71 | 1
January | 14 | 1AM to 2AM | 23 | 20.1 | 14 | 11.7 | 7.31 | 0.0792 | 0.08 | 12.65 | 1
January | 14 | 2AM to 3AM | 21.9 | 19.4 | 14 | 11.7 | 7.05 | 0.0794 | 0.08 | 12.62 | 1
January | 14 | 3AM to 4AM | 21 | 18.8 | 14 | 11.7 | 6.83 | 0.0795 | 0.08 | 12.6 | 1
January | 14 | 4AM to 5AM | 21 | 18.5 | 12.9 | 11.1 | 6.74 | 0.0795 | 0.07 | 12.6 | 1
January | 14 | 5AM to 6AM | 19.9 | 17.8 | 12.9 | 11.1 | 6.48 | 0.0797 | 0.07 | 12.57 | 1
January | 14 | 6AM to 7AM | 19.9 | 17.8 | 12.9 | 11.1 | 6.48 | 0.0797 | 0.07 | 12.57 | 1
January | 14 | 7AM to 8AM | 19.9 | 17.5 | 12 | 10.6 | 6.41 | 0.0797 | 0.07 | 12.57 | 1
January | 14 | 8AM to 9AM | 23 | 19.6 | 12 | 10.6 | 7.14 | 0.0792 | 0.07 | 12.65 | 1
January | 14 | 9AM to 10AM | 28 | 22.5 | 10.9 | 10 | 8.27 | 0.0784 | 0.07 | 12.78 | 1
January | 14 | 10AM to 11AM | 28.9 | 22.6 | 9 | 9.1 | 8.34 | 0.0782 | 0.06 | 12.8 | 1
January | 14 | 11AM to 12PM | 33.1 | 25.6 | 10.9 | 10 | 9.48 | 0.0776 | 0.07 | 12.91 | 1
January | 14 | 12PM to 1PM | 36 | 27.5 | 12 | 10.6 | 10.26 | 0.0771 | 0.07 | 12.99 | 1
January | 14 | 1PM to 2PM | 36 | 27.2 | 10.9 | 10 | 10.18 | 0.0771 | 0.07 | 12.99 | 1
January | 14 | 2PM to 3PM | 39 | 28.9 | 10.9 | 10 | 10.91 | 0.0766 | 0.07 | 13.07 | 1
January | 14 | 3PM to 4PM | 39 | 28.8 | 10 | 9.6 | 10.84 | 0.0766 | 0.06 | 13.06 | 1
January | 14 | 4PM to 5PM | 37 | 27.3 | 8.1 | 8.7 | 10.23 | 0.077 | 0.06 | 13.01 | 1
January | 14 | 5PM to 6PM | 36 | 26.8 | 9 | 9.1 | 10.03 | 0.0771 | 0.06 | 12.98 | 1
January | 14 | 6PM to 7PM | 36 | 27 | 10 | 9.6 | 10.11 | 0.0771 | 0.06 | 12.98 | 1
January | 14 | 7PM to 8PM | 34 | 26.1 | 10.9 | 10 | 9.7 | 0.0774 | 0.07 | 12.93 | 1
January | 14 | 8PM to 9PM | 33.1 | 25.6 | 10.9 | 10 | 9.48 | 0.0776 | 0.07 | 12.91 | 1
January | 14 | 9PM to 10PM | 33.1 | 26 | 12.9 | 11.1 | 9.64 | 0.0776 | 0.07 | 12.91 | 1
January | 14 | 10PM to 11PM | 32 | 25.4 | 12.9 | 11.1 | 9.38 | 0.0777 | 0.07 | 12.89 | 1
January | 14 | 11PM to 12AM | 32 | 25.4 | 12.9 | 11.1 | 9.38 | 0.0777 | 0.07 | 12.89 | 1
January | 15 | 12AM to 1AM | 30 | 24.2 | 12.9 | 11.1 | 8.91 | 0.078 | 0.07 | 12.83 | 1
January | 15 | 1AM to 2AM | 28.9 | 23.5 | 12.9 | 11.1 | 8.65 | 0.0782 | 0.07 | 12.81 | 1
January | 15 | 2AM to 3AM | 28 | 23 | 12.9 | 11.1 | 8.43 | 0.0784 | 0.07 | 12.78 | 1
January | 15 | 3AM to 4AM | 27 | 22.3 | 12.9 | 11.1 | 8.17 | 0.0785 | 0.07 | 12.75 | 1
January | 15 | 4AM to 5AM | 26.1 | 21.7 | 12.9 | 11.1 | 7.95 | 0.0787 | 0.07 | 12.73 | 1
January | 15 | 5AM to 6AM | 26.1 | 21.7 | 12.9 | 11.1 | 7.95 | 0.0787 | 0.07 | 12.73 | 1
January | 15 | 6AM to 7AM | 25 | 21.1 | 12.9 | 11.1 | 7.69 | 0.0789 | 0.07 | 12.7 | 1
January | 15 | 7AM to 8AM | 24.1 | 20.8 | 14 | 11.7 | 7.57 | 0.079 | 0.08 | 12.68 | 1
January | 15 | 8AM to 9AM | 26.1 | 21.7 | 12.9 | 11.1 | 7.95 | 0.0787 | 0.07 | 12.73 | 1
January | 15 | 9AM to 10AM | 30 | 24.2 | 12.9 | 11.1 | 8.91 | 0.078 | 0.07 | 12.83 | 1
January | 15 | 10AM to 11AM | 33.1 | 26 | 12.9 | 11.1 | 9.64 | 0.0776 | 0.07 | 12.91 | 1
January | 15 | 11AM to 12PM | 35.1 | 26.7 | 10.9 | 10 | 9.96 | 0.0773 | 0.07 | 12.96 | 1
January | 15 | 12PM to 1PM | 37.9 | 28.6 | 12 | 10.6 | 10.74 | 0.0768 | 0.07 | 13.04 | 1
January | 15 | 1PM to 2PM | 41 | 30.7 | 14 | 11.7 | 11.64 | 0.0763 | 0.08 | 13.12 | 1
January | 15 | 2PM to 3PM | 43 | 31.7 | 14 | 11.7 | 12.12 | 0.076 | 0.08 | 13.17 | 1
January | 15 | 3PM to 4PM | 45 | 33.4 | 12.9 | 11.1 | 12.5 | 0.0757 | 0.07 | 13.22 | 1
January | 15 | 4PM to 5PM | 44.1 | 32.9 | 12.9 | 11.1 | 12.29 | 0.0759 | 0.07 | 13.2 | 1
January | 15 | 5PM to 6PM | 42.1 | 30.8 | 12 | 10.6 | 11.73 | 0.0762 | 0.07 | 13.15 | 1
January | 15 | 6PM to 7PM | 39 | 29.6 | 14 | 11.7 | 11.17 | 0.0766 | 0.08 | 13.07 | 1
January | 15 | 7PM to 8PM | 39 | 29.6 | 14 | 11.7 | 11.17 | 0.0766 | 0.08 | 13.07 | 1
January | 15 | 8PM to 9PM | 36 | 27.9 | 14 | 11.7 | 10.43 | 0.0771 | 0.08 | 12.99 | 1
January | 15 | 9PM to 10PM | 36 | 27.9 | 14 | 11.7 | 10.43 | 0.0771 | 0.08 | 12.99 | 1
January | 15 | 10PM to 11PM | 33.1 | 26.3 | 14 | 11.7 | 9.74 | 0.0776 | 0.08 | 12.92 | 1
January | 15 | 11PM to 12AM | 33.1 | 26.3 | 14 | 11.7 | 9.74 | 0.0776 | 0.08 | 12.92 | 1
January | 16 | 12AM to 1AM | 28.9 | 24.1 | 15.1 | 12.3 | 8.84 | 0.0782 | 0.08 | 12.81 | 1
January | 16 | 1AM to 2AM | 30 | 24.4 | 14 | 11.7 | 9 | 0.078 | 0.08 | 12.84 | 1
January | 16 | 2AM to 3AM | 28.9 | 24.1 | 15.1 | 12.3 | 8.84 | 0.0782 | 0.08 | 12.81 | 1
January | 16 | 3AM to 4AM | 28.9 | 24.1 | 15.1 | 12.3 | 8.84 | 0.0782 | 0.08 | 12.81 | 1
January | 16 | 4AM to 5AM | 27 | 22.9 | 15.1 | 12.3 | 8.36 | 0.0785 | 0.08 | 12.76 | 1
January | 16 | 5AM to 6AM | 27 | 22.9 | 15.1 | 12.3 | 8.36 | 0.0785 | 0.08 | 12.76 | 1
January | 16 | 6AM to 7AM | 27 | 22.9 | 15.1 | 12.3 | 8.36 | 0.0785 | 0.08 | 12.76 | 1
January | 16 | 7AM to 8AM | 27 | 22.9 | 15.1 | 12.3 | 8.36 | 0.0785 | 0.08 | 12.76 | 1
January | 16 | 8AM to 9AM | 28.9 | 24.1 | 15.1 | 12.3 | 8.84 | 0.0782 | 0.08 | 12.81 | 1
January | 16 | 9AM to 10AM | 35.1 | 27.9 | 16 | 12.9 | 10.4 | 0.0772 | 0.08 | 12.97 | 1
January | 16 | 10AM to 11AM | 37.9 | 29.5 | 16 | 12.9 | 11.09 | 0.0768 | 0.08 | 13.05 | 1
January | 16 | 11AM to 12PM | 42.1 | 32.2 | 15.1 | 12.3 | 12 | 0.0762 | 0.08 | 13.15 | 1
January | 16 | 12PM to 1PM | 46 | 34.5 | 15.1 | 12.3 | 12.95 | 0.0756 | 0.08 | 13.26 | 1
January | 16 | 1PM to 2PM | 48 | 35.6 | 15.1 | 12.3 | 13.43 | 0.0753 | 0.08 | 13.31 | 1
January | 16 | 2PM to 3PM | 50 | 36.9 | 16 | 12.9 | 13.99 | 0.075 | 0.08 | 13.36 | 1
January | 16 | 3PM to 4PM | 51.1 | 37.7 | 17.1 | 13.6 | 14.36 | 0.0748 | 0.09 | 13.39 | 1
January | 16 | 4PM to 5PM | 51.1 | 37.7 | 17.1 | 13.6 | 14.36 | 0.0748 | 0.09 | 13.39 | 1
January | 16 | 5PM to 6PM | 46.9 | 35.7 | 18 | 14.2 | 13.46 | 0.0754 | 0.09 | 13.29 | 1
January | 16 | 6PM to 7PM | 46 | 35.2 | 18 | 14.2 | 13.24 | 0.0756 | 0.09 | 13.26 | 1
January | 16 | 7PM to 8PM | 45 | 34.5 | 18 | 14.2 | 12.98 | 0.0757 | 0.09 | 13.23 | 1
January | 16 | 8PM to 9PM | 44.1 | 34 | 18 | 14.2 | 12.76 | 0.0758 | 0.09 | 13.21 | 1
January | 16 | 9PM to 10PM | 44.1 | 34 | 18 | 14.2 | 12.76 | 0.0758 | 0.09 | 13.21 | 1
January | 16 | 10PM to 11PM | 42.1 | 32.9 | 18 | 14.2 | 12.29 | 0.0761 | 0.09 | 13.16 | 1
January | 16 | 11PM to 12AM | 42.1 | 32.9 | 18 | 14.2 | 12.29 | 0.0761 | 0.09 | 13.16 | 1
January | 17 | 12AM to 1AM | 43 | 33.7 | 19 | 14.9 | 12.62 | 0.076 | 0.1 | 13.18 | 1
January | 17 | 1AM to 2AM | 42.1 | 34.7 | 24.1 | 19 | 13.03 | 0.0761 | 0.12 | 13.17 | 1
January | 17 | 2AM to 3AM | 42.1 | 34.7 | 24.1 | 19 | 13.03 | 0.0761 | 0.12 | 13.17 | 1
January | 17 | 3AM to 4AM | 39.9 | 33.1 | 23 | 18.1 | 12.37 | 0.0765 | 0.12 | 13.11 | 1
January | 17 | 4AM to 5AM | 41 | 33.7 | 23 | 18.1 | 12.63 | 0.0763 | 0.12 | 13.14 | 1
January | 17 | 5AM to 6AM | 41 | 34.4 | 25 | 19.8 | 12.9 | 0.0763 | 0.13 | 13.15 | 1
January | 17 | 6AM to 7AM | 37.9 | 34.1 | 28.9 | 23.9 | 12.79 | 0.0767 | 0.16 | 13.08 | 1
January | 17 | 7AM to 8AM | 36 | 34.3 | 32 | 27.5 | 12.87 | 0.077 | 0.18 | 13.04 | 1
January | 17 | 8AM to 9AM | 36 | 34.3 | 32 | 27.5 | 12.87 | 0.077 | 0.18 | 13.04 | 1
January | 17 | 9AM to 10AM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
January | 17 | 10AM to 11AM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
January | 17 | 11AM to 12PM | 37.9 | 37.5 | 37 | 33.7 | 14.3 | 0.0767 | 0.22 | 13.11 | 1
January | 17 | 12PM to 1PM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
January | 17 | 1PM to 2PM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 17 | 2PM to 3PM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 17 | 3PM to 4PM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 17 | 4PM to 5PM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
January | 17 | 5PM to 6PM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
January | 17 | 6PM to 7PM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 17 | 7PM to 8PM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 17 | 8PM to 9PM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 17 | 9PM to 10PM | 39.9 | 39.5 | 39 | 36.4 | 15.2 | 0.0763 | 0.24 | 13.17 | 1
January | 17 | 10PM to 11PM | 39.9 | 39.9 | 39.9 | 37.8 | 15.4 | 0.0763 | 0.25 | 13.17 | 1
January | 17 | 11PM to 12AM | 41 | 40.5 | 39.9 | 37.8 | 15.67 | 0.0762 | 0.25 | 13.2 | 1
January | 18 | 12AM to 1AM | 41 | 41 | 41 | 39.4 | 15.92 | 0.0761 | 0.26 | 13.21 | 1
January | 18 | 1AM to 2AM | 41 | 41 | 41 | 39.4 | 15.92 | 0.0761 | 0.26 | 13.21 | 1
January | 18 | 2AM to 3AM | 41 | 41 | 41 | 39.4 | 15.92 | 0.0761 | 0.26 | 13.21 | 1
January | 18 | 3AM to 4AM | 41 | 41 | 41 | 39.4 | 15.92 | 0.0761 | 0.26 | 13.21 | 1
January | 18 | 4AM to 5AM | 41 | 41 | 41 | 39.4 | 15.92 | 0.0761 | 0.26 | 13.21 | 1
January | 18 | 5AM to 6AM | 42.1 | 41.5 | 41 | 39.4 | 16.18 | 0.076 | 0.26 | 13.23 | 1
January | 18 | 6AM to 7AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
January | 18 | 7AM to 8AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
January | 18 | 8AM to 9AM | 43 | 43 | 43 | 42.5 | 16.88 | 0.0758 | 0.28 | 13.27 | 1
January | 18 | 9AM to 10AM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
January | 18 | 10AM to 11AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
January | 18 | 11AM to 12PM | 46.9 | 46.9 | 46.9 | 49.6 | 18.93 | 0.0752 | 0.32 | 13.39 | 1
January | 18 | 12PM to 1PM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
January | 18 | 1PM to 2PM | 48.9 | 48.9 | 48.9 | 53.4 | 20.01 | 0.0749 | 0.35 | 13.46 | 1
January | 18 | 2PM to 3PM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
January | 18 | 3PM to 4PM | 51.1 | 51.1 | 51.1 | 58 | 21.24 | 0.0745 | 0.38 | 13.53 | 1
January | 18 | 4PM to 5PM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
January | 18 | 5PM to 6PM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
January | 18 | 6PM to 7PM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
January | 18 | 7PM to 8PM | 51.1 | 51.1 | 51.1 | 58 | 21.24 | 0.0745 | 0.38 | 13.53 | 1
January | 18 | 8PM to 9PM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
January | 18 | 9PM to 10PM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
January | 18 | 10PM to 11PM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
January | 18 | 11PM to 12AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
January | 19 | 12AM to 1AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
January | 19 | 1AM to 2AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
January | 19 | 2AM to 3AM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
January | 19 | 3AM to 4AM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
January | 19 | 4AM to 5AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
January | 19 | 5AM to 6AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
January | 19 | 6AM to 7AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
January | 19 | 7AM to 8AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
January | 19 | 8AM to 9AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
January | 19 | 9AM to 10AM | 57.9 | 57.9 | 57.9 | 74.7 | 25.5 | 0.0734 | 0.48 | 13.76 | 1
January | 19 | 10AM to 11AM | 60.1 | 59.4 | 59 | 77.7 | 26.49 | 0.0731 | 0.5 | 13.83 | 1
January | 19 | 11AM to 12PM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
January | 19 | 12PM to 1PM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
January | 19 | 1PM to 2PM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
January | 19 | 2PM to 3PM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
January | 19 | 3PM to 4PM | 66 | 61.5 | 59 | 77.7 | 27.95 | 0.0723 | 0.5 | 13.99 | 1
January | 19 | 4PM to 5PM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
January | 19 | 5PM to 6PM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
January | 19 | 6PM to 7PM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
January | 19 | 7PM to 8PM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
January | 19 | 8PM to 9PM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
January | 19 | 9PM to 10PM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
January | 19 | 10PM to 11PM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
January | 19 | 11PM to 12AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
January | 20 | 12AM to 1AM | 60.1 | 59.4 | 59 | 77.7 | 26.49 | 0.0731 | 0.5 | 13.83 | 1
January | 20 | 1AM to 2AM | 59 | 56.6 | 55 | 67.2 | 24.6 | 0.0733 | 0.44 | 13.77 | 1
January | 20 | 2AM to 3AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
January | 20 | 3AM to 4AM | 55 | 53.9 | 53.1 | 62.4 | 22.89 | 0.0739 | 0.41 | 13.65 | 1
January | 20 | 4AM to 5AM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
January | 20 | 5AM to 6AM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
January | 20 | 6AM to 7AM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
January | 20 | 7AM to 8AM | 54 | 53.4 | 53.1 | 62.4 | 22.63 | 0.0741 | 0.41 | 13.62 | 1
January | 20 | 8AM to 9AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
January | 20 | 9AM to 10AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
January | 20 | 10AM to 11AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
January | 20 | 11AM to 12PM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
January | 20 | 12PM to 1PM | 60.1 | 56.4 | 54 | 64.5 | 24.45 | 0.0732 | 0.42 | 13.79 | 1
January | 20 | 1PM to 2PM | 63 | 54.8 | 48.9 | 53.4 | 23.43 | 0.0729 | 0.35 | 13.83 | 1
January | 20 | 2PM to 3PM | 64 | 55.2 | 48.9 | 53.4 | 23.69 | 0.0727 | 0.35 | 13.86 | 1
January | 20 | 3PM to 4PM | 63 | 54.8 | 48.9 | 53.4 | 23.43 | 0.0729 | 0.35 | 13.83 | 1
January | 20 | 4PM to 5PM | 62.1 | 52.5 | 45 | 45.9 | 22.04 | 0.073 | 0.3 | 13.78 | 1
January | 20 | 5PM to 6PM | 61 | 51.7 | 44.1 | 44.4 | 21.54 | 0.0732 | 0.29 | 13.75 | 1
January | 20 | 6PM to 7PM | 59 | 50.8 | 44.1 | 44.4 | 21.05 | 0.0735 | 0.29 | 13.7 | 1
January | 20 | 7PM to 8PM | 57 | 49.5 | 43 | 42.5 | 20.29 | 0.0738 | 0.28 | 13.64 | 1
January | 20 | 8PM to 9PM | 55 | 47.7 | 41 | 39.4 | 19.32 | 0.0741 | 0.26 | 13.58 | 1
January | 20 | 9PM to 10PM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
January | 20 | 10PM to 11PM | 51.1 | 45.4 | 39.9 | 37.8 | 18.11 | 0.0747 | 0.25 | 13.47 | 1
January | 20 | 11PM to 12AM | 50 | 44.1 | 37.9 | 34.9 | 17.41 | 0.0748 | 0.23 | 13.43 | 1
January | 21 | 12AM to 1AM | 48.9 | 43.2 | 37 | 33.7 | 16.96 | 0.075 | 0.22 | 13.4 | 1
January | 21 | 1AM to 2AM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
January | 21 | 2AM to 3AM | 46 | 40.1 | 33.1 | 28.8 | 15.5 | 0.0755 | 0.19 | 13.31 | 1
January | 21 | 3AM to 4AM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
January | 21 | 4AM to 5AM | 43 | 39.3 | 35.1 | 31.1 | 15.12 | 0.0759 | 0.2 | 13.23 | 1
January | 21 | 5AM to 6AM | 42.1 | 38.4 | 34 | 29.8 | 14.7 | 0.076 | 0.2 | 13.21 | 1
January | 21 | 6AM to 7AM | 41 | 37.8 | 34 | 29.8 | 14.44 | 0.0762 | 0.2 | 13.18 | 1
January | 21 | 7AM to 8AM | 41 | 37.1 | 32 | 27.5 | 14.09 | 0.0762 | 0.18 | 13.17 | 1
January | 21 | 8AM to 9AM | 41 | 36.6 | 30.9 | 26.2 | 13.88 | 0.0762 | 0.17 | 13.17 | 1
January | 21 | 9AM to 10AM | 42.1 | 37.2 | 30.9 | 26.2 | 14.14 | 0.0761 | 0.17 | 13.2 | 1
January | 21 | 10AM to 11AM | 44.1 | 38.2 | 30.9 | 26.2 | 14.62 | 0.0758 | 0.17 | 13.25 | 1
January | 21 | 11AM to 12PM | 44.1 | 38.2 | 30.9 | 26.2 | 14.62 | 0.0758 | 0.17 | 13.25 | 1
January | 21 | 12PM to 1PM | 45 | 38.7 | 30.9 | 26.2 | 14.84 | 0.0756 | 0.17 | 13.27 | 1
January | 21 | 1PM to 2PM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
January | 21 | 2PM to 3PM | 50 | 41.8 | 32 | 27.5 | 16.26 | 0.0749 | 0.18 | 13.41 | 1
January | 21 | 3PM to 4PM | 48.9 | 40.4 | 30 | 25.1 | 15.63 | 0.0751 | 0.16 | 13.37 | 1
January | 21 | 4PM to 5PM | 48 | 40.3 | 30.9 | 26.2 | 15.58 | 0.0752 | 0.17 | 13.35 | 1
January | 21 | 5PM to 6PM | 46 | 39.3 | 30.9 | 26.2 | 15.1 | 0.0755 | 0.17 | 13.3 | 1
January | 21 | 6PM to 7PM | 43 | 37.3 | 30 | 25.1 | 14.19 | 0.0759 | 0.16 | 13.22 | 1
January | 21 | 7PM to 8PM | 42.1 | 37.2 | 30.9 | 26.2 | 14.14 | 0.0761 | 0.17 | 13.2 | 1
January | 21 | 8PM to 9PM | 39.9 | 35.6 | 30 | 25.1 | 13.46 | 0.0764 | 0.16 | 13.14 | 1
January | 21 | 9PM to 10PM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
January | 21 | 10PM to 11PM | 39 | 34.3 | 28 | 22.9 | 12.9 | 0.0766 | 0.15 | 13.1 | 1
January | 21 | 11PM to 12AM | 37.9 | 33.3 | 27 | 21.8 | 12.46 | 0.0767 | 0.14 | 13.07 | 1
January | 22 | 12AM to 1AM | 37 | 32.5 | 26.1 | 20.9 | 12.11 | 0.0769 | 0.14 | 13.05 | 1
January | 22 | 1AM to 2AM | 37 | 32.5 | 26.1 | 20.9 | 12.11 | 0.0769 | 0.14 | 13.05 | 1
January | 22 | 2AM to 3AM | 35.1 | 30.7 | 25 | 19.8 | 11.47 | 0.0772 | 0.13 | 12.99 | 1
January | 22 | 3AM to 4AM | 34 | 29.8 | 24.1 | 19 | 11.08 | 0.0774 | 0.12 | 12.96 | 1
January | 22 | 4AM to 5AM | 32 | 28.7 | 24.1 | 19 | 10.6 | 0.0777 | 0.12 | 12.91 | 1
January | 22 | 5AM to 6AM | 30.9 | 28.1 | 24.1 | 19 | 10.34 | 0.0778 | 0.12 | 12.88 | 1
January | 22 | 6AM to 7AM | 30.9 | 28.1 | 24.1 | 19 | 10.34 | 0.0778 | 0.12 | 12.88 | 1
January | 22 | 7AM to 8AM | 30.9 | 28.1 | 24.1 | 19 | 10.34 | 0.0778 | 0.12 | 12.88 | 1
January | 22 | 8AM to 9AM | 34 | 29.8 | 24.1 | 19 | 11.08 | 0.0774 | 0.12 | 12.96 | 1
January | 22 | 9AM to 10AM | 37 | 31 | 23 | 18.1 | 11.67 | 0.0769 | 0.12 | 13.04 | 1
January | 22 | 10AM to 11AM | 39 | 32.9 | 24.1 | 19 | 12.3 | 0.0766 | 0.12 | 13.09 | 1
January | 22 | 11AM to 12PM | 39 | 32.9 | 24.1 | 19 | 12.3 | 0.0766 | 0.12 | 13.09 | 1
January | 22 | 12PM to 1PM | 39.9 | 33.4 | 24.1 | 19 | 12.51 | 0.0764 | 0.12 | 13.12 | 1
January | 22 | 1PM to 2PM | 39 | 33.2 | 25 | 19.8 | 12.42 | 0.0766 | 0.13 | 13.1 | 1
January | 22 | 2PM to 3PM | 41 | 34.1 | 24.1 | 19 | 12.77 | 0.0763 | 0.12 | 13.15 | 1
January | 22 | 3PM to 4PM | 41 | 33.7 | 23 | 18.1 | 12.63 | 0.0763 | 0.12 | 13.14 | 1
January | 22 | 4PM to 5PM | 39 | 32.6 | 23 | 18.1 | 12.15 | 0.0766 | 0.12 | 13.09 | 1
January | 22 | 5PM to 6PM | 37 | 30.7 | 21.9 | 17.1 | 11.53 | 0.0769 | 0.11 | 13.04 | 1
January | 22 | 6PM to 7PM | 34 | 29 | 21.9 | 17.1 | 10.8 | 0.0774 | 0.11 | 12.96 | 1
January | 22 | 7PM to 8PM | 33.1 | 28.5 | 21.9 | 17.1 | 10.58 | 0.0775 | 0.11 | 12.93 | 1
January | 22 | 8PM to 9PM | 30.9 | 27.3 | 21.9 | 17.1 | 10.06 | 0.0779 | 0.11 | 12.87 | 1
January | 22 | 9PM to 10PM | 32 | 27.9 | 21.9 | 17.1 | 10.32 | 0.0777 | 0.11 | 12.9 | 1
January | 22 | 10PM to 11PM | 28.9 | 26.5 | 23 | 18.1 | 9.72 | 0.0782 | 0.12 | 12.83 | 1
January | 22 | 11PM to 12AM | 30.9 | 27.3 | 21.9 | 17.1 | 10.06 | 0.0779 | 0.11 | 12.87 | 1
January | 23 | 12AM to 1AM | 28 | 26.4 | 24.1 | 19 | 9.65 | 0.0783 | 0.12 | 12.8 | 1
January | 23 | 1AM to 2AM | 28 | 25.6 | 21.9 | 17.1 | 9.36 | 0.0783 | 0.11 | 12.8 | 1
January | 23 | 2AM to 3AM | 28.9 | 25.9 | 21 | 16.4 | 9.47 | 0.0782 | 0.11 | 12.82 | 1
January | 23 | 3AM to 4AM | 30 | 25.9 | 19 | 14.9 | 9.5 | 0.078 | 0.1 | 12.84 | 1
January | 23 | 4AM to 5AM | 28.9 | 25.2 | 19 | 14.9 | 9.24 | 0.0782 | 0.1 | 12.82 | 1
January | 23 | 5AM to 6AM | 28.9 | 25.5 | 19.9 | 15.6 | 9.34 | 0.0782 | 0.1 | 12.82 | 1
January | 23 | 6AM to 7AM | 30 | 25.9 | 19 | 14.9 | 9.5 | 0.078 | 0.1 | 12.84 | 1
January | 23 | 7AM to 8AM | 28.9 | 25.5 | 19.9 | 15.6 | 9.34 | 0.0782 | 0.1 | 12.82 | 1
January | 23 | 8AM to 9AM | 33.1 | 28.2 | 21 | 16.4 | 10.47 | 0.0775 | 0.11 | 12.93 | 1
January | 23 | 9AM to 10AM | 37.9 | 30.6 | 19.9 | 15.6 | 11.51 | 0.0768 | 0.1 | 13.05 | 1
January | 23 | 10AM to 11AM | 41 | 31.6 | 18 | 14.2 | 12.03 | 0.0763 | 0.09 | 13.13 | 1
January | 23 | 11AM to 12PM | 45 | 34.8 | 19 | 14.9 | 13.1 | 0.0757 | 0.1 | 13.24 | 1
January | 23 | 12PM to 1PM | 46 | 35.7 | 19.9 | 15.6 | 13.46 | 0.0755 | 0.1 | 13.27 | 1
January | 23 | 1PM to 2PM | 48.9 | 37 | 19 | 14.9 | 14.05 | 0.0751 | 0.1 | 13.34 | 1
January | 23 | 2PM to 3PM | 50 | 38.1 | 21 | 16.4 | 14.55 | 0.075 | 0.11 | 13.37 | 1
January | 23 | 3PM to 4PM | 50 | 37.8 | 19.9 | 15.6 | 14.42 | 0.075 | 0.1 | 13.37 | 1
January | 23 | 4PM to 5PM | 50 | 37.8 | 19.9 | 15.6 | 14.42 | 0.075 | 0.1 | 13.37 | 1
January | 23 | 5PM to 6PM | 46.9 | 35.9 | 19 | 14.9 | 13.58 | 0.0754 | 0.1 | 13.29 | 1
January | 23 | 6PM to 7PM | 43 | 33.9 | 19.9 | 15.6 | 12.72 | 0.076 | 0.1 | 13.19 | 1
January | 23 | 7PM to 8PM | 42.1 | 33.4 | 19.9 | 15.6 | 12.51 | 0.0761 | 0.1 | 13.16 | 1
January | 23 | 8PM to 9PM | 42.1 | 33.4 | 19.9 | 15.6 | 12.51 | 0.0761 | 0.1 | 13.16 | 1
January | 23 | 9PM to 10PM | 39 | 31.5 | 21 | 16.4 | 11.9 | 0.0766 | 0.11 | 13.09 | 1
January | 23 | 10PM to 11PM | 39.9 | 32.8 | 21.9 | 17.1 | 12.23 | 0.0765 | 0.11 | 13.11 | 1
January | 23 | 11PM to 12AM | 39 | 32.2 | 21.9 | 17.1 | 12.01 | 0.0766 | 0.11 | 13.09 | 1
January | 24 | 12AM to 1AM | 37 | 30.7 | 21.9 | 17.1 | 11.53 | 0.0769 | 0.11 | 13.04 | 1
January | 24 | 1AM to 2AM | 36 | 29.8 | 21 | 16.4 | 11.16 | 0.0771 | 0.11 | 13.01 | 1
January | 24 | 2AM to 3AM | 33.1 | 28.5 | 21.9 | 17.1 | 10.58 | 0.0775 | 0.11 | 12.93 | 1
January | 24 | 3AM to 4AM | 34 | 28.7 | 21 | 16.4 | 10.68 | 0.0774 | 0.11 | 12.95 | 1
January | 24 | 4AM to 5AM | 32 | 27.6 | 21 | 16.4 | 10.21 | 0.0777 | 0.11 | 12.9 | 1
January | 24 | 5AM to 6AM | 32 | 27.9 | 21.9 | 17.1 | 10.32 | 0.0777 | 0.11 | 12.9 | 1
January | 24 | 6AM to 7AM | 32 | 27.9 | 21.9 | 17.1 | 10.32 | 0.0777 | 0.11 | 12.9 | 1
January | 24 | 7AM to 8AM | 34 | 29.8 | 24.1 | 19 | 11.08 | 0.0774 | 0.12 | 12.96 | 1
January | 24 | 8AM to 9AM | 37 | 31.4 | 24.1 | 19 | 11.82 | 0.0769 | 0.12 | 13.04 | 1
January | 24 | 9AM to 10AM | 41 | 34.4 | 25 | 19.8 | 12.9 | 0.0763 | 0.13 | 13.15 | 1
January | 24 | 10AM to 11AM | 45 | 37.6 | 28 | 22.9 | 14.33 | 0.0757 | 0.15 | 13.26 | 1
January | 24 | 11AM to 12PM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
January | 24 | 12PM to 1PM | 53.1 | 41.2 | 26.1 | 20.9 | 15.97 | 0.0745 | 0.14 | 13.47 | 1
January | 24 | 1PM to 2PM | 51.1 | 41.1 | 28.9 | 23.9 | 15.96 | 0.0747 | 0.16 | 13.42 | 1
January | 24 | 2PM to 3PM | 52 | 41.6 | 28.9 | 23.9 | 16.18 | 0.0746 | 0.16 | 13.45 | 1
January | 24 | 3PM to 4PM | 52 | 42 | 30 | 25.1 | 16.37 | 0.0746 | 0.16 | 13.45 | 1
January | 24 | 4PM to 5PM | 52 | 42 | 30 | 25.1 | 16.37 | 0.0746 | 0.16 | 13.45 | 1
January | 24 | 5PM to 6PM | 51.1 | 41.5 | 30 | 25.1 | 16.15 | 0.0747 | 0.16 | 13.43 | 1
January | 24 | 6PM to 7PM | 51.1 | 41.5 | 30 | 25.1 | 16.15 | 0.0747 | 0.16 | 13.43 | 1
January | 24 | 7PM to 8PM | 48.9 | 40.8 | 30.9 | 26.2 | 15.8 | 0.075 | 0.17 | 13.37 | 1
January | 24 | 8PM to 9PM | 48.9 | 40.4 | 30 | 25.1 | 15.63 | 0.0751 | 0.16 | 13.37 | 1
January | 24 | 9PM to 10PM | 48 | 41.1 | 33.1 | 28.8 | 15.97 | 0.0752 | 0.19 | 13.36 | 1
January | 24 | 10PM to 11PM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
January | 24 | 11PM to 12AM | 46 | 40.9 | 35.1 | 31.1 | 15.86 | 0.0754 | 0.2 | 13.31 | 1
January | 25 | 12AM to 1AM | 44.1 | 40.7 | 37 | 33.7 | 15.78 | 0.0757 | 0.22 | 13.27 | 1
January | 25 | 1AM to 2AM | 42.1 | 40.1 | 37.9 | 34.9 | 15.49 | 0.076 | 0.23 | 13.22 | 1
January | 25 | 2AM to 3AM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
January | 25 | 3AM to 4AM | 41 | 40.5 | 39.9 | 37.8 | 15.67 | 0.0762 | 0.25 | 13.2 | 1
January | 25 | 4AM to 5AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
January | 25 | 5AM to 6AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
January | 25 | 6AM to 7AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
January | 25 | 7AM to 8AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
January | 25 | 8AM to 9AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
January | 25 | 9AM to 10AM | 41 | 40 | 39 | 36.4 | 15.46 | 0.0762 | 0.24 | 13.2 | 1
January | 25 | 10AM to 11AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
January | 25 | 11AM to 12PM | 43 | 40.6 | 37.9 | 34.9 | 15.71 | 0.0759 | 0.23 | 13.25 | 1
January | 25 | 12PM to 1PM | 45 | 39.2 | 32 | 27.5 | 15.05 | 0.0756 | 0.18 | 13.27 | 1
January | 25 | 1PM to 2PM | 46.9 | 37.6 | 25 | 19.8 | 14.34 | 0.0754 | 0.13 | 13.3 | 1
January | 25 | 2PM to 3PM | 46.9 | 35.7 | 18 | 14.2 | 13.46 | 0.0754 | 0.09 | 13.29 | 1
January | 25 | 3PM to 4PM | 46.9 | 35.7 | 18 | 14.2 | 13.46 | 0.0754 | 0.09 | 13.29 | 1
January | 25 | 4PM to 5PM | 44.1 | 34.6 | 19.9 | 15.6 | 12.99 | 0.0758 | 0.1 | 13.22 | 1
January | 25 | 5PM to 6PM | 43 | 34.2 | 21 | 16.4 | 12.85 | 0.076 | 0.11 | 13.19 | 1
January | 25 | 6PM to 7PM | 41 | 34.1 | 24.1 | 19 | 12.77 | 0.0763 | 0.12 | 13.15 | 1
January | 25 | 7PM to 8PM | 39 | 33.9 | 27 | 21.8 | 12.72 | 0.0766 | 0.14 | 13.1 | 1
January | 25 | 8PM to 9PM | 37 | 32.8 | 27 | 21.8 | 12.25 | 0.0769 | 0.14 | 13.05 | 1
January | 25 | 9PM to 10PM | 36 | 30.8 | 24.1 | 19 | 11.56 | 0.0771 | 0.12 | 13.01 | 1
January | 25 | 10PM to 11PM | 35.1 | 29.3 | 21 | 16.4 | 10.94 | 0.0772 | 0.11 | 12.98 | 1
January | 25 | 11PM to 12AM | 34 | 27.8 | 18 | 14.2 | 10.34 | 0.0774 | 0.09 | 12.95 | 1
January | 26 | 12AM to 1AM | 32 | 26.4 | 17.1 | 13.6 | 9.77 | 0.0777 | 0.09 | 12.89 | 1
January | 26 | 1AM to 2AM | 28.9 | 24.1 | 15.1 | 12.3 | 8.84 | 0.0782 | 0.08 | 12.81 | 1
January | 26 | 2AM to 3AM | 27 | 22.3 | 12.9 | 11.1 | 8.17 | 0.0785 | 0.07 | 12.75 | 1
January | 26 | 3AM to 4AM | 26.1 | 21.3 | 10.9 | 10 | 7.79 | 0.0787 | 0.07 | 12.73 | 1
January | 26 | 4AM to 5AM | 24.1 | 19.6 | 9 | 9.1 | 7.17 | 0.079 | 0.06 | 12.67 | 1
January | 26 | 5AM to 6AM | 23 | 19.3 | 10.9 | 10 | 7.06 | 0.0792 | 0.07 | 12.65 | 1
January | 26 | 6AM to 7AM | 23 | 18.8 | 9 | 9.1 | 6.91 | 0.0792 | 0.06 | 12.64 | 1
January | 26 | 7AM to 8AM | 21.9 | 18.1 | 9 | 9.1 | 6.65 | 0.0794 | 0.06 | 12.62 | 1
January | 26 | 8AM to 9AM | 24.1 | 19.6 | 9 | 9.1 | 7.17 | 0.079 | 0.06 | 12.67 | 1
January | 26 | 9AM to 10AM | 26.1 | 20.6 | 8.1 | 8.7 | 7.59 | 0.0787 | 0.06 | 12.72 | 1
January | 26 | 10AM to 11AM | 27 | 20.8 | 6.1 | 7.8 | 7.68 | 0.0786 | 0.05 | 12.74 | 1
January | 26 | 11AM to 12PM | 30 | 22.9 | 7 | 8.2 | 8.47 | 0.0781 | 0.05 | 12.83 | 1
January | 26 | 12PM to 1PM | 32 | 24.1 | 7 | 8.2 | 8.94 | 0.0777 | 0.05 | 12.88 | 1
January | 26 | 1PM to 2PM | 32 | 24.3 | 8.1 | 8.7 | 9.01 | 0.0777 | 0.06 | 12.88 | 1
January | 26 | 2PM to 3PM | 36 | 26.8 | 9 | 9.1 | 10.03 | 0.0771 | 0.06 | 12.98 | 1
January | 26 | 3PM to 4PM | 36 | 26.5 | 7 | 8.2 | 9.9 | 0.0771 | 0.05 | 12.98 | 1
January | 26 | 4PM to 5PM | 36 | 26.3 | 6.1 | 7.8 | 9.84 | 0.0771 | 0.05 | 12.98 | 1
January | 26 | 5PM to 6PM | 33.1 | 24.8 | 7 | 8.2 | 9.2 | 0.0776 | 0.05 | 12.91 | 1
January | 26 | 6PM to 7PM | 30.9 | 23.7 | 8.1 | 8.7 | 8.76 | 0.0779 | 0.06 | 12.85 | 1
January | 26 | 7PM to 8PM | 30 | 23.3 | 9 | 9.1 | 8.6 | 0.0781 | 0.06 | 12.83 | 1
January | 26 | 8PM to 9PM | 28.9 | 22.9 | 10 | 9.6 | 8.42 | 0.0782 | 0.06 | 12.8 | 1
January | 26 | 9PM to 10PM | 28 | 22.5 | 10.9 | 10 | 8.27 | 0.0784 | 0.07 | 12.78 | 1
January | 26 | 10PM to 11PM | 27 | 21.6 | 10 | 9.6 | 7.94 | 0.0785 | 0.06 | 12.75 | 1
January | 26 | 11PM to 12AM | 25 | 20.6 | 10.9 | 10 | 7.53 | 0.0789 | 0.07 | 12.7 | 1
January | 27 | 12AM to 1AM | 25 | 20.6 | 10.9 | 10 | 7.53 | 0.0789 | 0.07 | 12.7 | 1
January | 27 | 1AM to 2AM | 24.1 | 20 | 10.9 | 10 | 7.32 | 0.079 | 0.07 | 12.67 | 1
January | 27 | 2AM to 3AM | 23 | 19.3 | 10.9 | 10 | 7.06 | 0.0792 | 0.07 | 12.65 | 1
January | 27 | 3AM to 4AM | 23 | 19.3 | 10.9 | 10 | 7.06 | 0.0792 | 0.07 | 12.65 | 1
January | 27 | 4AM to 5AM | 21.9 | 18.9 | 12 | 10.6 | 6.88 | 0.0794 | 0.07 | 12.62 | 1
January | 27 | 5AM to 6AM | 21 | 18.3 | 12 | 10.6 | 6.67 | 0.0795 | 0.07 | 12.6 | 1
January | 27 | 6AM to 7AM | 19.9 | 17.5 | 12 | 10.6 | 6.41 | 0.0797 | 0.07 | 12.57 | 1
January | 27 | 7AM to 8AM | 19.9 | 17.5 | 12 | 10.6 | 6.41 | 0.0797 | 0.07 | 12.57 | 1
January | 27 | 8AM to 9AM | 23 | 19.8 | 12.9 | 11.1 | 7.22 | 0.0792 | 0.07 | 12.65 | 1
January | 27 | 9AM to 10AM | 26.1 | 21.5 | 12 | 10.6 | 7.88 | 0.0787 | 0.07 | 12.73 | 1
January | 27 | 10AM to 11AM | 28.9 | 23.3 | 12 | 10.6 | 8.57 | 0.0782 | 0.07 | 12.8 | 1
January | 27 | 11AM to 12PM | 30.9 | 23.7 | 8.1 | 8.7 | 8.76 | 0.0779 | 0.06 | 12.85 | 1
January | 27 | 12PM to 1PM | 34 | 25.5 | 8.1 | 8.7 | 9.49 | 0.0774 | 0.06 | 12.93 | 1
January | 27 | 1PM to 2PM | 37 | 27.1 | 7 | 8.2 | 10.16 | 0.077 | 0.05 | 13.01 | 1
January | 27 | 2PM to 3PM | 39 | 28.1 | 6.1 | 7.8 | 10.58 | 0.0767 | 0.05 | 13.06 | 1
January | 27 | 3PM to 4PM | 39.9 | 28 | 1.9 | 6.3 | 10.56 | 0.0765 | 0.04 | 13.08 | 1
January | 27 | 4PM to 5PM | 39.9 | 28.4 | 5 | 7.4 | 10.73 | 0.0765 | 0.05 | 13.08 | 1
January | 27 | 5PM to 6PM | 37.9 | 27.3 | 5 | 7.4 | 10.25 | 0.0768 | 0.05 | 13.03 | 1
January | 27 | 6PM to 7PM | 35.1 | 26.1 | 8.1 | 8.7 | 9.75 | 0.0773 | 0.06 | 12.96 | 1
January | 27 | 7PM to 8PM | 34 | 25.7 | 9 | 9.1 | 9.55 | 0.0774 | 0.06 | 12.93 | 1
January | 27 | 8PM to 9PM | 32 | 24.9 | 10.9 | 10 | 9.22 | 0.0777 | 0.07 | 12.88 | 1
January | 27 | 9PM to 10PM | 30.9 | 24.3 | 10.9 | 10 | 8.96 | 0.0779 | 0.07 | 12.85 | 1
January | 27 | 10PM to 11PM | 30 | 23.7 | 10.9 | 10 | 8.75 | 0.0781 | 0.07 | 12.83 | 1
January | 27 | 11PM to 12AM | 28 | 23 | 12.9 | 11.1 | 8.43 | 0.0784 | 0.07 | 12.78 | 1
January | 28 | 12AM to 1AM | 28.9 | 23.3 | 12 | 10.6 | 8.57 | 0.0782 | 0.07 | 12.8 | 1
January | 28 | 1AM to 2AM | 28 | 23 | 12.9 | 11.1 | 8.43 | 0.0784 | 0.07 | 12.78 | 1
January | 28 | 2AM to 3AM | 27 | 22.3 | 12.9 | 11.1 | 8.17 | 0.0785 | 0.07 | 12.75 | 1
January | 28 | 3AM to 4AM | 26.1 | 22 | 14 | 11.7 | 8.05 | 0.0787 | 0.08 | 12.73 | 1
January | 28 | 4AM to 5AM | 26.1 | 22 | 14 | 11.7 | 8.05 | 0.0787 | 0.08 | 12.73 | 1
January | 28 | 5AM to 6AM | 26.1 | 22 | 14 | 11.7 | 8.05 | 0.0787 | 0.08 | 12.73 | 1
January | 28 | 6AM to 7AM | 26.1 | 22 | 14 | 11.7 | 8.05 | 0.0787 | 0.08 | 12.73 | 1
January | 28 | 7AM to 8AM | 24.1 | 21.3 | 16 | 12.9 | 7.75 | 0.079 | 0.08 | 12.68 | 1
January | 28 | 8AM to 9AM | 28.9 | 24.6 | 17.1 | 13.6 | 9.03 | 0.0782 | 0.09 | 12.81 | 1
January | 28 | 9AM to 10AM | 35.1 | 28.4 | 18 | 14.2 | 10.6 | 0.0772 | 0.09 | 12.97 | 1
January | 28 | 10AM to 11AM | 41 | 31.9 | 19 | 14.9 | 12.15 | 0.0763 | 0.1 | 13.13 | 1
January | 28 | 11AM to 12PM | 44.1 | 34.6 | 19.9 | 15.6 | 12.99 | 0.0758 | 0.1 | 13.22 | 1
January | 28 | 12PM to 1PM | 46.9 | 36.2 | 19.9 | 15.6 | 13.68 | 0.0754 | 0.1 | 13.29 | 1
January | 28 | 1PM to 2PM | 51.1 | 38.7 | 21 | 16.4 | 14.81 | 0.0748 | 0.11 | 13.4 | 1
January | 28 | 2PM to 3PM | 54 | 39.7 | 19 | 14.9 | 15.27 | 0.0744 | 0.1 | 13.47 | 1
January | 28 | 3PM to 4PM | 54 | 39.7 | 19 | 14.9 | 15.27 | 0.0744 | 0.1 | 13.47 | 1
January | 28 | 4PM to 5PM | 54 | 39.7 | 19 | 14.9 | 15.27 | 0.0744 | 0.1 | 13.47 | 1
January | 28 | 5PM to 6PM | 51.1 | 38.2 | 19 | 14.9 | 14.57 | 0.0748 | 0.1 | 13.4 | 1
January | 28 | 6PM to 7PM | 48 | 36.5 | 19 | 14.9 | 13.84 | 0.0753 | 0.1 | 13.32 | 1
January | 28 | 7PM to 8PM | 48 | 36.7 | 19.9 | 15.6 | 13.94 | 0.0752 | 0.1 | 13.32 | 1
January | 28 | 8PM to 9PM | 45 | 35.1 | 19.9 | 15.6 | 13.2 | 0.0757 | 0.1 | 13.24 | 1
January | 28 | 9PM to 10PM | 42.1 | 33.4 | 19.9 | 15.6 | 12.51 | 0.0761 | 0.1 | 13.16 | 1
January | 28 | 10PM to 11PM | 42.1 | 33.4 | 19.9 | 15.6 | 12.51 | 0.0761 | 0.1 | 13.16 | 1
January | 28 | 11PM to 12AM | 41 | 32.8 | 19.9 | 15.6 | 12.25 | 0.0763 | 0.1 | 13.13 | 1
January | 29 | 12AM to 1AM | 39.9 | 31.6 | 19.9 | 15.6 | 11.99 | 0.0765 | 0.1 | 13.11 | 1
January | 29 | 1AM to 2AM | 37 | 30.1 | 19.9 | 15.6 | 11.29 | 0.0769 | 0.1 | 13.03 | 1
January | 29 | 2AM to 3AM | 35.1 | 29 | 19.9 | 15.6 | 10.82 | 0.0772 | 0.1 | 12.98 | 1
January | 29 | 3AM to 4AM | 33.1 | 28.9 | 23 | 18.1 | 10.72 | 0.0775 | 0.12 | 12.93 | 1
January | 29 | 4AM to 5AM | 33.1 | 28.5 | 21.9 | 17.1 | 10.58 | 0.0775 | 0.11 | 12.93 | 1
January | 29 | 5AM to 6AM | 33.1 | 28.5 | 21.9 | 17.1 | 10.58 | 0.0775 | 0.11 | 12.93 | 1
January | 29 | 6AM to 7AM | 36 | 30.1 | 21.9 | 17.1 | 11.27 | 0.0771 | 0.11 | 13.01 | 1
January | 29 | 7AM to 8AM | 36 | 30.1 | 21.9 | 17.1 | 11.27 | 0.0771 | 0.11 | 13.01 | 1
January | 29 | 8AM to 9AM | 41 | 33.7 | 23 | 18.1 | 12.63 | 0.0763 | 0.12 | 13.14 | 1
January | 29 | 9AM to 10AM | 48 | 37.9 | 24.1 | 19 | 14.47 | 0.0752 | 0.12 | 13.33 | 1
January | 29 | 10AM to 11AM | 53.1 | 40.6 | 24.1 | 19 | 15.68 | 0.0745 | 0.12 | 13.46 | 1
January | 29 | 11AM to 12PM | 55 | 41.6 | 24.1 | 19 | 16.16 | 0.0742 | 0.12 | 13.51 | 1
January | 29 | 12PM to 1PM | 57 | 42.6 | 24.1 | 19 | 16.64 | 0.0739 | 0.12 | 13.57 | 1
January | 29 | 1PM to 2PM | 59 | 42.7 | 21 | 16.4 | 16.71 | 0.0736 | 0.11 | 13.61 | 1
January | 29 | 2PM to 3PM | 60.1 | 43 | 19.9 | 15.6 | 16.85 | 0.0735 | 0.1 | 13.64 | 1
January | 29 | 3PM to 4PM | 62.1 | 43.5 | 18 | 14.2 | 17.1 | 0.0732 | 0.09 | 13.68 | 1
January | 29 | 4PM to 5PM | 60.1 | 42.5 | 18 | 14.2 | 16.62 | 0.0735 | 0.09 | 13.63 | 1
January | 29 | 5PM to 6PM | 57.9 | 41.9 | 19.9 | 15.6 | 16.33 | 0.0738 | 0.1 | 13.58 | 1
January | 29 | 6PM to 7PM | 55.9 | 41.2 | 21 | 16.4 | 15.98 | 0.0741 | 0.11 | 13.53 | 1
January | 29 | 7PM to 8PM | 54 | 39.9 | 19.9 | 15.6 | 15.37 | 0.0744 | 0.1 | 13.47 | 1
January | 29 | 8PM to 9PM | 50 | 37.8 | 19.9 | 15.6 | 14.42 | 0.075 | 0.1 | 13.37 | 1
January | 29 | 9PM to 10PM | 48.9 | 37.8 | 21.9 | 17.1 | 14.4 | 0.0751 | 0.11 | 13.35 | 1
January | 29 | 10PM to 11PM | 46 | 36.2 | 21.9 | 17.1 | 13.7 | 0.0755 | 0.11 | 13.27 | 1
January | 29 | 11PM to 12AM | 46 | 36.5 | 23 | 18.1 | 13.84 | 0.0755 | 0.12 | 13.27 | 1
January | 30 | 12AM to 1AM | 42.1 | 34.3 | 23 | 18.1 | 12.89 | 0.0761 | 0.12 | 13.17 | 1
January | 30 | 1AM to 2AM | 42.1 | 34.3 | 23 | 18.1 | 12.89 | 0.0761 | 0.12 | 13.17 | 1
January | 30 | 2AM to 3AM | 39 | 32.9 | 24.1 | 19 | 12.3 | 0.0766 | 0.12 | 13.09 | 1
January | 30 | 3AM to 4AM | 41 | 33.7 | 23 | 18.1 | 12.63 | 0.0763 | 0.12 | 13.14 | 1
January | 30 | 4AM to 5AM | 39.9 | 33.4 | 24.1 | 19 | 12.51 | 0.0764 | 0.12 | 13.12 | 1
January | 30 | 5AM to 6AM | 37.9 | 31.9 | 24.1 | 19 | 12.04 | 0.0767 | 0.12 | 13.06 | 1
January | 30 | 6AM to 7AM | 39 | 33.9 | 27 | 21.8 | 12.72 | 0.0766 | 0.14 | 13.1 | 1
January | 30 | 7AM to 8AM | 39.9 | 36 | 30.9 | 26.2 | 13.62 | 0.0764 | 0.17 | 13.14 | 1
January | 30 | 8AM to 9AM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
January | 30 | 9AM to 10AM | 50 | 44.5 | 39 | 36.4 | 17.64 | 0.0748 | 0.24 | 13.43 | 1
January | 30 | 10AM to 11AM | 57.9 | 49.5 | 42.1 | 41.1 | 20.28 | 0.0736 | 0.27 | 13.66 | 1
January | 30 | 11AM to 12PM | 61 | 49.9 | 39.9 | 37.8 | 20.51 | 0.0732 | 0.25 | 13.73 | 1
January | 30 | 12PM to 1PM | 62.1 | 50.8 | 41 | 39.4 | 21.02 | 0.0731 | 0.26 | 13.76 | 1
January | 30 | 1PM to 2PM | 62.1 | 50.4 | 39.9 | 37.8 | 20.77 | 0.0731 | 0.25 | 13.76 | 1
January | 30 | 2PM to 3PM | 62.1 | 50.8 | 41 | 39.4 | 21.02 | 0.0731 | 0.26 | 13.76 | 1
January | 30 | 3PM to 4PM | 62.1 | 50.8 | 41 | 39.4 | 21.02 | 0.0731 | 0.26 | 13.76 | 1
January | 30 | 4PM to 5PM | 62.1 | 50.8 | 41 | 39.4 | 21.02 | 0.0731 | 0.26 | 13.76 | 1
January | 30 | 5PM to 6PM | 60.1 | 49.9 | 41 | 39.4 | 20.54 | 0.0734 | 0.26 | 13.71 | 1
January | 30 | 6PM to 7PM | 57.9 | 49 | 41 | 39.4 | 20.02 | 0.0737 | 0.26 | 13.65 | 1
January | 30 | 7PM to 8PM | 57.9 | 49.5 | 42.1 | 41.1 | 20.28 | 0.0736 | 0.27 | 13.66 | 1
January | 30 | 8PM to 9PM | 57 | 49.1 | 42.1 | 41.1 | 20.07 | 0.0738 | 0.27 | 13.63 | 1
January | 30 | 9PM to 10PM | 55 | 48.6 | 43 | 42.5 | 19.81 | 0.0741 | 0.28 | 13.59 | 1
January | 30 | 10PM to 11PM | 53.1 | 47.7 | 43 | 42.5 | 19.33 | 0.0743 | 0.28 | 13.53 | 1
January | 30 | 11PM to 12AM | 53.1 | 48.2 | 44.1 | 44.4 | 19.61 | 0.0743 | 0.29 | 13.54 | 1
January | 31 | 12AM to 1AM | 51.1 | 47.3 | 44.1 | 44.4 | 19.13 | 0.0746 | 0.29 | 13.49 | 1
January | 31 | 1AM to 2AM | 51.1 | 47.3 | 44.1 | 44.4 | 19.13 | 0.0746 | 0.29 | 13.49 | 1
January | 31 | 2AM to 3AM | 50 | 46.9 | 44.1 | 44.4 | 18.87 | 0.0748 | 0.29 | 13.46 | 1
January | 31 | 3AM to 4AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
January | 31 | 4AM to 5AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
January | 31 | 5AM to 6AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
January | 31 | 6AM to 7AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
January | 31 | 7AM to 8AM | 51.1 | 48.3 | 46 | 47.9 | 19.67 | 0.0746 | 0.31 | 13.5 | 1
January | 31 | 8AM to 9AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
January | 31 | 9AM to 10AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
January | 31 | 10AM to 11AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
January | 31 | 11AM to 12PM | 63 | 55.9 | 51.1 | 58 | 24.13 | 0.0728 | 0.38 | 13.84 | 1
January | 31 | 12PM to 1PM | 66.9 | 56.3 | 48.9 | 53.4 | 24.39 | 0.0723 | 0.35 | 13.93 | 1
January | 31 | 1PM to 2PM | 69.1 | 55.8 | 46 | 47.9 | 24.05 | 0.0721 | 0.31 | 13.97 | 1
January | 31 | 2PM to 3PM | 70 | 55.3 | 44.1 | 44.4 | 23.72 | 0.072 | 0.29 | 13.99 | 1
January | 31 | 3PM to 4PM | 68 | 56.3 | 48 | 51.6 | 24.37 | 0.0722 | 0.34 | 13.96 | 1
January | 31 | 4PM to 5PM | 66.9 | 55.9 | 48 | 51.6 | 24.11 | 0.0723 | 0.34 | 13.93 | 1
January | 31 | 5PM to 6PM | 66 | 55.5 | 48 | 51.6 | 23.89 | 0.0724 | 0.34 | 13.9 | 1
January | 31 | 6PM to 7PM | 64 | 54.8 | 48 | 51.6 | 23.41 | 0.0727 | 0.34 | 13.85 | 1
January | 31 | 7PM to 8PM | 64 | 54.8 | 48 | 51.6 | 23.41 | 0.0727 | 0.34 | 13.85 | 1
January | 31 | 8PM to 9PM | 63 | 54.3 | 48 | 51.6 | 23.15 | 0.0729 | 0.34 | 13.82 | 1
January | 31 | 9PM to 10PM | 58.8 | 50.3 | 43 | 42.5 | 20.73 | 0.0735 | 0.28 | 13.69 | 1
January | 31 | 10PM to 11PM | 54.7 | 46.3 | 37.9 | 34.9 | 18.54 | 0.0742 | 0.23 | 13.55 | 1
January | 31 | 11PM to 12AM | 50.5 | 42.3 | 32.9 | 28.5 | 16.55 | 0.0748 | 0.19 | 13.42 | 1
February | 1 | 12AM to 1AM | 46.4 | 38.4 | 28.2 | 23.1 | 14.71 | 0.0754 | 0.15 | 13.3 | 1
February | 1 | 1AM to 2AM | 42.3 | 34.5 | 23.2 | 18.2 | 12.96 | 0.0761 | 0.12 | 13.18 | 1
February | 1 | 2AM to 3AM | 38.1 | 30.2 | 18.1 | 14.3 | 11.35 | 0.0768 | 0.09 | 13.06 | 1
February | 1 | 3AM to 4AM | 34 | 26.5 | 12.9 | 11.1 | 9.86 | 0.0774 | 0.07 | 12.94 | 1
February | 1 | 4AM to 5AM | 34 | 26.8 | 14 | 11.7 | 9.95 | 0.0774 | 0.08 | 12.94 | 1
February | 1 | 5AM to 6AM | 34 | 27.3 | 16 | 12.9 | 10.14 | 0.0774 | 0.08 | 12.94 | 1
February | 1 | 6AM to 7AM | 32 | 28.3 | 23 | 18.1 | 10.46 | 0.0777 | 0.12 | 12.91 | 1
February | 1 | 7AM to 8AM | 30.9 | 28.1 | 24.1 | 19 | 10.34 | 0.0778 | 0.12 | 12.88 | 1
February | 1 | 8AM to 9AM | 30.9 | 29.2 | 27 | 21.8 | 10.77 | 0.0778 | 0.14 | 12.89 | 1
February | 1 | 9AM to 10AM | 32 | 30.2 | 28 | 22.9 | 11.2 | 0.0777 | 0.15 | 12.92 | 1
February | 1 | 10AM to 11AM | 32 | 31.5 | 30.9 | 26.2 | 11.71 | 0.0776 | 0.17 | 12.93 | 1
February | 1 | 11AM to 12PM | 33.1 | 32.6 | 32 | 27.5 | 12.17 | 0.0774 | 0.18 | 12.96 | 1
February | 1 | 12PM to 1PM | 35.1 | 33.8 | 32 | 27.5 | 12.65 | 0.0771 | 0.18 | 13.01 | 1
February | 1 | 1PM to 2PM | 39 | 36 | 32 | 27.5 | 13.61 | 0.0765 | 0.18 | 13.12 | 1
February | 1 | 2PM to 3PM | 44.1 | 42 | 39.9 | 37.8 | 16.41 | 0.0757 | 0.25 | 13.28 | 1
February | 1 | 3PM to 4PM | 45 | 43 | 41 | 39.4 | 16.88 | 0.0756 | 0.26 | 13.31 | 1
February | 1 | 4PM to 5PM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
February | 1 | 5PM to 6PM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
February | 1 | 6PM to 7PM | 62.1 | 56 | 52 | 59.9 | 24.22 | 0.0729 | 0.39 | 13.83 | 1
February | 1 | 7PM to 8PM | 63 | 57 | 53.1 | 62.4 | 24.82 | 0.0728 | 0.41 | 13.86 | 1
February | 1 | 8PM to 9PM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
February | 1 | 9PM to 10PM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
February | 1 | 10PM to 11PM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
February | 1 | 11PM to 12AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
February | 2 | 12AM to 1AM | 45 | 44.5 | 44.1 | 44.4 | 17.65 | 0.0755 | 0.29 | 13.33 | 1
February | 2 | 1AM to 2AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
February | 2 | 2AM to 3AM | 36 | 35.6 | 35.1 | 31.1 | 13.43 | 0.077 | 0.2 | 13.05 | 1
February | 2 | 3AM to 4AM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
February | 2 | 4AM to 5AM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
February | 2 | 5AM to 6AM | 35.1 | 32.9 | 30 | 25.1 | 12.28 | 0.0772 | 0.16 | 13.01 | 1
February | 2 | 6AM to 7AM | 30.9 | 28.8 | 26.1 | 20.9 | 10.63 | 0.0778 | 0.14 | 12.89 | 1
February | 2 | 7AM to 8AM | 30 | 27.9 | 25 | 19.8 | 10.25 | 0.078 | 0.13 | 12.86 | 1
February | 2 | 8AM to 9AM | 30 | 26.8 | 21.9 | 17.1 | 9.84 | 0.078 | 0.11 | 12.85 | 1
February | 2 | 9AM to 10AM | 30 | 26.8 | 21.9 | 17.1 | 9.84 | 0.078 | 0.11 | 12.85 | 1
February | 2 | 10AM to 11AM | 32 | 27.6 | 21 | 16.4 | 10.21 | 0.0777 | 0.11 | 12.9 | 1
February | 2 | 11AM to 12PM | 34 | 28.7 | 21 | 16.4 | 10.68 | 0.0774 | 0.11 | 12.95 | 1
February | 2 | 12PM to 1PM | 35.1 | 28.7 | 19 | 14.9 | 10.71 | 0.0772 | 0.1 | 12.98 | 1
February | 2 | 1PM to 2PM | 37 | 29.3 | 17.1 | 13.6 | 10.98 | 0.0769 | 0.09 | 13.02 | 1
February | 2 | 2PM to 3PM | 36 | 28.4 | 16 | 12.9 | 10.61 | 0.0771 | 0.08 | 12.99 | 1
February | 2 | 3PM to 4PM | 35.1 | 27.9 | 16 | 12.9 | 10.4 | 0.0772 | 0.08 | 12.97 | 1
February | 2 | 4PM to 5PM | 32 | 25.4 | 12.9 | 11.1 | 9.38 | 0.0777 | 0.07 | 12.89 | 1
February | 2 | 5PM to 6PM | 28.9 | 23.3 | 12 | 10.6 | 8.57 | 0.0782 | 0.07 | 12.8 | 1
February | 2 | 6PM to 7PM | 28 | 22.8 | 12 | 10.6 | 8.35 | 0.0784 | 0.07 | 12.78 | 1
February | 2 | 7PM to 8PM | 27 | 22.3 | 12.9 | 11.1 | 8.17 | 0.0785 | 0.07 | 12.75 | 1
February | 2 | 8PM to 9PM | 26.1 | 21.5 | 12 | 10.6 | 7.88 | 0.0787 | 0.07 | 12.73 | 1
February | 2 | 9PM to 10PM | 25 | 20.8 | 12 | 10.6 | 7.62 | 0.0789 | 0.07 | 12.7 | 1
February | 2 | 10PM to 11PM | 25 | 20.8 | 12 | 10.6 | 7.62 | 0.0789 | 0.07 | 12.7 | 1
February | 2 | 11PM to 12AM | 23 | 18.8 | 9 | 9.1 | 6.91 | 0.0792 | 0.06 | 12.64 | 1
February | 3 | 12AM to 1AM | 21.9 | 17.7 | 7 | 8.2 | 6.52 | 0.0794 | 0.05 | 12.61 | 1
February | 3 | 1AM to 2AM | 21 | 16.7 | 5 | 7.4 | 6.18 | 0.0795 | 0.05 | 12.59 | 1
February | 3 | 2AM to 3AM | 19.9 | 15.8 | 3.9 | 7 | 5.86 | 0.0797 | 0.05 | 12.56 | 1
February | 3 | 3AM to 4AM | 19 | 15.2 | 3.9 | 7 | 5.64 | 0.0799 | 0.05 | 12.53 | 1
February | 3 | 4AM to 5AM | 18 | 14.6 | 5 | 7.4 | 5.45 | 0.08 | 0.05 | 12.51 | 1
February | 3 | 5AM to 6AM | 17.1 | 14 | 5 | 7.4 | 5.23 | 0.0802 | 0.05 | 12.48 | 1
February | 3 | 6AM to 7AM | 16 | 13.4 | 6.1 | 7.8 | 5.03 | 0.0804 | 0.05 | 12.46 | 1
February | 3 | 7AM to 8AM | 16 | 13.6 | 7 | 8.2 | 5.09 | 0.0804 | 0.05 | 12.46 | 1
February | 3 | 8AM to 9AM | 19 | 15.8 | 7 | 8.2 | 5.83 | 0.0799 | 0.05 | 12.54 | 1
February | 3 | 9AM to 10AM | 23 | 18.4 | 7 | 8.2 | 6.78 | 0.0792 | 0.05 | 12.64 | 1
February | 3 | 10AM to 11AM | 26.1 | 20.3 | 6.1 | 7.8 | 7.46 | 0.0787 | 0.05 | 12.72 | 1
February | 3 | 11AM to 12PM | 28.9 | 21.9 | 5 | 7.4 | 8.09 | 0.0782 | 0.05 | 12.79 | 1
February | 3 | 12PM to 1PM | 30 | 22.6 | 5 | 7.4 | 8.35 | 0.0781 | 0.05 | 12.82 | 1
February | 3 | 1PM to 2PM | 32 | 23.8 | 5 | 7.4 | 8.82 | 0.0778 | 0.05 | 12.87 | 1
February | 3 | 2PM to 3PM | 34 | 24.8 | 3.9 | 7 | 9.24 | 0.0774 | 0.05 | 12.93 | 1
February | 3 | 3PM to 4PM | 35.1 | 25.4 | 3.9 | 7 | 9.5 | 0.0773 | 0.05 | 12.95 | 1
February | 3 | 4PM to 5PM | 34 | 24.7 | 3 | 6.7 | 9.19 | 0.0774 | 0.04 | 12.92 | 1
February | 3 | 5PM to 6PM | 30.9 | 22.8 | 3 | 6.7 | 8.45 | 0.0779 | 0.04 | 12.84 | 1
February | 3 | 6PM to 7PM | 30 | 22.2 | 3 | 6.7 | 8.24 | 0.0781 | 0.04 | 12.82 | 1
February | 3 | 7PM to 8PM | 28 | 21.5 | 6.1 | 7.8 | 7.93 | 0.0784 | 0.05 | 12.77 | 1
February | 3 | 8PM to 9PM | 27 | 20.8 | 6.1 | 7.8 | 7.68 | 0.0786 | 0.05 | 12.74 | 1
February | 3 | 9PM to 10PM | 26.1 | 20.4 | 7 | 8.2 | 7.52 | 0.0787 | 0.05 | 12.72 | 1
February | 3 | 10PM to 11PM | 25 | 19.7 | 7 | 8.2 | 7.26 | 0.0789 | 0.05 | 12.69 | 1
February | 3 | 11PM to 12AM | 23 | 18.7 | 8.1 | 8.7 | 6.85 | 0.0792 | 0.06 | 12.64 | 1
February | 4 | 12AM to 1AM | 23 | 18.4 | 7 | 8.2 | 6.78 | 0.0792 | 0.05 | 12.64 | 1
February | 4 | 1AM to 2AM | 23 | 18.4 | 7 | 8.2 | 6.78 | 0.0792 | 0.05 | 12.64 | 1
February | 4 | 2AM to 3AM | 21 | 17.3 | 8.1 | 8.7 | 6.37 | 0.0795 | 0.06 | 12.59 | 1
February | 4 | 3AM to 4AM | 21.9 | 17.9 | 8.1 | 8.7 | 6.59 | 0.0794 | 0.06 | 12.61 | 1
February | 4 | 4AM to 5AM | 21.9 | 17.7 | 7 | 8.2 | 6.52 | 0.0794 | 0.05 | 12.61 | 1
February | 4 | 5AM to 6AM | 21 | 17.3 | 8.1 | 8.7 | 6.37 | 0.0795 | 0.06 | 12.59 | 1
February | 4 | 6AM to 7AM | 21.9 | 17.9 | 8.1 | 8.7 | 6.59 | 0.0794 | 0.06 | 12.61 | 1
February | 4 | 7AM to 8AM | 21.9 | 17.9 | 8.1 | 8.7 | 6.59 | 0.0794 | 0.06 | 12.61 | 1
February | 4 | 8AM to 9AM | 21.9 | 17.9 | 8.1 | 8.7 | 6.59 | 0.0794 | 0.06 | 12.61 | 1
February | 4 | 9AM to 10AM | 32 | 24.7 | 10 | 9.6 | 9.15 | 0.0777 | 0.06 | 12.88 | 1
February | 4 | 10AM to 11AM | 36 | 27.2 | 10.9 | 10 | 10.18 | 0.0771 | 0.07 | 12.99 | 1
February | 4 | 11AM to 12PM | 39 | 29.2 | 12 | 10.6 | 11 | 0.0766 | 0.07 | 13.07 | 1
February | 4 | 12PM to 1PM | 42.1 | 31 | 12.9 | 11.1 | 11.81 | 0.0762 | 0.07 | 13.15 | 1
February | 4 | 1PM to 2PM | 42.1 | 31 | 12.9 | 11.1 | 11.81 | 0.0762 | 0.07 | 13.15 | 1
February | 4 | 2PM to 3PM | 44.1 | 33.1 | 14 | 11.7 | 12.38 | 0.0759 | 0.08 | 13.2 | 1
February | 4 | 3PM to 4PM | 46 | 34.5 | 15.1 | 12.3 | 12.95 | 0.0756 | 0.08 | 13.26 | 1
February | 4 | 4PM to 5PM | 44.1 | 33.1 | 14 | 11.7 | 12.38 | 0.0759 | 0.08 | 13.2 | 1
February | 4 | 5PM to 6PM | 39.9 | 30.1 | 14 | 11.7 | 11.38 | 0.0765 | 0.08 | 13.09 | 1
February | 4 | 6PM to 7PM | 37 | 28.5 | 14 | 11.7 | 10.69 | 0.0769 | 0.08 | 13.02 | 1
February | 4 | 7PM to 8PM | 35.1 | 27.4 | 14 | 11.7 | 10.21 | 0.0772 | 0.08 | 12.97 | 1
February | 4 | 8PM to 9PM | 32 | 25.4 | 12.9 | 11.1 | 9.38 | 0.0777 | 0.07 | 12.89 | 1
February | 4 | 9PM to 10PM | 30.9 | 24.5 | 12 | 10.6 | 9.05 | 0.0779 | 0.07 | 12.86 | 1
February | 4 | 10PM to 11PM | 30 | 23.5 | 10 | 9.6 | 8.68 | 0.0781 | 0.06 | 12.83 | 1
February | 4 | 11PM to 12AM | 28.9 | 22.9 | 10 | 9.6 | 8.42 | 0.0782 | 0.06 | 12.8 | 1
February | 5 | 12AM to 1AM | 28 | 22.1 | 9 | 9.1 | 8.12 | 0.0784 | 0.06 | 12.78 | 1
February | 5 | 1AM to 2AM | 25 | 19.7 | 7 | 8.2 | 7.26 | 0.0789 | 0.05 | 12.69 | 1
February | 5 | 2AM to 3AM | 24.1 | 18.8 | 5 | 7.4 | 6.92 | 0.079 | 0.05 | 12.67 | 1
February | 5 | 3AM to 4AM | 21.9 | 17.1 | 3.9 | 7 | 6.34 | 0.0794 | 0.05 | 12.61 | 1
February | 5 | 4AM to 5AM | 21 | 16.7 | 5 | 7.4 | 6.18 | 0.0795 | 0.05 | 12.59 | 1
February | 5 | 5AM to 6AM | 21 | 16.7 | 5 | 7.4 | 6.18 | 0.0795 | 0.05 | 12.59 | 1
February | 5 | 6AM to 7AM | 19.9 | 16 | 5 | 7.4 | 5.92 | 0.0797 | 0.05 | 12.56 | 1
February | 5 | 7AM to 8AM | 19.9 | 16 | 5 | 7.4 | 5.92 | 0.0797 | 0.05 | 12.56 | 1
February | 5 | 8AM to 9AM | 25 | 20.4 | 10 | 9.6 | 7.47 | 0.0789 | 0.06 | 12.7 | 1
February | 5 | 9AM to 10AM | 28.9 | 22.1 | 6.1 | 7.8 | 8.15 | 0.0782 | 0.05 | 12.8 | 1
February | 5 | 10AM to 11AM | 32 | 23.6 | 3.9 | 7 | 8.76 | 0.0778 | 0.05 | 12.87 | 1
February | 5 | 11AM to 12PM | 35.1 | 25.3 | 3 | 6.7 | 9.45 | 0.0773 | 0.04 | 12.95 | 1
February | 5 | 12PM to 1PM | 37.9 | 27.1 | 3.9 | 7 | 10.19 | 0.0768 | 0.05 | 13.03 | 1
February | 5 | 1PM to 2PM | 41 | 28.8 | 3.9 | 7 | 10.92 | 0.0764 | 0.05 | 13.11 | 1
February | 5 | 2PM to 3PM | 41 | 28.8 | 3.9 | 7 | 10.92 | 0.0764 | 0.05 | 13.11 | 1
February | 5 | 3PM to 4PM | 41 | 29.2 | 6.1 | 7.8 | 11.05 | 0.0764 | 0.05 | 13.11 | 1
February | 5 | 4PM to 5PM | 39.9 | 28.4 | 5 | 7.4 | 10.73 | 0.0765 | 0.05 | 13.08 | 1
February | 5 | 5PM to 6PM | 39.9 | 28.7 | 7 | 8.2 | 10.85 | 0.0765 | 0.05 | 13.08 | 1
February | 5 | 6PM to 7PM | 37.9 | 28 | 9 | 9.1 | 10.51 | 0.0768 | 0.06 | 13.04 | 1
February | 5 | 7PM to 8PM | 37.9 | 27.8 | 8.1 | 8.7 | 10.44 | 0.0768 | 0.06 | 13.03 | 1
February | 5 | 8PM to 9PM | 37.9 | 28 | 9 | 9.1 | 10.51 | 0.0768 | 0.06 | 13.04 | 1
February | 5 | 9PM to 10PM | 37 | 27.7 | 10 | 9.6 | 10.37 | 0.077 | 0.06 | 13.01 | 1
February | 5 | 10PM to 11PM | 37.9 | 28.6 | 12 | 10.6 | 10.74 | 0.0768 | 0.07 | 13.04 | 1
February | 5 | 11PM to 12AM | 37 | 28.1 | 12 | 10.6 | 10.52 | 0.0769 | 0.07 | 13.02 | 1
February | 6 | 12AM to 1AM | 37 | 28.1 | 12 | 10.6 | 10.52 | 0.0769 | 0.07 | 13.02 | 1
February | 6 | 1AM to 2AM | 36 | 27.7 | 12.9 | 11.1 | 10.34 | 0.0771 | 0.07 | 12.99 | 1
February | 6 | 2AM to 3AM | 36 | 27.7 | 12.9 | 11.1 | 10.34 | 0.0771 | 0.07 | 12.99 | 1
February | 6 | 3AM to 4AM | 36 | 27.9 | 14 | 11.7 | 10.43 | 0.0771 | 0.08 | 12.99 | 1
February | 6 | 4AM to 5AM | 34 | 28.4 | 19.9 | 15.6 | 10.56 | 0.0774 | 0.1 | 12.95 | 1
February | 6 | 5AM to 6AM | 33.1 | 29.3 | 24.1 | 19 | 10.86 | 0.0775 | 0.12 | 12.94 | 1
February | 6 | 6AM to 7AM | 32 | 29 | 25 | 19.8 | 10.73 | 0.0777 | 0.13 | 12.91 | 1
February | 6 | 7AM to 8AM | 32 | 29.8 | 27 | 21.8 | 11.03 | 0.0777 | 0.14 | 12.92 | 1
February | 6 | 8AM to 9AM | 32 | 30.2 | 28 | 22.9 | 11.2 | 0.0777 | 0.15 | 12.92 | 1
February | 6 | 9AM to 10AM | 33.1 | 31.2 | 28.9 | 23.9 | 11.61 | 0.0775 | 0.16 | 12.95 | 1
February | 6 | 10AM to 11AM | 34 | 31.7 | 28.9 | 23.9 | 11.83 | 0.0773 | 0.16 | 12.98 | 1
February | 6 | 11AM to 12PM | 36 | 33 | 28.9 | 23.9 | 12.31 | 0.077 | 0.16 | 13.03 | 1
February | 6 | 12PM to 1PM | 37.9 | 34.9 | 30.9 | 26.2 | 13.14 | 0.0767 | 0.17 | 13.09 | 1
February | 6 | 1PM to 2PM | 41 | 37.1 | 32 | 27.5 | 14.09 | 0.0762 | 0.18 | 13.17 | 1
February | 6 | 2PM to 3PM | 43 | 38.9 | 34 | 29.8 | 14.92 | 0.0759 | 0.2 | 13.23 | 1
February | 6 | 3PM to 4PM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
February | 6 | 4PM to 5PM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
February | 6 | 5PM to 6PM | 43 | 39.7 | 36 | 32.3 | 15.3 | 0.0759 | 0.21 | 13.24 | 1
February | 6 | 6PM to 7PM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
February | 6 | 7PM to 8PM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
February | 6 | 8PM to 9PM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
February | 6 | 9PM to 10PM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
February | 6 | 10PM to 11PM | 39 | 37.6 | 36 | 32.3 | 14.34 | 0.0765 | 0.21 | 13.13 | 1
February | 6 | 11PM to 12AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
February | 7 | 12AM to 1AM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
February | 7 | 1AM to 2AM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
February | 7 | 2AM to 3AM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
February | 7 | 3AM to 4AM | 35.1 | 33.8 | 32 | 27.5 | 12.65 | 0.0771 | 0.18 | 13.01 | 1
February | 7 | 4AM to 5AM | 35.1 | 34.2 | 33.1 | 28.8 | 12.84 | 0.0771 | 0.19 | 13.02 | 1
February | 7 | 5AM to 6AM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
February | 7 | 6AM to 7AM | 36 | 35.6 | 35.1 | 31.1 | 13.43 | 0.077 | 0.2 | 13.05 | 1
February | 7 | 7AM to 8AM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
February | 7 | 8AM to 9AM | 37 | 36.6 | 36 | 32.3 | 13.86 | 0.0768 | 0.21 | 13.08 | 1
February | 7 | 9AM to 10AM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
February | 7 | 10AM to 11AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
February | 7 | 11AM to 12PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
February | 7 | 12PM to 1PM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
February | 7 | 1PM to 2PM | 42.1 | 41.5 | 41 | 39.4 | 16.18 | 0.076 | 0.26 | 13.23 | 1
February | 7 | 2PM to 3PM | 43 | 42.5 | 42.1 | 41.1 | 16.66 | 0.0758 | 0.27 | 13.26 | 1
February | 7 | 3PM to 4PM | 44.1 | 43.5 | 43 | 42.5 | 17.15 | 0.0757 | 0.28 | 13.3 | 1
February | 7 | 4PM to 5PM | 44.1 | 43.1 | 42.1 | 41.1 | 16.92 | 0.0757 | 0.27 | 13.29 | 1
February | 7 | 5PM to 6PM | 43 | 42.5 | 42.1 | 41.1 | 16.66 | 0.0758 | 0.27 | 13.26 | 1
February | 7 | 6PM to 7PM | 43 | 42.5 | 42.1 | 41.1 | 16.66 | 0.0758 | 0.27 | 13.26 | 1
February | 7 | 7PM to 8PM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
February | 7 | 8PM to 9PM | 42.1 | 41.5 | 41 | 39.4 | 16.18 | 0.076 | 0.26 | 13.23 | 1
February | 7 | 9PM to 10PM | 41 | 41 | 41 | 39.4 | 15.92 | 0.0761 | 0.26 | 13.21 | 1
February | 7 | 10PM to 11PM | 41 | 41 | 41 | 39.4 | 15.92 | 0.0761 | 0.26 | 13.21 | 1
February | 7 | 11PM to 12AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
February | 8 | 12AM to 1AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
February | 8 | 1AM to 2AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
February | 8 | 2AM to 3AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
February | 8 | 3AM to 4AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
February | 8 | 4AM to 5AM | 43 | 43 | 43 | 42.5 | 16.88 | 0.0758 | 0.28 | 13.27 | 1
February | 8 | 5AM to 6AM | 45 | 44.5 | 44.1 | 44.4 | 17.65 | 0.0755 | 0.29 | 13.33 | 1
February | 8 | 6AM to 7AM | 46.9 | 45.9 | 45 | 45.9 | 18.37 | 0.0752 | 0.3 | 13.38 | 1
February | 8 | 7AM to 8AM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
February | 8 | 8AM to 9AM | 48 | 47.4 | 46.9 | 49.6 | 19.19 | 0.075 | 0.32 | 13.42 | 1
February | 8 | 9AM to 10AM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
February | 8 | 10AM to 11AM | 48 | 45 | 42.1 | 41.1 | 17.88 | 0.0751 | 0.27 | 13.4 | 1
February | 8 | 11AM to 12PM | 46.9 | 42.6 | 37.9 | 34.9 | 16.67 | 0.0753 | 0.23 | 13.35 | 1
February | 8 | 12PM to 1PM | 48.9 | 43.5 | 37.9 | 34.9 | 17.15 | 0.075 | 0.23 | 13.4 | 1
February | 8 | 1PM to 2PM | 52 | 42.7 | 32 | 27.5 | 16.74 | 0.0746 | 0.18 | 13.46 | 1
February | 8 | 2PM to 3PM | 51.1 | 40.4 | 27 | 21.8 | 15.63 | 0.0748 | 0.14 | 13.42 | 1
February | 8 | 3PM to 4PM | 51.1 | 38.9 | 21.9 | 17.1 | 14.92 | 0.0748 | 0.11 | 13.4 | 1
February | 8 | 4PM to 5PM | 48.9 | 37.2 | 19.9 | 15.6 | 14.16 | 0.0751 | 0.1 | 13.34 | 1
February | 8 | 5PM to 6PM | 45 | 34.5 | 18 | 14.2 | 12.98 | 0.0757 | 0.09 | 13.23 | 1
February | 8 | 6PM to 7PM | 43 | 33.2 | 17.1 | 13.6 | 12.41 | 0.076 | 0.09 | 13.18 | 1
February | 8 | 7PM to 8PM | 41 | 31.4 | 17.1 | 13.6 | 11.93 | 0.0763 | 0.09 | 13.13 | 1
February | 8 | 8PM to 9PM | 37.9 | 29.5 | 16 | 12.9 | 11.09 | 0.0768 | 0.08 | 13.05 | 1
February | 8 | 9PM to 10PM | 35.1 | 27.7 | 15.1 | 12.3 | 10.31 | 0.0772 | 0.08 | 12.97 | 1
February | 8 | 10PM to 11PM | 32 | 25.9 | 15.1 | 12.3 | 9.57 | 0.0777 | 0.08 | 12.89 | 1
February | 8 | 11PM to 12AM | 30 | 24.4 | 14 | 11.7 | 9 | 0.078 | 0.08 | 12.84 | 1
February | 9 | 12AM to 1AM | 28 | 22.8 | 12 | 10.6 | 8.35 | 0.0784 | 0.07 | 12.78 | 1
February | 9 | 1AM to 2AM | 28 | 22.8 | 12 | 10.6 | 8.35 | 0.0784 | 0.07 | 12.78 | 1
February | 9 | 2AM to 3AM | 26.1 | 21.3 | 10.9 | 10 | 7.79 | 0.0787 | 0.07 | 12.73 | 1
February | 9 | 3AM to 4AM | 26.1 | 21.3 | 10.9 | 10 | 7.79 | 0.0787 | 0.07 | 12.73 | 1
February | 9 | 4AM to 5AM | 23 | 18.7 | 8.1 | 8.7 | 6.85 | 0.0792 | 0.06 | 12.64 | 1
February | 9 | 5AM to 6AM | 24.1 | 19.8 | 10 | 9.6 | 7.25 | 0.079 | 0.06 | 12.67 | 1
February | 9 | 6AM to 7AM | 21.9 | 17.9 | 8.1 | 8.7 | 6.59 | 0.0794 | 0.06 | 12.61 | 1
February | 9 | 7AM to 8AM | 21.9 | 18.4 | 10 | 9.6 | 6.73 | 0.0794 | 0.06 | 12.62 | 1
February | 9 | 8AM to 9AM | 32 | 25.2 | 12 | 10.6 | 9.31 | 0.0777 | 0.07 | 12.88 | 1
February | 9 | 9AM to 10AM | 37.9 | 27.8 | 8.1 | 8.7 | 10.44 | 0.0768 | 0.06 | 13.03 | 1
February | 9 | 10AM to 11AM | 42.1 | 29.4 | 3.9 | 7 | 11.18 | 0.0762 | 0.05 | 13.14 | 1
February | 9 | 11AM to 12PM | 46 | 31 | -0.9 | 5.4 | 11.89 | 0.0756 | 0.04 | 13.24 | 1
February | 9 | 12PM to 1PM | 48.9 | 33.7 | 0 | 5.7 | 12.63 | 0.0752 | 0.04 | 13.31 | 1
February | 9 | 1PM to 2PM | 51.1 | 35.3 | 3 | 6.7 | 13.3 | 0.0749 | 0.04 | 13.37 | 1
February | 9 | 2PM to 3PM | 52 | 36.2 | 6.1 | 7.8 | 13.69 | 0.0747 | 0.05 | 13.4 | 1
February | 9 | 3PM to 4PM | 54 | 37.6 | 8.1 | 8.7 | 14.3 | 0.0744 | 0.06 | 13.45 | 1
February | 9 | 4PM to 5PM | 53.1 | 37.2 | 9 | 9.1 | 14.14 | 0.0746 | 0.06 | 13.43 | 1
February | 9 | 5PM to 6PM | 51.1 | 36.7 | 12 | 10.6 | 13.9 | 0.0748 | 0.07 | 13.38 | 1
February | 9 | 6PM to 7PM | 48.9 | 35.5 | 12 | 10.6 | 13.38 | 0.0751 | 0.07 | 13.33 | 1
February | 9 | 7PM to 8PM | 48 | 35.4 | 14 | 11.7 | 13.33 | 0.0753 | 0.08 | 13.31 | 1
February | 9 | 8PM to 9PM | 46.9 | 35 | 15.1 | 12.3 | 13.17 | 0.0754 | 0.08 | 13.28 | 1
February | 9 | 9PM to 10PM | 46 | 34.9 | 17.1 | 13.6 | 13.15 | 0.0756 | 0.09 | 13.26 | 1
February | 9 | 10PM to 11PM | 44.1 | 34 | 18 | 14.2 | 12.76 | 0.0758 | 0.09 | 13.21 | 1
February | 9 | 11PM to 12AM | 44.1 | 34.3 | 19 | 14.9 | 12.88 | 0.0758 | 0.1 | 13.21 | 1
February | 10 | 12AM to 1AM | 43 | 34.2 | 21 | 16.4 | 12.85 | 0.076 | 0.11 | 13.19 | 1
February | 10 | 1AM to 2AM | 43 | 34.2 | 21 | 16.4 | 12.85 | 0.076 | 0.11 | 13.19 | 1
February | 10 | 2AM to 3AM | 42.1 | 34.3 | 23 | 18.1 | 12.89 | 0.0761 | 0.12 | 13.17 | 1
February | 10 | 3AM to 4AM | 42.1 | 35.7 | 27 | 21.8 | 13.46 | 0.0761 | 0.14 | 13.18 | 1
February | 10 | 4AM to 5AM | 41 | 36.2 | 30 | 25.1 | 13.72 | 0.0762 | 0.16 | 13.16 | 1
February | 10 | 5AM to 6AM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
February | 10 | 6AM to 7AM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
February | 10 | 7AM to 8AM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
February | 10 | 8AM to 9AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
February | 10 | 9AM to 10AM | 39.9 | 38.6 | 37 | 33.7 | 14.78 | 0.0763 | 0.22 | 13.16 | 1
February | 10 | 10AM to 11AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
February | 10 | 11AM to 12PM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
February | 10 | 12PM to 1PM | 44.1 | 43.5 | 43 | 42.5 | 17.15 | 0.0757 | 0.28 | 13.3 | 1
February | 10 | 1PM to 2PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
February | 10 | 2PM to 3PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
February | 10 | 3PM to 4PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
February | 10 | 4PM to 5PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
February | 10 | 5PM to 6PM | 44.1 | 43.5 | 43 | 42.5 | 17.15 | 0.0757 | 0.28 | 13.3 | 1
February | 10 | 6PM to 7PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
February | 10 | 7PM to 8PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
February | 10 | 8PM to 9PM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
February | 10 | 9PM to 10PM | 46.9 | 46.5 | 46 | 47.9 | 18.67 | 0.0752 | 0.31 | 13.39 | 1
February | 10 | 10PM to 11PM | 50 | 49.4 | 48.9 | 53.4 | 20.27 | 0.0747 | 0.35 | 13.49 | 1
February | 10 | 11PM to 12AM | 51.1 | 50.5 | 50 | 55.6 | 20.88 | 0.0745 | 0.36 | 13.52 | 1
February | 11 | 12AM to 1AM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
February | 11 | 1AM to 2AM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
February | 11 | 2AM to 3AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
February | 11 | 3AM to 4AM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
February | 11 | 4AM to 5AM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
February | 11 | 5AM to 6AM | 54 | 53.4 | 53.1 | 62.4 | 22.63 | 0.0741 | 0.41 | 13.62 | 1
February | 11 | 6AM to 7AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
February | 11 | 7AM to 8AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
February | 11 | 8AM to 9AM | 48.9 | 47.4 | 46 | 47.9 | 19.15 | 0.0749 | 0.31 | 13.44 | 1
February | 11 | 9AM to 10AM | 44.1 | 41.1 | 37.9 | 34.9 | 15.97 | 0.0757 | 0.23 | 13.27 | 1
February | 11 | 10AM to 11AM | 36 | 34.7 | 33.1 | 28.8 | 13.06 | 0.077 | 0.19 | 13.04 | 1
February | 11 | 11AM to 12PM | 28.9 | 27.3 | 25 | 19.8 | 9.99 | 0.0782 | 0.13 | 12.83 | 1
February | 11 | 12PM to 1PM | 32 | 28.3 | 23 | 18.1 | 10.46 | 0.0777 | 0.12 | 12.91 | 1
February | 11 | 1PM to 2PM | 32 | 27.3 | 19.9 | 15.6 | 10.08 | 0.0777 | 0.1 | 12.9 | 1
February | 11 | 2PM to 3PM | 28 | 23.8 | 16 | 12.9 | 8.71 | 0.0783 | 0.08 | 12.79 | 1
February | 11 | 3PM to 4PM | 26.1 | 22 | 14 | 11.7 | 8.05 | 0.0787 | 0.08 | 12.73 | 1
February | 11 | 4PM to 5PM | 26.1 | 21.7 | 12.9 | 11.1 | 7.95 | 0.0787 | 0.07 | 12.73 | 1
February | 11 | 5PM to 6PM | 23 | 19.1 | 10 | 9.6 | 6.99 | 0.0792 | 0.06 | 12.65 | 1
February | 11 | 6PM to 7PM | 21 | 17.1 | 7 | 8.2 | 6.3 | 0.0795 | 0.05 | 12.59 | 1
February | 11 | 7PM to 8PM | 19.9 | 16.4 | 7 | 8.2 | 6.04 | 0.0797 | 0.05 | 12.56 | 1
February | 11 | 8PM to 9PM | 19 | 15.6 | 6.1 | 7.8 | 5.77 | 0.0799 | 0.05 | 12.54 | 1
February | 11 | 9PM to 10PM | 18 | 14.6 | 5 | 7.4 | 5.45 | 0.08 | 0.05 | 12.51 | 1
February | 11 | 10PM to 11PM | 17.1 | 13.4 | 1.9 | 6.3 | 5.06 | 0.0802 | 0.04 | 12.48 | 1
February | 11 | 11PM to 12AM | 15.1 | 11.7 | 0 | 5.7 | 4.49 | 0.0805 | 0.04 | 12.43 | 1
February | 12 | 12AM to 1AM | 14 | 10.9 | 0 | 5.7 | 4.23 | 0.0807 | 0.04 | 12.4 | 1
February | 12 | 1AM to 2AM | 12.9 | 10 | -0.9 | 5.4 | 3.93 | 0.0809 | 0.04 | 12.37 | 1
February | 12 | 2AM to 3AM | 12 | 9.1 | -2 | 5.1 | 3.67 | 0.0811 | 0.03 | 12.35 | 1
February | 12 | 3AM to 4AM | 10.9 | 8.3 | -2 | 5.1 | 3.41 | 0.0812 | 0.03 | 12.32 | 1
February | 12 | 4AM to 5AM | 10.9 | 8.3 | -2 | 5.1 | 3.41 | 0.0812 | 0.03 | 12.32 | 1
February | 12 | 5AM to 6AM | 10 | 7.6 | -2 | 5.1 | 3.2 | 0.0814 | 0.03 | 12.29 | 1
February | 12 | 6AM to 7AM | 9 | 7 | -0.9 | 5.4 | 2.98 | 0.0816 | 0.04 | 12.27 | 1
February | 12 | 7AM to 8AM | 10 | 7.8 | -0.9 | 5.4 | 3.24 | 0.0814 | 0.04 | 12.29 | 1
February | 12 | 8AM to 9AM | 12.9 | 10.1 | 0 | 5.7 | 3.97 | 0.0809 | 0.04 | 12.37 | 1
February | 12 | 9AM to 10AM | 17.1 | 13.3 | 1 | 6 | 5.02 | 0.0802 | 0.04 | 12.48 | 1
February | 12 | 10AM to 11AM | 23 | 17.4 | 1 | 6 | 6.45 | 0.0792 | 0.04 | 12.63 | 1
February | 12 | 11AM to 12PM | 28 | 21 | 3 | 6.7 | 7.76 | 0.0784 | 0.04 | 12.77 | 1
February | 12 | 12PM to 1PM | 30 | 22.4 | 3.9 | 7 | 8.28 | 0.0781 | 0.05 | 12.82 | 1
February | 12 | 1PM to 2PM | 33.1 | 24.4 | 5 | 7.4 | 9.08 | 0.0776 | 0.05 | 12.9 | 1
February | 12 | 2PM to 3PM | 37 | 26.6 | 3.9 | 7 | 9.97 | 0.077 | 0.05 | 13.01 | 1
February | 12 | 3PM to 4PM | 37.9 | 27 | 3 | 6.7 | 10.14 | 0.0768 | 0.04 | 13.03 | 1
February | 12 | 4PM to 5PM | 39 | 27.4 | 1.9 | 6.3 | 10.34 | 0.0767 | 0.04 | 13.06 | 1
February | 12 | 5PM to 6PM | 35.1 | 25.1 | 1.9 | 6.3 | 9.39 | 0.0773 | 0.04 | 12.95 | 1
February | 12 | 6PM to 7PM | 33.1 | 24.1 | 3 | 6.7 | 8.97 | 0.0776 | 0.04 | 12.9 | 1
February | 12 | 7PM to 8PM | 32 | 23.6 | 3.9 | 7 | 8.76 | 0.0778 | 0.05 | 12.87 | 1
February | 12 | 8PM to 9PM | 30 | 22.4 | 3.9 | 7 | 8.28 | 0.0781 | 0.05 | 12.82 | 1
February | 12 | 9PM to 10PM | 28.9 | 21.9 | 5 | 7.4 | 8.09 | 0.0782 | 0.05 | 12.79 | 1
February | 12 | 10PM to 11PM | 28 | 21.5 | 6.1 | 7.8 | 7.93 | 0.0784 | 0.05 | 12.77 | 1
February | 12 | 11PM to 12AM | 28 | 21.3 | 5 | 7.4 | 7.87 | 0.0784 | 0.05 | 12.77 | 1
February | 13 | 12AM to 1AM | 26.1 | 20.1 | 5 | 7.4 | 7.39 | 0.0787 | 0.05 | 12.72 | 1
February | 13 | 1AM to 2AM | 26.1 | 20.1 | 5 | 7.4 | 7.39 | 0.0787 | 0.05 | 12.72 | 1
February | 13 | 2AM to 3AM | 25 | 19.2 | 3.9 | 7 | 7.07 | 0.0789 | 0.05 | 12.69 | 1
February | 13 | 3AM to 4AM | 23 | 17.9 | 3.9 | 7 | 6.6 | 0.0792 | 0.05 | 12.64 | 1
February | 13 | 4AM to 5AM | 23 | 17.7 | 3 | 6.7 | 6.55 | 0.0792 | 0.04 | 12.64 | 1
February | 13 | 5AM to 6AM | 21.9 | 16.8 | 1.9 | 6.3 | 6.23 | 0.0794 | 0.04 | 12.61 | 1
February | 13 | 6AM to 7AM | 21.9 | 16.8 | 1.9 | 6.3 | 6.23 | 0.0794 | 0.04 | 12.61 | 1
February | 13 | 7AM to 8AM | 21.9 | 17 | 3 | 6.7 | 6.29 | 0.0794 | 0.04 | 12.61 | 1
February | 13 | 8AM to 9AM | 26.1 | 19.7 | 3 | 6.7 | 7.28 | 0.0787 | 0.04 | 12.72 | 1
February | 13 | 9AM to 10AM | 30 | 22.2 | 3 | 6.7 | 8.24 | 0.0781 | 0.04 | 12.82 | 1
February | 13 | 10AM to 11AM | 33.1 | 24.1 | 3 | 6.7 | 8.97 | 0.0776 | 0.04 | 12.9 | 1
February | 13 | 11AM to 12PM | 37 | 26.8 | 5 | 7.4 | 10.03 | 0.077 | 0.05 | 13.01 | 1
February | 13 | 12PM to 1PM | 39.9 | 28.2 | 3.9 | 7 | 10.67 | 0.0765 | 0.05 | 13.08 | 1
February | 13 | 1PM to 2PM | 41 | 28.7 | 3 | 6.7 | 10.88 | 0.0764 | 0.04 | 13.11 | 1
February | 13 | 2PM to 3PM | 44.1 | 30.5 | 3.9 | 7 | 11.66 | 0.0759 | 0.05 | 13.19 | 1
February | 13 | 3PM to 4PM | 43 | 30.1 | 5 | 7.4 | 11.46 | 0.0761 | 0.05 | 13.16 | 1
February | 13 | 4PM to 5PM | 43 | 30.4 | 7 | 8.2 | 11.58 | 0.0761 | 0.05 | 13.16 | 1
February | 13 | 5PM to 6PM | 42.1 | 30.2 | 9 | 9.1 | 11.5 | 0.0762 | 0.06 | 13.14 | 1
February | 13 | 6PM to 7PM | 41 | 29.9 | 10 | 9.6 | 11.32 | 0.0763 | 0.06 | 13.12 | 1
February | 13 | 7PM to 8PM | 39.9 | 29.4 | 10.9 | 10 | 11.13 | 0.0765 | 0.07 | 13.09 | 1
February | 13 | 8PM to 9PM | 39 | 28.9 | 10.9 | 10 | 10.91 | 0.0766 | 0.07 | 13.07 | 1
February | 13 | 9PM to 10PM | 39 | 28.8 | 10 | 9.6 | 10.84 | 0.0766 | 0.06 | 13.06 | 1
February | 13 | 10PM to 11PM | 39 | 28.9 | 10.9 | 10 | 10.91 | 0.0766 | 0.07 | 13.07 | 1
February | 13 | 11PM to 12AM | 39 | 29.2 | 12 | 10.6 | 11 | 0.0766 | 0.07 | 13.07 | 1
February | 14 | 12AM to 1AM | 37.9 | 28.8 | 12.9 | 11.1 | 10.81 | 0.0768 | 0.07 | 13.04 | 1
February | 14 | 1AM to 2AM | 37 | 28.3 | 12.9 | 11.1 | 10.6 | 0.0769 | 0.07 | 13.02 | 1
February | 14 | 2AM to 3AM | 36 | 27.5 | 12 | 10.6 | 10.26 | 0.0771 | 0.07 | 12.99 | 1
February | 14 | 3AM to 4AM | 36 | 27.5 | 12 | 10.6 | 10.26 | 0.0771 | 0.07 | 12.99 | 1
February | 14 | 4AM to 5AM | 35.1 | 27.1 | 12.9 | 11.1 | 10.12 | 0.0772 | 0.07 | 12.97 | 1
February | 14 | 5AM to 6AM | 34 | 26.8 | 14 | 11.7 | 9.95 | 0.0774 | 0.08 | 12.94 | 1
February | 14 | 6AM to 7AM | 34 | 26.8 | 14 | 11.7 | 9.95 | 0.0774 | 0.08 | 12.94 | 1
February | 14 | 7AM to 8AM | 33.1 | 26.5 | 15.1 | 12.3 | 9.83 | 0.0776 | 0.08 | 12.92 | 1
February | 14 | 8AM to 9AM | 36 | 28.2 | 15.1 | 12.3 | 10.53 | 0.0771 | 0.08 | 12.99 | 1
February | 14 | 9AM to 10AM | 42.1 | 33.2 | 19 | 14.9 | 12.41 | 0.0761 | 0.1 | 13.16 | 1
February | 14 | 10AM to 11AM | 45 | 35.9 | 23 | 18.1 | 13.58 | 0.0757 | 0.12 | 13.25 | 1
February | 14 | 11AM to 12PM | 50 | 39.6 | 26.1 | 20.9 | 15.23 | 0.0749 | 0.14 | 13.39 | 1
February | 14 | 12PM to 1PM | 51.1 | 41.5 | 30 | 25.1 | 16.15 | 0.0747 | 0.16 | 13.43 | 1
February | 14 | 1PM to 2PM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
February | 14 | 2PM to 3PM | 55 | 44.6 | 33.1 | 28.8 | 17.67 | 0.0741 | 0.19 | 13.54 | 1
February | 14 | 3PM to 4PM | 57 | 45.9 | 34 | 29.8 | 18.32 | 0.0738 | 0.2 | 13.6 | 1
February | 14 | 4PM to 5PM | 55.9 | 45.3 | 34 | 29.8 | 18.05 | 0.074 | 0.2 | 13.57 | 1
February | 14 | 5PM to 6PM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
February | 14 | 6PM to 7PM | 50 | 42.1 | 33.1 | 28.8 | 16.45 | 0.0749 | 0.19 | 13.41 | 1
February | 14 | 7PM to 8PM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
February | 14 | 8PM to 9PM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
February | 14 | 9PM to 10PM | 45 | 39.6 | 33.1 | 28.8 | 15.23 | 0.0756 | 0.19 | 13.28 | 1
February | 14 | 10PM to 11PM | 43 | 38.1 | 32 | 27.5 | 14.57 | 0.0759 | 0.18 | 13.22 | 1
February | 14 | 11PM to 12AM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
February | 15 | 12AM to 1AM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
February | 15 | 1AM to 2AM | 41 | 37.5 | 33.1 | 28.8 | 14.28 | 0.0762 | 0.19 | 13.17 | 1
February | 15 | 2AM to 3AM | 39.9 | 36.5 | 32 | 27.5 | 13.83 | 0.0764 | 0.18 | 13.14 | 1
February | 15 | 3AM to 4AM | 39 | 36 | 32 | 27.5 | 13.61 | 0.0765 | 0.18 | 13.12 | 1
February | 15 | 4AM to 5AM | 39.9 | 36.5 | 32 | 27.5 | 13.83 | 0.0764 | 0.18 | 13.14 | 1
February | 15 | 5AM to 6AM | 39.9 | 36.5 | 32 | 27.5 | 13.83 | 0.0764 | 0.18 | 13.14 | 1
February | 15 | 6AM to 7AM | 39.9 | 36 | 30.9 | 26.2 | 13.62 | 0.0764 | 0.17 | 13.14 | 1
February | 15 | 7AM to 8AM | 39.9 | 36 | 30.9 | 26.2 | 13.62 | 0.0764 | 0.17 | 13.14 | 1
February | 15 | 8AM to 9AM | 41 | 36.6 | 30.9 | 26.2 | 13.88 | 0.0762 | 0.17 | 13.17 | 1
February | 15 | 9AM to 10AM | 46 | 40.1 | 33.1 | 28.8 | 15.5 | 0.0755 | 0.19 | 13.31 | 1
February | 15 | 10AM to 11AM | 48.9 | 41.9 | 34 | 29.8 | 16.36 | 0.075 | 0.2 | 13.39 | 1
February | 15 | 11AM to 12PM | 53.1 | 45.1 | 37 | 33.7 | 17.96 | 0.0744 | 0.22 | 13.51 | 1
February | 15 | 12PM to 1PM | 55 | 46.9 | 39 | 36.4 | 18.87 | 0.0741 | 0.24 | 13.57 | 1
February | 15 | 1PM to 2PM | 59 | 49 | 39.9 | 37.8 | 20.03 | 0.0735 | 0.25 | 13.68 | 1
February | 15 | 2PM to 3PM | 61 | 50.3 | 41 | 39.4 | 20.76 | 0.0732 | 0.26 | 13.73 | 1
February | 15 | 3PM to 4PM | 61 | 49.9 | 39.9 | 37.8 | 20.51 | 0.0732 | 0.25 | 13.73 | 1
February | 15 | 4PM to 5PM | 61 | 50.3 | 41 | 39.4 | 20.76 | 0.0732 | 0.26 | 13.73 | 1
February | 15 | 5PM to 6PM | 60.1 | 49.9 | 41 | 39.4 | 20.54 | 0.0734 | 0.26 | 13.71 | 1
February | 15 | 6PM to 7PM | 57 | 48.1 | 39.9 | 37.8 | 19.55 | 0.0738 | 0.25 | 13.62 | 1
February | 15 | 7PM to 8PM | 55.9 | 47.7 | 39.9 | 37.8 | 19.29 | 0.074 | 0.25 | 13.6 | 1
February | 15 | 8PM to 9PM | 55.9 | 47.3 | 39 | 36.4 | 19.08 | 0.074 | 0.24 | 13.59 | 1
February | 15 | 9PM to 10PM | 55 | 46.4 | 37.9 | 34.9 | 18.63 | 0.0741 | 0.23 | 13.56 | 1
February | 15 | 10PM to 11PM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
February | 15 | 11PM to 12AM | 54 | 45.1 | 36 | 32.3 | 17.96 | 0.0743 | 0.21 | 13.53 | 1
February | 16 | 12AM to 1AM | 53.1 | 45.1 | 37 | 33.7 | 17.96 | 0.0744 | 0.22 | 13.51 | 1
February | 16 | 1AM to 2AM | 52 | 45 | 37.9 | 34.9 | 17.89 | 0.0745 | 0.23 | 13.48 | 1
February | 16 | 2AM to 3AM | 52 | 46.3 | 41 | 39.4 | 18.58 | 0.0745 | 0.26 | 13.5 | 1
February | 16 | 3AM to 4AM | 51.1 | 46.4 | 42.1 | 41.1 | 18.62 | 0.0746 | 0.27 | 13.48 | 1
February | 16 | 4AM to 5AM | 51.1 | 46.8 | 43 | 42.5 | 18.85 | 0.0746 | 0.28 | 13.48 | 1
February | 16 | 5AM to 6AM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
February | 16 | 6AM to 7AM | 50 | 47.9 | 46 | 47.9 | 19.41 | 0.0747 | 0.31 | 13.47 | 1
February | 16 | 7AM to 8AM | 50 | 47.9 | 46 | 47.9 | 19.41 | 0.0747 | 0.31 | 13.47 | 1
February | 16 | 8AM to 9AM | 51.1 | 48.3 | 46 | 47.9 | 19.67 | 0.0746 | 0.31 | 13.5 | 1
February | 16 | 9AM to 10AM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
February | 16 | 10AM to 11AM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
February | 16 | 11AM to 12PM | 60.1 | 53.2 | 48 | 51.6 | 22.45 | 0.0733 | 0.34 | 13.75 | 1
February | 16 | 12PM to 1PM | 63 | 54.8 | 48.9 | 53.4 | 23.43 | 0.0729 | 0.35 | 13.83 | 1
February | 16 | 1PM to 2PM | 64.9 | 55.6 | 48.9 | 53.4 | 23.91 | 0.0726 | 0.35 | 13.88 | 1
February | 16 | 2PM to 3PM | 66.9 | 56.9 | 50 | 55.6 | 24.74 | 0.0723 | 0.36 | 13.94 | 1
February | 16 | 3PM to 4PM | 68 | 56.3 | 48 | 51.6 | 24.37 | 0.0722 | 0.34 | 13.96 | 1
February | 16 | 4PM to 5PM | 69.1 | 56.7 | 48 | 51.6 | 24.64 | 0.072 | 0.34 | 13.99 | 1
February | 16 | 5PM to 6PM | 66 | 55.5 | 48 | 51.6 | 23.89 | 0.0724 | 0.34 | 13.9 | 1
February | 16 | 6PM to 7PM | 64 | 54.8 | 48 | 51.6 | 23.41 | 0.0727 | 0.34 | 13.85 | 1
February | 16 | 7PM to 8PM | 63 | 54.3 | 48 | 51.6 | 23.15 | 0.0729 | 0.34 | 13.82 | 1
February | 16 | 8PM to 9PM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
February | 16 | 9PM to 10PM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
February | 16 | 10PM to 11PM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
February | 16 | 11PM to 12AM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
February | 17 | 12AM to 1AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
February | 17 | 1AM to 2AM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
February | 17 | 2AM to 3AM | 55.9 | 53.1 | 51.1 | 58 | 22.42 | 0.0738 | 0.38 | 13.66 | 1
February | 17 | 3AM to 4AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
February | 17 | 4AM to 5AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
February | 17 | 5AM to 6AM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
February | 17 | 6AM to 7AM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
February | 17 | 7AM to 8AM | 55 | 53.9 | 53.1 | 62.4 | 22.89 | 0.0739 | 0.41 | 13.65 | 1
February | 17 | 8AM to 9AM | 55 | 53.9 | 53.1 | 62.4 | 22.89 | 0.0739 | 0.41 | 13.65 | 1
February | 17 | 9AM to 10AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
February | 17 | 10AM to 11AM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
February | 17 | 11AM to 12PM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
February | 17 | 12PM to 1PM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
February | 17 | 1PM to 2PM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
February | 17 | 2PM to 3PM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
February | 17 | 3PM to 4PM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
February | 17 | 4PM to 5PM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
February | 17 | 5PM to 6PM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
February | 17 | 6PM to 7PM | 59 | 58.3 | 57.9 | 74.7 | 25.76 | 0.0733 | 0.48 | 13.79 | 1
February | 17 | 7PM to 8PM | 59 | 58.3 | 57.9 | 74.7 | 25.76 | 0.0733 | 0.48 | 13.79 | 1
February | 17 | 8PM to 9PM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 17 | 9PM to 10PM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 17 | 10PM to 11PM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 17 | 11PM to 12AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 18 | 12AM to 1AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 18 | 1AM to 2AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 18 | 2AM to 3AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 18 | 3AM to 4AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 18 | 4AM to 5AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 18 | 5AM to 6AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 18 | 6AM to 7AM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 18 | 7AM to 8AM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 18 | 8AM to 9AM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 18 | 9AM to 10AM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 18 | 10AM to 11AM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 18 | 11AM to 12PM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 18 | 12PM to 1PM | 60.1 | 58.2 | 57 | 72.3 | 25.65 | 0.0731 | 0.47 | 13.81 | 1
February | 18 | 1PM to 2PM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
February | 18 | 2PM to 3PM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
February | 18 | 3PM to 4PM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
February | 18 | 4PM to 5PM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
February | 18 | 5PM to 6PM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
February | 18 | 6PM to 7PM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
February | 18 | 7PM to 8PM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
February | 18 | 8PM to 9PM | 57.9 | 57.9 | 57.9 | 74.7 | 25.5 | 0.0734 | 0.48 | 13.76 | 1
February | 18 | 9PM to 10PM | 57.9 | 57.9 | 57.9 | 74.7 | 25.5 | 0.0734 | 0.48 | 13.76 | 1
February | 18 | 10PM to 11PM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 18 | 11PM to 12AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 19 | 12AM to 1AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
February | 19 | 1AM to 2AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 19 | 2AM to 3AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 19 | 3AM to 4AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 19 | 4AM to 5AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
February | 19 | 5AM to 6AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
February | 19 | 6AM to 7AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
February | 19 | 7AM to 8AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
February | 19 | 8AM to 9AM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
February | 19 | 9AM to 10AM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
February | 19 | 10AM to 11AM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
February | 19 | 11AM to 12PM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
February | 19 | 12PM to 1PM | 64 | 59.6 | 57 | 72.3 | 26.62 | 0.0726 | 0.47 | 13.92 | 1
February | 19 | 1PM to 2PM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
February | 19 | 2PM to 3PM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
February | 19 | 3PM to 4PM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
February | 19 | 4PM to 5PM | 66.9 | 58.4 | 53.1 | 62.4 | 25.79 | 0.0723 | 0.41 | 13.96 | 1
February | 19 | 5PM to 6PM | 66.9 | 58.4 | 53.1 | 62.4 | 25.79 | 0.0723 | 0.41 | 13.96 | 1
February | 19 | 6PM to 7PM | 64 | 56.3 | 51.1 | 58 | 24.39 | 0.0727 | 0.38 | 13.87 | 1
February | 19 | 7PM to 8PM | 60.1 | 53.6 | 48.9 | 53.4 | 22.72 | 0.0733 | 0.35 | 13.75 | 1
February | 19 | 8PM to 9PM | 57 | 51.9 | 48 | 51.6 | 21.7 | 0.0737 | 0.34 | 13.67 | 1
February | 19 | 9PM to 10PM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
February | 19 | 10PM to 11PM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
February | 19 | 11PM to 12AM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
February | 20 | 12AM to 1AM | 55 | 50.5 | 46.9 | 49.6 | 20.9 | 0.074 | 0.32 | 13.61 | 1
February | 20 | 1AM to 2AM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
February | 20 | 2AM to 3AM | 54 | 51.1 | 48.9 | 53.4 | 21.23 | 0.0741 | 0.35 | 13.59 | 1
February | 20 | 3AM to 4AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
February | 20 | 4AM to 5AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
February | 20 | 5AM to 6AM | 53.1 | 50.7 | 48.9 | 53.4 | 21.02 | 0.0743 | 0.35 | 13.57 | 1
February | 20 | 6AM to 7AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
February | 20 | 7AM to 8AM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
February | 20 | 8AM to 9AM | 53.1 | 48.2 | 44.1 | 44.4 | 19.61 | 0.0743 | 0.29 | 13.54 | 1
February | 20 | 9AM to 10AM | 57 | 47.3 | 37.9 | 34.9 | 19.11 | 0.0738 | 0.23 | 13.61 | 1
February | 20 | 10AM to 11AM | 60.1 | 47.3 | 34 | 29.8 | 19.06 | 0.0734 | 0.2 | 13.68 | 1
February | 20 | 11AM to 12PM | 63 | 48.6 | 34 | 29.8 | 19.75 | 0.073 | 0.2 | 13.76 | 1
February | 20 | 12PM to 1PM | 64 | 49.4 | 35.1 | 31.1 | 20.22 | 0.0728 | 0.2 | 13.79 | 1
February | 20 | 1PM to 2PM | 64.9 | 50.1 | 36 | 32.3 | 20.62 | 0.0727 | 0.21 | 13.82 | 1
February | 20 | 2PM to 3PM | 66 | 50.6 | 36 | 32.3 | 20.88 | 0.0726 | 0.21 | 13.84 | 1
February | 20 | 3PM to 4PM | 66.9 | 50.6 | 35.1 | 31.1 | 20.92 | 0.0725 | 0.2 | 13.86 | 1
February | 20 | 4PM to 5PM | 64.9 | 49.8 | 35.1 | 31.1 | 20.44 | 0.0727 | 0.2 | 13.81 | 1
February | 20 | 5PM to 6PM | 63 | 48.9 | 35.1 | 31.1 | 19.96 | 0.073 | 0.2 | 13.76 | 1
February | 20 | 6PM to 7PM | 57.9 | 46.7 | 35.1 | 31.1 | 18.74 | 0.0737 | 0.2 | 13.63 | 1
February | 20 | 7PM to 8PM | 55 | 45.7 | 36 | 32.3 | 18.22 | 0.0741 | 0.21 | 13.55 | 1
February | 20 | 8PM to 9PM | 53.1 | 44.7 | 36 | 32.3 | 17.74 | 0.0744 | 0.21 | 13.5 | 1
February | 20 | 9PM to 10PM | 50 | 43.7 | 37 | 33.7 | 17.22 | 0.0748 | 0.22 | 13.43 | 1
February | 20 | 10PM to 11PM | 51.1 | 43.8 | 36 | 32.3 | 17.26 | 0.0747 | 0.21 | 13.45 | 1
February | 20 | 11PM to 12AM | 50 | 43.2 | 36 | 32.3 | 17 | 0.0748 | 0.21 | 13.42 | 1
February | 21 | 12AM to 1AM | 48.9 | 42.4 | 35.1 | 31.1 | 16.56 | 0.075 | 0.2 | 13.39 | 1
February | 21 | 1AM to 2AM | 46 | 40.9 | 35.1 | 31.1 | 15.86 | 0.0754 | 0.2 | 13.31 | 1
February | 21 | 2AM to 3AM | 46 | 40.9 | 35.1 | 31.1 | 15.86 | 0.0754 | 0.2 | 13.31 | 1
February | 21 | 3AM to 4AM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
February | 21 | 4AM to 5AM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
February | 21 | 5AM to 6AM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
February | 21 | 6AM to 7AM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
February | 21 | 7AM to 8AM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
February | 21 | 8AM to 9AM | 48.9 | 42.7 | 36 | 32.3 | 16.74 | 0.075 | 0.21 | 13.39 | 1
February | 21 | 9AM to 10AM | 55.9 | 46.5 | 37 | 33.7 | 18.66 | 0.074 | 0.22 | 13.58 | 1
February | 21 | 10AM to 11AM | 62.1 | 48.5 | 35.1 | 31.1 | 19.74 | 0.0731 | 0.2 | 13.74 | 1
February | 21 | 11AM to 12PM | 64.9 | 49.1 | 33.1 | 28.8 | 20.07 | 0.0727 | 0.19 | 13.8 | 1
February | 21 | 12PM to 1PM | 69.1 | 49.9 | 30 | 25.1 | 20.5 | 0.0722 | 0.16 | 13.9 | 1
February | 21 | 1PM to 2PM | 71.1 | 50.5 | 28.9 | 23.9 | 20.79 | 0.0719 | 0.16 | 13.95 | 1
February | 21 | 2PM to 3PM | 73 | 52.3 | 32 | 27.5 | 21.83 | 0.0716 | 0.18 | 14.01 | 1
February | 21 | 3PM to 4PM | 72 | 51.8 | 32 | 27.5 | 21.57 | 0.0718 | 0.18 | 13.99 | 1
February | 21 | 4PM to 5PM | 71.1 | 50.5 | 28.9 | 23.9 | 20.79 | 0.0719 | 0.16 | 13.95 | 1
February | 21 | 5PM to 6PM | 68 | 49.8 | 30.9 | 26.2 | 20.41 | 0.0723 | 0.17 | 13.88 | 1
February | 21 | 6PM to 7PM | 64.9 | 48.4 | 30.9 | 26.2 | 19.67 | 0.0728 | 0.17 | 13.8 | 1
February | 21 | 7PM to 8PM | 63 | 47.9 | 32 | 27.5 | 19.4 | 0.073 | 0.18 | 13.75 | 1
February | 21 | 8PM to 9PM | 62.1 | 47.9 | 33.1 | 28.8 | 19.37 | 0.0731 | 0.19 | 13.73 | 1
February | 21 | 9PM to 10PM | 57.9 | 46 | 33.1 | 28.8 | 18.37 | 0.0737 | 0.19 | 13.62 | 1
February | 21 | 10PM to 11PM | 57 | 46.6 | 36 | 32.3 | 18.7 | 0.0738 | 0.21 | 13.61 | 1
February | 21 | 11PM to 12AM | 57 | 46.6 | 36 | 32.3 | 18.7 | 0.0738 | 0.21 | 13.61 | 1
February | 22 | 12AM to 1AM | 60.1 | 47 | 33.1 | 28.8 | 18.89 | 0.0734 | 0.19 | 13.68 | 1
February | 22 | 1AM to 2AM | 60.1 | 46.6 | 32 | 27.5 | 18.7 | 0.0734 | 0.18 | 13.67 | 1
February | 22 | 2AM to 3AM | 57 | 46.2 | 35.1 | 31.1 | 18.52 | 0.0738 | 0.2 | 13.6 | 1
February | 22 | 3AM to 4AM | 55 | 46.4 | 37.9 | 34.9 | 18.63 | 0.0741 | 0.23 | 13.56 | 1
February | 22 | 4AM to 5AM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
February | 22 | 5AM to 6AM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
February | 22 | 6AM to 7AM | 52 | 43.4 | 34 | 29.8 | 17.1 | 0.0746 | 0.2 | 13.47 | 1
February | 22 | 7AM to 8AM | 51.1 | 43 | 34 | 29.8 | 16.88 | 0.0747 | 0.2 | 13.44 | 1
February | 22 | 8AM to 9AM | 53.1 | 43.3 | 32 | 27.5 | 17 | 0.0744 | 0.18 | 13.49 | 1
February | 22 | 9AM to 10AM | 55 | 44.2 | 32 | 27.5 | 17.48 | 0.0741 | 0.18 | 13.54 | 1
February | 22 | 10AM to 11AM | 57 | 45.5 | 33.1 | 28.8 | 18.15 | 0.0739 | 0.19 | 13.6 | 1
February | 22 | 11AM to 12PM | 63 | 48.6 | 34 | 29.8 | 19.75 | 0.073 | 0.2 | 13.76 | 1
February | 22 | 12PM to 1PM | 66 | 50.6 | 36 | 32.3 | 20.88 | 0.0726 | 0.21 | 13.84 | 1
February | 22 | 1PM to 2PM | 69.1 | 53.3 | 39.9 | 37.8 | 22.47 | 0.0721 | 0.25 | 13.94 | 1
February | 22 | 2PM to 3PM | 68 | 54.1 | 43 | 42.5 | 22.96 | 0.0722 | 0.28 | 13.93 | 1
February | 22 | 3PM to 4PM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
February | 22 | 4PM to 5PM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
February | 22 | 5PM to 6PM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
February | 22 | 6PM to 7PM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
February | 22 | 7PM to 8PM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 22 | 8PM to 9PM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 22 | 9PM to 10PM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
February | 22 | 10PM to 11PM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
February | 22 | 11PM to 12AM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
February | 23 | 12AM to 1AM | 48.9 | 46.4 | 44.1 | 44.4 | 18.61 | 0.0749 | 0.29 | 13.43 | 1
February | 23 | 1AM to 2AM | 48 | 44.5 | 41 | 39.4 | 17.62 | 0.0751 | 0.26 | 13.39 | 1
February | 23 | 2AM to 3AM | 46 | 43.5 | 41 | 39.4 | 17.14 | 0.0754 | 0.26 | 13.34 | 1
February | 23 | 3AM to 4AM | 44.1 | 41.1 | 37.9 | 34.9 | 15.97 | 0.0757 | 0.23 | 13.27 | 1
February | 23 | 4AM to 5AM | 43 | 40.2 | 37 | 33.7 | 15.52 | 0.0759 | 0.22 | 13.24 | 1
February | 23 | 5AM to 6AM | 42.1 | 39.2 | 36 | 32.3 | 15.08 | 0.076 | 0.21 | 13.21 | 1
February | 23 | 6AM to 7AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
February | 23 | 7AM to 8AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
February | 23 | 8AM to 9AM | 43 | 39.7 | 36 | 32.3 | 15.3 | 0.0759 | 0.21 | 13.24 | 1
February | 23 | 9AM to 10AM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
February | 23 | 10AM to 11AM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
February | 23 | 11AM to 12PM | 54 | 43.3 | 30.9 | 26.2 | 17.01 | 0.0743 | 0.17 | 13.51 | 1
February | 23 | 12PM to 1PM | 55.9 | 43.5 | 28.9 | 23.9 | 17.14 | 0.074 | 0.16 | 13.55 | 1
February | 23 | 1PM to 2PM | 57 | 43.1 | 26.1 | 20.9 | 16.93 | 0.0739 | 0.14 | 13.57 | 1
February | 23 | 2PM to 3PM | 59 | 43.8 | 25 | 19.8 | 17.24 | 0.0736 | 0.13 | 13.62 | 1
February | 23 | 3PM to 4PM | 61 | 45 | 26.1 | 20.9 | 17.88 | 0.0733 | 0.14 | 13.68 | 1
February | 23 | 4PM to 5PM | 60.1 | 43.8 | 23 | 18.1 | 17.23 | 0.0735 | 0.12 | 13.64 | 1
February | 23 | 5PM to 6PM | 57.9 | 41.5 | 18 | 14.2 | 16.1 | 0.0738 | 0.09 | 13.57 | 1
February | 23 | 6PM to 7PM | 55.9 | 40.7 | 19 | 14.9 | 15.75 | 0.0741 | 0.1 | 13.52 | 1
February | 23 | 7PM to 8PM | 53.1 | 39.2 | 19 | 14.9 | 15.05 | 0.0745 | 0.1 | 13.45 | 1
February | 23 | 8PM to 9PM | 48 | 36.7 | 19.9 | 15.6 | 13.94 | 0.0752 | 0.1 | 13.32 | 1
February | 23 | 9PM to 10PM | 48 | 36.5 | 19 | 14.9 | 13.84 | 0.0753 | 0.1 | 13.32 | 1
February | 23 | 10PM to 11PM | 46 | 35.7 | 19.9 | 15.6 | 13.46 | 0.0755 | 0.1 | 13.27 | 1
February | 23 | 11PM to 12AM | 44.1 | 34.9 | 21 | 16.4 | 13.11 | 0.0758 | 0.11 | 13.22 | 1
February | 24 | 12AM to 1AM | 43 | 33.9 | 19.9 | 15.6 | 12.72 | 0.076 | 0.1 | 13.19 | 1
February | 24 | 1AM to 2AM | 42.1 | 33.4 | 19.9 | 15.6 | 12.51 | 0.0761 | 0.1 | 13.16 | 1
February | 24 | 2AM to 3AM | 41 | 33.1 | 21 | 16.4 | 12.38 | 0.0763 | 0.11 | 13.14 | 1
February | 24 | 3AM to 4AM | 41 | 33.4 | 21.9 | 17.1 | 12.49 | 0.0763 | 0.11 | 13.14 | 1
February | 24 | 4AM to 5AM | 39 | 32.6 | 23 | 18.1 | 12.15 | 0.0766 | 0.12 | 13.09 | 1
February | 24 | 5AM to 6AM | 39 | 32.6 | 23 | 18.1 | 12.15 | 0.0766 | 0.12 | 13.09 | 1
February | 24 | 6AM to 7AM | 37 | 31 | 23 | 18.1 | 11.67 | 0.0769 | 0.12 | 13.04 | 1
February | 24 | 7AM to 8AM | 39.9 | 33.1 | 23 | 18.1 | 12.37 | 0.0765 | 0.12 | 13.11 | 1
February | 24 | 8AM to 9AM | 45 | 36.3 | 24.1 | 19 | 13.73 | 0.0757 | 0.12 | 13.25 | 1
February | 24 | 9AM to 10AM | 48.9 | 38.7 | 25 | 19.8 | 14.81 | 0.0751 | 0.13 | 13.36 | 1
February | 24 | 10AM to 11AM | 53.1 | 40.8 | 25 | 19.8 | 15.81 | 0.0745 | 0.13 | 13.46 | 1
February | 24 | 11AM to 12PM | 55.9 | 41.4 | 21.9 | 17.1 | 16.09 | 0.0741 | 0.11 | 13.53 | 1
February | 24 | 12PM to 1PM | 59 | 42.7 | 21 | 16.4 | 16.71 | 0.0736 | 0.11 | 13.61 | 1
February | 24 | 1PM to 2PM | 60.1 | 43.8 | 23 | 18.1 | 17.23 | 0.0735 | 0.12 | 13.64 | 1
February | 24 | 2PM to 3PM | 62.1 | 45.2 | 25 | 19.8 | 17.98 | 0.0732 | 0.13 | 13.7 | 1
February | 24 | 3PM to 4PM | 61 | 44.7 | 25 | 19.8 | 17.72 | 0.0733 | 0.13 | 13.67 | 1
February | 24 | 4PM to 5PM | 61 | 44.7 | 25 | 19.8 | 17.72 | 0.0733 | 0.13 | 13.67 | 1
February | 24 | 5PM to 6PM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
February | 24 | 6PM to 7PM | 55 | 41.6 | 24.1 | 19 | 16.16 | 0.0742 | 0.12 | 13.51 | 1
February | 24 | 7PM to 8PM | 52 | 40 | 24.1 | 19 | 15.42 | 0.0746 | 0.12 | 13.43 | 1
February | 24 | 8PM to 9PM | 48 | 37.9 | 24.1 | 19 | 14.47 | 0.0752 | 0.12 | 13.33 | 1
February | 24 | 9PM to 10PM | 45 | 36.3 | 24.1 | 19 | 13.73 | 0.0757 | 0.12 | 13.25 | 1
February | 24 | 10PM to 11PM | 44.1 | 36.1 | 25 | 19.8 | 13.64 | 0.0758 | 0.13 | 13.23 | 1
February | 24 | 11PM to 12AM | 45 | 36.3 | 24.1 | 19 | 13.73 | 0.0757 | 0.12 | 13.25 | 1
February | 25 | 12AM to 1AM | 44.1 | 35.8 | 24.1 | 19 | 13.51 | 0.0758 | 0.12 | 13.23 | 1
February | 25 | 1AM to 2AM | 39.9 | 33.4 | 24.1 | 19 | 12.51 | 0.0764 | 0.12 | 13.12 | 1
February | 25 | 2AM to 3AM | 43 | 35.2 | 24.1 | 19 | 13.25 | 0.076 | 0.12 | 13.2 | 1
February | 25 | 3AM to 4AM | 39 | 32.9 | 24.1 | 19 | 12.3 | 0.0766 | 0.12 | 13.09 | 1
February | 25 | 4AM to 5AM | 37.9 | 32.6 | 25 | 19.8 | 12.16 | 0.0767 | 0.13 | 13.07 | 1
February | 25 | 5AM to 6AM | 36 | 31.2 | 25 | 19.8 | 11.69 | 0.0771 | 0.13 | 13.02 | 1
February | 25 | 6AM to 7AM | 35.1 | 30.3 | 24.1 | 19 | 11.34 | 0.0772 | 0.12 | 12.99 | 1
February | 25 | 7AM to 8AM | 37.9 | 32.6 | 25 | 19.8 | 12.16 | 0.0767 | 0.13 | 13.07 | 1
February | 25 | 8AM to 9AM | 45 | 36.9 | 26.1 | 20.9 | 14.02 | 0.0757 | 0.14 | 13.25 | 1
February | 25 | 9AM to 10AM | 52 | 40.6 | 26.1 | 20.9 | 15.71 | 0.0746 | 0.14 | 13.44 | 1
February | 25 | 10AM to 11AM | 59 | 44.4 | 27 | 21.8 | 17.55 | 0.0736 | 0.14 | 13.63 | 1
February | 25 | 11AM to 12PM | 64 | 46.7 | 27 | 21.8 | 18.76 | 0.0729 | 0.14 | 13.76 | 1
February | 25 | 12PM to 1PM | 66 | 47.6 | 27 | 21.8 | 19.24 | 0.0726 | 0.14 | 13.81 | 1
February | 25 | 1PM to 2PM | 68 | 48.3 | 26.1 | 20.9 | 19.58 | 0.0724 | 0.14 | 13.86 | 1
February | 25 | 2PM to 3PM | 71.1 | 49.6 | 26.1 | 20.9 | 20.32 | 0.0719 | 0.14 | 13.94 | 1
February | 25 | 3PM to 4PM | 69.1 | 48.5 | 25 | 19.8 | 19.68 | 0.0722 | 0.13 | 13.88 | 1
February | 25 | 4PM to 5PM | 68 | 48.3 | 26.1 | 20.9 | 19.58 | 0.0724 | 0.14 | 13.86 | 1
February | 25 | 5PM to 6PM | 64.9 | 47.2 | 27 | 21.8 | 18.98 | 0.0728 | 0.14 | 13.78 | 1
February | 25 | 6PM to 7PM | 63 | 46 | 26.1 | 20.9 | 18.36 | 0.0731 | 0.14 | 13.73 | 1
February | 25 | 7PM to 8PM | 57 | 43.8 | 28 | 22.9 | 17.24 | 0.0739 | 0.15 | 13.58 | 1
February | 25 | 8PM to 9PM | 55 | 43.5 | 30 | 25.1 | 17.11 | 0.0742 | 0.16 | 13.53 | 1
February | 25 | 9PM to 10PM | 54 | 43 | 30 | 25.1 | 16.85 | 0.0743 | 0.16 | 13.5 | 1
February | 25 | 10PM to 11PM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
February | 25 | 11PM to 12AM | 52 | 42.3 | 30.9 | 26.2 | 16.53 | 0.0746 | 0.17 | 13.46 | 1
February | 26 | 12AM to 1AM | 50 | 41.8 | 32 | 27.5 | 16.26 | 0.0749 | 0.18 | 13.41 | 1
February | 26 | 1AM to 2AM | 48 | 40.8 | 32 | 27.5 | 15.78 | 0.0752 | 0.18 | 13.36 | 1
February | 26 | 2AM to 3AM | 48.9 | 41.2 | 32 | 27.5 | 16 | 0.075 | 0.18 | 13.38 | 1
February | 26 | 3AM to 4AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
February | 26 | 4AM to 5AM | 45 | 39.2 | 32 | 27.5 | 15.05 | 0.0756 | 0.18 | 13.27 | 1
February | 26 | 5AM to 6AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
February | 26 | 6AM to 7AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
February | 26 | 7AM to 8AM | 50 | 42.1 | 33.1 | 28.8 | 16.45 | 0.0749 | 0.19 | 13.41 | 1
February | 26 | 8AM to 9AM | 55.9 | 45 | 33.1 | 28.8 | 17.89 | 0.074 | 0.19 | 13.57 | 1
February | 26 | 9AM to 10AM | 61 | 47.7 | 34 | 29.8 | 19.27 | 0.0733 | 0.2 | 13.7 | 1
February | 26 | 10AM to 11AM | 69.1 | 51.6 | 35.1 | 31.1 | 21.44 | 0.0722 | 0.2 | 13.92 | 1
February | 26 | 11AM to 12PM | 73 | 53.5 | 36 | 32.3 | 22.58 | 0.0716 | 0.21 | 14.03 | 1
February | 26 | 12PM to 1PM | 75 | 54.6 | 37 | 33.7 | 23.28 | 0.0713 | 0.22 | 14.09 | 1
February | 26 | 1PM to 2PM | 75.9 | 54.6 | 36 | 32.3 | 23.27 | 0.0712 | 0.21 | 14.1 | 1
February | 26 | 2PM to 3PM | 77 | 54.8 | 35.1 | 31.1 | 23.36 | 0.0711 | 0.2 | 14.13 | 1
February | 26 | 3PM to 4PM | 75.9 | 54 | 34 | 29.8 | 22.89 | 0.0712 | 0.2 | 14.1 | 1
February | 26 | 4PM to 5PM | 75 | 53.7 | 34 | 29.8 | 22.67 | 0.0714 | 0.2 | 14.07 | 1
February | 26 | 5PM to 6PM | 73 | 52.9 | 34 | 29.8 | 22.19 | 0.0716 | 0.2 | 14.02 | 1
February | 26 | 6PM to 7PM | 68 | 51.1 | 35.1 | 31.1 | 21.18 | 0.0723 | 0.2 | 13.89 | 1
February | 26 | 7PM to 8PM | 68 | 51.1 | 35.1 | 31.1 | 21.18 | 0.0723 | 0.2 | 13.89 | 1
February | 26 | 8PM to 9PM | 62.1 | 49.2 | 37 | 33.7 | 20.14 | 0.0731 | 0.22 | 13.74 | 1
February | 26 | 9PM to 10PM | 61 | 48.8 | 37 | 33.7 | 19.88 | 0.0733 | 0.22 | 13.72 | 1
February | 26 | 10PM to 11PM | 59 | 47.9 | 37 | 33.7 | 19.4 | 0.0735 | 0.22 | 13.66 | 1
February | 26 | 11PM to 12AM | 57 | 47 | 37 | 33.7 | 18.92 | 0.0738 | 0.22 | 13.61 | 1
February | 27 | 12AM to 1AM | 55.9 | 46.5 | 37 | 33.7 | 18.66 | 0.074 | 0.22 | 13.58 | 1
February | 27 | 1AM to 2AM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
February | 27 | 2AM to 3AM | 54 | 45.9 | 37.9 | 34.9 | 18.37 | 0.0743 | 0.23 | 13.53 | 1
February | 27 | 3AM to 4AM | 52 | 43.9 | 35.1 | 31.1 | 17.3 | 0.0746 | 0.2 | 13.47 | 1
February | 27 | 4AM to 5AM | 53.1 | 42.8 | 30.9 | 26.2 | 16.8 | 0.0744 | 0.17 | 13.48 | 1
February | 27 | 5AM to 6AM | 50 | 40.6 | 28.9 | 23.9 | 15.7 | 0.0749 | 0.16 | 13.4 | 1
February | 27 | 6AM to 7AM | 48 | 39.2 | 28 | 22.9 | 15.07 | 0.0752 | 0.15 | 13.34 | 1
February | 27 | 7AM to 8AM | 48.9 | 39.7 | 28 | 22.9 | 15.29 | 0.0751 | 0.15 | 13.36 | 1
February | 27 | 8AM to 9AM | 52 | 40.6 | 26.1 | 20.9 | 15.71 | 0.0746 | 0.14 | 13.44 | 1
February | 27 | 9AM to 10AM | 55 | 41.8 | 25 | 19.8 | 16.29 | 0.0742 | 0.13 | 13.52 | 1
February | 27 | 10AM to 11AM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
February | 27 | 11AM to 12PM | 63 | 45.4 | 24.1 | 19 | 18.07 | 0.0731 | 0.12 | 13.72 | 1
February | 27 | 12PM to 1PM | 66.9 | 47.5 | 25 | 19.8 | 19.16 | 0.0725 | 0.13 | 13.83 | 1
February | 27 | 1PM to 2PM | 69.1 | 49 | 27 | 21.8 | 19.98 | 0.0722 | 0.14 | 13.89 | 1
February | 27 | 2PM to 3PM | 70 | 50 | 28.9 | 23.9 | 20.53 | 0.0721 | 0.16 | 13.92 | 1
February | 27 | 3PM to 4PM | 73 | 52.3 | 32 | 27.5 | 21.83 | 0.0716 | 0.18 | 14.01 | 1
February | 27 | 4PM to 5PM | 72 | 52.4 | 34 | 29.8 | 21.93 | 0.0718 | 0.2 | 13.99 | 1
February | 27 | 5PM to 6PM | 71.1 | 52 | 34 | 29.8 | 21.71 | 0.0719 | 0.2 | 13.97 | 1
February | 27 | 6PM to 7PM | 68 | 50.8 | 34 | 29.8 | 20.97 | 0.0723 | 0.2 | 13.89 | 1
February | 27 | 7PM to 8PM | 66 | 50.3 | 35.1 | 31.1 | 20.7 | 0.0726 | 0.2 | 13.84 | 1
February | 27 | 8PM to 9PM | 64 | 49.4 | 35.1 | 31.1 | 20.22 | 0.0728 | 0.2 | 13.79 | 1
February | 27 | 9PM to 10PM | 60.1 | 47.3 | 34 | 29.8 | 19.06 | 0.0734 | 0.2 | 13.68 | 1
February | 27 | 10PM to 11PM | 57.9 | 46.3 | 34 | 29.8 | 18.53 | 0.0737 | 0.2 | 13.62 | 1
February | 27 | 11PM to 12AM | 57.9 | 46.3 | 34 | 29.8 | 18.53 | 0.0737 | 0.2 | 13.62 | 1
February | 28 | 12AM to 1AM | 57.9 | 46.3 | 34 | 29.8 | 18.53 | 0.0737 | 0.2 | 13.62 | 1
February | 28 | 1AM to 2AM | 55 | 44.6 | 33.1 | 28.8 | 17.67 | 0.0741 | 0.19 | 13.54 | 1
February | 28 | 2AM to 3AM | 55 | 44.6 | 33.1 | 28.8 | 17.67 | 0.0741 | 0.19 | 13.54 | 1
February | 28 | 3AM to 4AM | 52 | 43.1 | 33.1 | 28.8 | 16.93 | 0.0746 | 0.19 | 13.46 | 1
February | 28 | 4AM to 5AM | 51.1 | 42.7 | 33.1 | 28.8 | 16.71 | 0.0747 | 0.19 | 13.44 | 1
February | 28 | 5AM to 6AM | 51.1 | 42.3 | 32 | 27.5 | 16.52 | 0.0747 | 0.18 | 13.44 | 1
February | 28 | 6AM to 7AM | 53.1 | 43.3 | 32 | 27.5 | 17 | 0.0744 | 0.18 | 13.49 | 1
February | 28 | 7AM to 8AM | 53.1 | 43.3 | 32 | 27.5 | 17 | 0.0744 | 0.18 | 13.49 | 1
February | 28 | 8AM to 9AM | 55 | 45.3 | 35.1 | 31.1 | 18.04 | 0.0741 | 0.2 | 13.55 | 1
February | 28 | 9AM to 10AM | 62.1 | 48.8 | 36 | 32.3 | 19.92 | 0.0731 | 0.21 | 13.74 | 1
February | 28 | 10AM to 11AM | 69.1 | 53.3 | 39.9 | 37.8 | 22.47 | 0.0721 | 0.25 | 13.94 | 1
February | 28 | 11AM to 12PM | 72 | 54.1 | 39 | 36.4 | 22.96 | 0.0717 | 0.24 | 14.01 | 1
February | 28 | 12PM to 1PM | 73.9 | 54.9 | 39 | 36.4 | 23.44 | 0.0715 | 0.24 | 14.07 | 1
February | 28 | 1PM to 2PM | 77 | 56.4 | 39.9 | 37.8 | 24.39 | 0.071 | 0.25 | 14.15 | 1
February | 28 | 2PM to 3PM | 77 | 56.4 | 39.9 | 37.8 | 24.39 | 0.071 | 0.25 | 14.15 | 1
February | 28 | 3PM to 4PM | 73.9 | 54.5 | 37.9 | 34.9 | 23.21 | 0.0715 | 0.23 | 14.06 | 1
February | 28 | 4PM to 5PM | 75 | 55.3 | 39 | 36.4 | 23.71 | 0.0713 | 0.24 | 14.09 | 1
February | 28 | 5PM to 6PM | 73 | 54.2 | 37.9 | 34.9 | 22.99 | 0.0716 | 0.23 | 14.04 | 1
February | 28 | 6PM to 7PM | 71.1 | 53.8 | 39 | 36.4 | 22.75 | 0.0719 | 0.24 | 13.99 | 1
February | 28 | 7PM to 8PM | 69.1 | 53 | 39 | 36.4 | 22.27 | 0.0721 | 0.24 | 13.94 | 1
February | 28 | 8PM to 9PM | 69.1 | 53 | 39 | 36.4 | 22.27 | 0.0721 | 0.24 | 13.94 | 1
February | 28 | 9PM to 10PM | 66 | 51.3 | 38.1 | 35.2 | 21.33 | 0.0725 | 0.23 | 13.85 | 1
February | 28 | 10PM to 11PM | 63.1 | 49.8 | 37.4 | 34.2 | 20.48 | 0.073 | 0.22 | 13.77 | 1
February | 28 | 11PM to 12AM | 60.1 | 48.2 | 36.5 | 33 | 19.55 | 0.0734 | 0.22 | 13.69 | 1
March | 1 | 12AM to 1AM | 57 | 46.4 | 35.6 | 31.8 | 18.63 | 0.0738 | 0.21 | 13.61 | 1
March | 1 | 1AM to 2AM | 54 | 44.7 | 34.7 | 30.7 | 17.71 | 0.0743 | 0.2 | 13.52 | 1
March | 1 | 2AM to 3AM | 51.1 | 43 | 34 | 29.8 | 16.88 | 0.0747 | 0.2 | 13.44 | 1
March | 1 | 3AM to 4AM | 48 | 41.1 | 33.1 | 28.8 | 15.97 | 0.0752 | 0.19 | 13.36 | 1
March | 1 | 4AM to 5AM | 48 | 41.1 | 33.1 | 28.8 | 15.97 | 0.0752 | 0.19 | 13.36 | 1
March | 1 | 5AM to 6AM | 46.9 | 41.7 | 36 | 32.3 | 16.26 | 0.0753 | 0.21 | 13.34 | 1
March | 1 | 6AM to 7AM | 48 | 44.5 | 41 | 39.4 | 17.62 | 0.0751 | 0.26 | 13.39 | 1
March | 1 | 7AM to 8AM | 48 | 45.4 | 43 | 42.5 | 18.11 | 0.0751 | 0.28 | 13.4 | 1
March | 1 | 8AM to 9AM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
March | 1 | 9AM to 10AM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
March | 1 | 10AM to 11AM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
March | 1 | 11AM to 12PM | 50 | 47.9 | 46 | 47.9 | 19.41 | 0.0747 | 0.31 | 13.47 | 1
March | 1 | 12PM to 1PM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
March | 1 | 1PM to 2PM | 51.1 | 48.8 | 46.9 | 49.6 | 19.93 | 0.0746 | 0.32 | 13.5 | 1
March | 1 | 2PM to 3PM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
March | 1 | 3PM to 4PM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
March | 1 | 4PM to 5PM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
March | 1 | 5PM to 6PM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
March | 1 | 6PM to 7PM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
March | 1 | 7PM to 8PM | 51.1 | 49.9 | 48.9 | 53.4 | 20.53 | 0.0746 | 0.35 | 13.52 | 1
March | 1 | 8PM to 9PM | 51.1 | 49.9 | 48.9 | 53.4 | 20.53 | 0.0746 | 0.35 | 13.52 | 1
March | 1 | 9PM to 10PM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
March | 1 | 10PM to 11PM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
March | 1 | 11PM to 12AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
March | 2 | 12AM to 1AM | 50 | 48.3 | 46.9 | 49.6 | 19.67 | 0.0747 | 0.32 | 13.47 | 1
March | 2 | 1AM to 2AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
March | 2 | 2AM to 3AM | 48.9 | 48.4 | 48 | 51.6 | 19.73 | 0.0749 | 0.34 | 13.45 | 1
March | 2 | 3AM to 4AM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
March | 2 | 4AM to 5AM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
March | 2 | 5AM to 6AM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
March | 2 | 6AM to 7AM | 48.9 | 47.4 | 46 | 47.9 | 19.15 | 0.0749 | 0.31 | 13.44 | 1
March | 2 | 7AM to 8AM | 48.9 | 46.4 | 44.1 | 44.4 | 18.61 | 0.0749 | 0.29 | 13.43 | 1
March | 2 | 8AM to 9AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
March | 2 | 9AM to 10AM | 53.1 | 49.2 | 46 | 47.9 | 20.16 | 0.0743 | 0.31 | 13.55 | 1
March | 2 | 10AM to 11AM | 55.9 | 49.9 | 45 | 45.9 | 20.55 | 0.0739 | 0.3 | 13.62 | 1
March | 2 | 11AM to 12PM | 59 | 51.8 | 46 | 47.9 | 21.6 | 0.0735 | 0.31 | 13.71 | 1
March | 2 | 12PM to 1PM | 61 | 51.2 | 43 | 42.5 | 21.25 | 0.0732 | 0.28 | 13.74 | 1
March | 2 | 1PM to 2PM | 62.1 | 51.6 | 43 | 42.5 | 21.52 | 0.0731 | 0.28 | 13.77 | 1
March | 2 | 2PM to 3PM | 62.1 | 52.1 | 44.1 | 44.4 | 21.8 | 0.073 | 0.29 | 13.78 | 1
March | 2 | 3PM to 4PM | 62.1 | 52.1 | 44.1 | 44.4 | 21.8 | 0.073 | 0.29 | 13.78 | 1
March | 2 | 4PM to 5PM | 60.1 | 50.4 | 42.1 | 41.1 | 20.81 | 0.0733 | 0.27 | 13.71 | 1
March | 2 | 5PM to 6PM | 59 | 49.5 | 41 | 39.4 | 20.28 | 0.0735 | 0.26 | 13.68 | 1
March | 2 | 6PM to 7PM | 57 | 48.6 | 41 | 39.4 | 19.8 | 0.0738 | 0.26 | 13.63 | 1
March | 2 | 7PM to 8PM | 55 | 47.7 | 41 | 39.4 | 19.32 | 0.0741 | 0.26 | 13.58 | 1
March | 2 | 8PM to 9PM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
March | 2 | 9PM to 10PM | 51.1 | 45.9 | 41 | 39.4 | 18.36 | 0.0746 | 0.26 | 13.47 | 1
March | 2 | 10PM to 11PM | 48.9 | 44.9 | 41 | 39.4 | 17.84 | 0.075 | 0.26 | 13.42 | 1
March | 2 | 11PM to 12AM | 46.9 | 43.9 | 41 | 39.4 | 17.36 | 0.0753 | 0.26 | 13.36 | 1
March | 3 | 12AM to 1AM | 46.9 | 43 | 39 | 36.4 | 16.9 | 0.0753 | 0.24 | 13.35 | 1
March | 3 | 1AM to 2AM | 45 | 42.5 | 39.9 | 37.8 | 16.63 | 0.0756 | 0.25 | 13.31 | 1
March | 3 | 2AM to 3AM | 44.1 | 42 | 39.9 | 37.8 | 16.41 | 0.0757 | 0.25 | 13.28 | 1
March | 3 | 3AM to 4AM | 44.1 | 41.6 | 39 | 36.4 | 16.2 | 0.0757 | 0.24 | 13.28 | 1
March | 3 | 4AM to 5AM | 45 | 42.1 | 39 | 36.4 | 16.42 | 0.0756 | 0.24 | 13.3 | 1
March | 3 | 5AM to 6AM | 45 | 41.6 | 37.9 | 34.9 | 16.19 | 0.0756 | 0.23 | 13.3 | 1
March | 3 | 6AM to 7AM | 43 | 40.2 | 37 | 33.7 | 15.52 | 0.0759 | 0.22 | 13.24 | 1
March | 3 | 7AM to 8AM | 45 | 40.7 | 36 | 32.3 | 15.78 | 0.0756 | 0.21 | 13.29 | 1
March | 3 | 8AM to 9AM | 50 | 43.2 | 36 | 32.3 | 17 | 0.0748 | 0.21 | 13.42 | 1
March | 3 | 9AM to 10AM | 54 | 44.8 | 35.1 | 31.1 | 17.78 | 0.0743 | 0.2 | 13.52 | 1
March | 3 | 10AM to 11AM | 57 | 47 | 37 | 33.7 | 18.92 | 0.0738 | 0.22 | 13.61 | 1
March | 3 | 11AM to 12PM | 61 | 49.9 | 39.9 | 37.8 | 20.51 | 0.0732 | 0.25 | 13.73 | 1
March | 3 | 12PM to 1PM | 64 | 52.1 | 42.1 | 41.1 | 21.77 | 0.0728 | 0.27 | 13.82 | 1
March | 3 | 1PM to 2PM | 64.9 | 52.8 | 43 | 42.5 | 22.21 | 0.0727 | 0.28 | 13.85 | 1
March | 3 | 2PM to 3PM | 66.9 | 53.3 | 42.1 | 41.1 | 22.47 | 0.0724 | 0.27 | 13.9 | 1
March | 3 | 3PM to 4PM | 68 | 53.7 | 42.1 | 41.1 | 22.73 | 0.0722 | 0.27 | 13.92 | 1
March | 3 | 4PM to 5PM | 66.9 | 53.6 | 43 | 42.5 | 22.69 | 0.0724 | 0.28 | 13.9 | 1
March | 3 | 5PM to 6PM | 66 | 52.9 | 42.1 | 41.1 | 22.25 | 0.0725 | 0.27 | 13.87 | 1
March | 3 | 6PM to 7PM | 64 | 52.5 | 43 | 42.5 | 22 | 0.0728 | 0.28 | 13.82 | 1
March | 3 | 7PM to 8PM | 62.1 | 51.6 | 43 | 42.5 | 21.52 | 0.0731 | 0.28 | 13.77 | 1
March | 3 | 8PM to 9PM | 60.1 | 50.8 | 43 | 42.5 | 21.03 | 0.0733 | 0.28 | 13.72 | 1
March | 3 | 9PM to 10PM | 57.9 | 49.9 | 43 | 42.5 | 20.51 | 0.0736 | 0.28 | 13.66 | 1
March | 3 | 10PM to 11PM | 57 | 49.1 | 42.1 | 41.1 | 20.07 | 0.0738 | 0.27 | 13.63 | 1
March | 3 | 11PM to 12AM | 55 | 48.2 | 42.1 | 41.1 | 19.58 | 0.0741 | 0.27 | 13.58 | 1
March | 4 | 12AM to 1AM | 55 | 48.6 | 43 | 42.5 | 19.81 | 0.0741 | 0.28 | 13.59 | 1
March | 4 | 1AM to 2AM | 53.1 | 48.2 | 44.1 | 44.4 | 19.61 | 0.0743 | 0.29 | 13.54 | 1
March | 4 | 2AM to 3AM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
March | 4 | 3AM to 4AM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
March | 4 | 4AM to 5AM | 51.1 | 48.3 | 46 | 47.9 | 19.67 | 0.0746 | 0.31 | 13.5 | 1
March | 4 | 5AM to 6AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
March | 4 | 6AM to 7AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
March | 4 | 7AM to 8AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
March | 4 | 8AM to 9AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
March | 4 | 9AM to 10AM | 55 | 52.7 | 51.1 | 58 | 22.2 | 0.074 | 0.38 | 13.63 | 1
March | 4 | 10AM to 11AM | 57 | 54 | 52 | 59.9 | 22.99 | 0.0737 | 0.39 | 13.69 | 1
March | 4 | 11AM to 12PM | 60.1 | 55.9 | 53.1 | 62.4 | 24.12 | 0.0732 | 0.41 | 13.78 | 1
March | 4 | 12PM to 1PM | 64.9 | 58.2 | 54 | 64.5 | 25.64 | 0.0725 | 0.42 | 13.92 | 1
March | 4 | 1PM to 2PM | 71.1 | 60.4 | 54 | 64.5 | 27.13 | 0.0717 | 0.42 | 14.08 | 1
March | 4 | 2PM to 3PM | 73.9 | 61.4 | 54 | 64.5 | 27.83 | 0.0713 | 0.42 | 14.16 | 1
March | 4 | 3PM to 4PM | 75 | 60.8 | 52 | 59.9 | 27.38 | 0.0712 | 0.39 | 14.17 | 1
March | 4 | 4PM to 5PM | 75.9 | 61.1 | 52 | 59.9 | 27.6 | 0.0711 | 0.39 | 14.19 | 1
March | 4 | 5PM to 6PM | 73.9 | 60.4 | 52 | 59.9 | 27.12 | 0.0713 | 0.39 | 14.14 | 1
March | 4 | 6PM to 7PM | 71.1 | 59.4 | 52 | 59.9 | 26.41 | 0.0717 | 0.39 | 14.06 | 1
March | 4 | 7PM to 8PM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
March | 4 | 8PM to 9PM | 68 | 58.8 | 53.1 | 62.4 | 26.05 | 0.0721 | 0.41 | 13.99 | 1
March | 4 | 9PM to 10PM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
March | 4 | 10PM to 11PM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
March | 4 | 11PM to 12AM | 66.9 | 58.4 | 53.1 | 62.4 | 25.79 | 0.0723 | 0.41 | 13.96 | 1
March | 5 | 12AM to 1AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
March | 5 | 1AM to 2AM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
March | 5 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 62.4 | 23.11 | 0.0738 | 0.41 | 13.67 | 1
March | 5 | 3AM to 4AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
March | 5 | 4AM to 5AM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
March | 5 | 5AM to 6AM | 51.1 | 46.8 | 43 | 42.5 | 18.85 | 0.0746 | 0.28 | 13.48 | 1
March | 5 | 6AM to 7AM | 51.1 | 47.3 | 44.1 | 44.4 | 19.13 | 0.0746 | 0.29 | 13.49 | 1
March | 5 | 7AM to 8AM | 51.1 | 47.3 | 44.1 | 44.4 | 19.13 | 0.0746 | 0.29 | 13.49 | 1
March | 5 | 8AM to 9AM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
March | 5 | 9AM to 10AM | 53.1 | 48.7 | 45 | 45.9 | 19.85 | 0.0743 | 0.3 | 13.54 | 1
March | 5 | 10AM to 11AM | 55.9 | 49 | 43 | 42.5 | 20.03 | 0.0739 | 0.28 | 13.61 | 1
March | 5 | 11AM to 12PM | 60.1 | 50.4 | 42.1 | 41.1 | 20.81 | 0.0733 | 0.27 | 13.71 | 1
March | 5 | 12PM to 1PM | 61 | 50.3 | 41 | 39.4 | 20.76 | 0.0732 | 0.26 | 13.73 | 1
March | 5 | 1PM to 2PM | 63 | 50 | 37.9 | 34.9 | 20.55 | 0.073 | 0.23 | 13.77 | 1
March | 5 | 2PM to 3PM | 64 | 49.7 | 36 | 32.3 | 20.4 | 0.0728 | 0.21 | 13.79 | 1
March | 5 | 3PM to 4PM | 64 | 47.7 | 30 | 25.1 | 19.28 | 0.0729 | 0.16 | 13.77 | 1
March | 5 | 4PM to 5PM | 63 | 46.6 | 28 | 22.9 | 18.68 | 0.0731 | 0.15 | 13.73 | 1
March | 5 | 5PM to 6PM | 61 | 45.3 | 27 | 21.8 | 18.02 | 0.0733 | 0.14 | 13.68 | 1
March | 5 | 6PM to 7PM | 57.9 | 43.3 | 25 | 19.8 | 16.98 | 0.0738 | 0.13 | 13.59 | 1
March | 5 | 7PM to 8PM | 55 | 42.2 | 26.1 | 20.9 | 16.45 | 0.0742 | 0.14 | 13.52 | 1
March | 5 | 8PM to 9PM | 53.1 | 41.2 | 26.1 | 20.9 | 15.97 | 0.0745 | 0.14 | 13.47 | 1
March | 5 | 9PM to 10PM | 51.1 | 39.5 | 24.1 | 19 | 15.21 | 0.0748 | 0.12 | 13.41 | 1
March | 5 | 10PM to 11PM | 48.9 | 38.7 | 25 | 19.8 | 14.81 | 0.0751 | 0.13 | 13.36 | 1
March | 5 | 11PM to 12AM | 48 | 37.6 | 23 | 18.1 | 14.32 | 0.0752 | 0.12 | 13.33 | 1
March | 6 | 12AM to 1AM | 46 | 36.9 | 24.1 | 19 | 13.99 | 0.0755 | 0.12 | 13.28 | 1
March | 6 | 1AM to 2AM | 44.1 | 35.8 | 24.1 | 19 | 13.51 | 0.0758 | 0.12 | 13.23 | 1
March | 6 | 2AM to 3AM | 43 | 35.2 | 24.1 | 19 | 13.25 | 0.076 | 0.12 | 13.2 | 1
March | 6 | 3AM to 4AM | 41 | 34.7 | 26.1 | 20.9 | 13.06 | 0.0763 | 0.14 | 13.15 | 1
March | 6 | 4AM to 5AM | 39.9 | 33.7 | 25 | 19.8 | 12.64 | 0.0764 | 0.13 | 13.12 | 1
March | 6 | 5AM to 6AM | 37.9 | 32.6 | 25 | 19.8 | 12.16 | 0.0767 | 0.13 | 13.07 | 1
March | 6 | 6AM to 7AM | 37 | 31.4 | 24.1 | 19 | 11.82 | 0.0769 | 0.12 | 13.04 | 1
March | 6 | 7AM to 8AM | 37 | 32.1 | 25 | 19.8 | 11.95 | 0.0769 | 0.13 | 13.04 | 1
March | 6 | 8AM to 9AM | 39.9 | 33.7 | 25 | 19.8 | 12.64 | 0.0764 | 0.13 | 13.12 | 1
March | 6 | 9AM to 10AM | 45 | 36.9 | 26.1 | 20.9 | 14.02 | 0.0757 | 0.14 | 13.25 | 1
March | 6 | 10AM to 11AM | 51.1 | 40.2 | 26.1 | 20.9 | 15.49 | 0.0748 | 0.14 | 13.42 | 1
March | 6 | 11AM to 12PM | 54 | 41.3 | 25 | 19.8 | 16.03 | 0.0744 | 0.13 | 13.49 | 1
March | 6 | 12PM to 1PM | 57.9 | 43.3 | 25 | 19.8 | 16.98 | 0.0738 | 0.13 | 13.59 | 1
March | 6 | 1PM to 2PM | 61 | 45 | 26.1 | 20.9 | 17.88 | 0.0733 | 0.14 | 13.68 | 1
March | 6 | 2PM to 3PM | 63 | 46 | 26.1 | 20.9 | 18.36 | 0.0731 | 0.14 | 13.73 | 1
March | 6 | 3PM to 4PM | 64.9 | 47.2 | 27 | 21.8 | 18.98 | 0.0728 | 0.14 | 13.78 | 1
March | 6 | 4PM to 5PM | 64 | 46.2 | 25 | 19.8 | 18.46 | 0.0729 | 0.13 | 13.75 | 1
March | 6 | 5PM to 6PM | 64 | 46.7 | 27 | 21.8 | 18.76 | 0.0729 | 0.14 | 13.76 | 1
March | 6 | 6PM to 7PM | 61 | 45.3 | 27 | 21.8 | 18.02 | 0.0733 | 0.14 | 13.68 | 1
March | 6 | 7PM to 8PM | 60.1 | 44.9 | 27 | 21.8 | 17.81 | 0.0735 | 0.14 | 13.65 | 1
March | 6 | 8PM to 9PM | 57.9 | 43.6 | 26.1 | 20.9 | 17.15 | 0.0738 | 0.14 | 13.6 | 1
March | 6 | 9PM to 10PM | 55 | 42.4 | 27 | 21.8 | 16.59 | 0.0742 | 0.14 | 13.52 | 1
March | 6 | 10PM to 11PM | 52 | 41.6 | 28.9 | 23.9 | 16.18 | 0.0746 | 0.16 | 13.45 | 1
March | 6 | 11PM to 12AM | 51.1 | 40.8 | 28 | 22.9 | 15.81 | 0.0748 | 0.15 | 13.42 | 1
March | 7 | 12AM to 1AM | 48.9 | 39.7 | 28 | 22.9 | 15.29 | 0.0751 | 0.15 | 13.36 | 1
March | 7 | 1AM to 2AM | 46.9 | 38.7 | 28 | 22.9 | 14.81 | 0.0754 | 0.15 | 13.31 | 1
March | 7 | 2AM to 3AM | 46 | 37.8 | 27 | 21.8 | 14.42 | 0.0755 | 0.14 | 13.29 | 1
March | 7 | 3AM to 4AM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
March | 7 | 4AM to 5AM | 43 | 36.5 | 28 | 22.9 | 13.85 | 0.076 | 0.15 | 13.21 | 1
March | 7 | 5AM to 6AM | 42.1 | 35.7 | 27 | 21.8 | 13.46 | 0.0761 | 0.14 | 13.18 | 1
March | 7 | 6AM to 7AM | 41 | 35.5 | 28 | 22.9 | 13.38 | 0.0763 | 0.15 | 13.16 | 1
March | 7 | 7AM to 8AM | 41 | 35.5 | 28 | 22.9 | 13.38 | 0.0763 | 0.15 | 13.16 | 1
March | 7 | 8AM to 9AM | 43 | 37.3 | 30 | 25.1 | 14.19 | 0.0759 | 0.16 | 13.22 | 1
March | 7 | 9AM to 10AM | 46.9 | 39.4 | 30 | 25.1 | 15.15 | 0.0753 | 0.16 | 13.32 | 1
March | 7 | 10AM to 11AM | 50 | 41 | 30 | 25.1 | 15.89 | 0.0749 | 0.16 | 13.4 | 1
March | 7 | 11AM to 12PM | 54 | 42.6 | 28.9 | 23.9 | 16.66 | 0.0743 | 0.16 | 13.5 | 1
March | 7 | 12PM to 1PM | 55 | 43.1 | 28.9 | 23.9 | 16.92 | 0.0742 | 0.16 | 13.53 | 1
March | 7 | 1PM to 2PM | 57.9 | 45.2 | 30.9 | 26.2 | 17.97 | 0.0737 | 0.17 | 13.61 | 1
March | 7 | 2PM to 3PM | 60.1 | 47.3 | 34 | 29.8 | 19.06 | 0.0734 | 0.2 | 13.68 | 1
March | 7 | 3PM to 4PM | 60.1 | 47.3 | 34 | 29.8 | 19.06 | 0.0734 | 0.2 | 13.68 | 1
March | 7 | 4PM to 5PM | 62.1 | 48.8 | 36 | 32.3 | 19.92 | 0.0731 | 0.21 | 13.74 | 1
March | 7 | 5PM to 6PM | 61 | 48.8 | 37 | 33.7 | 19.88 | 0.0733 | 0.22 | 13.72 | 1
March | 7 | 6PM to 7PM | 59 | 47.9 | 37 | 33.7 | 19.4 | 0.0735 | 0.22 | 13.66 | 1
March | 7 | 7PM to 8PM | 57.9 | 47 | 36 | 32.3 | 18.92 | 0.0737 | 0.21 | 13.63 | 1
March | 7 | 8PM to 9PM | 55.9 | 46.1 | 36 | 32.3 | 18.44 | 0.074 | 0.21 | 13.58 | 1
March | 7 | 9PM to 10PM | 55.9 | 45.7 | 35.1 | 31.1 | 18.26 | 0.074 | 0.2 | 13.57 | 1
March | 7 | 10PM to 11PM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
March | 7 | 11PM to 12AM | 53.1 | 44 | 34 | 29.8 | 17.36 | 0.0744 | 0.2 | 13.49 | 1
March | 8 | 12AM to 1AM | 52 | 42.7 | 32 | 27.5 | 16.74 | 0.0746 | 0.18 | 13.46 | 1
March | 8 | 1AM to 2AM | 51.1 | 42.7 | 33.1 | 28.8 | 16.71 | 0.0747 | 0.19 | 13.44 | 1
March | 8 | 2AM to 3AM | 51.1 | 43 | 34 | 29.8 | 16.88 | 0.0747 | 0.2 | 13.44 | 1
March | 8 | 3AM to 4AM | 48.9 | 42.7 | 36 | 32.3 | 16.74 | 0.075 | 0.21 | 13.39 | 1
March | 8 | 4AM to 5AM | 48.9 | 41.9 | 34 | 29.8 | 16.36 | 0.075 | 0.2 | 13.39 | 1
March | 8 | 5AM to 6AM | 46.9 | 41.4 | 35.1 | 31.1 | 16.08 | 0.0753 | 0.2 | 13.34 | 1
March | 8 | 6AM to 7AM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
March | 8 | 7AM to 8AM | 46.9 | 41.4 | 35.1 | 31.1 | 16.08 | 0.0753 | 0.2 | 13.34 | 1
March | 8 | 8AM to 9AM | 51.1 | 45.4 | 39.9 | 37.8 | 18.11 | 0.0747 | 0.25 | 13.47 | 1
March | 8 | 9AM to 10AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
March | 8 | 10AM to 11AM | 64.9 | 56.1 | 50 | 55.6 | 24.25 | 0.0726 | 0.36 | 13.89 | 1
March | 8 | 11AM to 12PM | 70 | 58.5 | 51.1 | 58 | 25.84 | 0.0719 | 0.38 | 14.03 | 1
March | 8 | 12PM to 1PM | 72 | 59.3 | 51.1 | 58 | 26.32 | 0.0716 | 0.38 | 14.08 | 1
March | 8 | 1PM to 2PM | 73 | 59.6 | 51.1 | 58 | 26.59 | 0.0715 | 0.38 | 14.11 | 1
March | 8 | 2PM to 3PM | 75.9 | 61.1 | 52 | 59.9 | 27.6 | 0.0711 | 0.39 | 14.19 | 1
March | 8 | 3PM to 4PM | 75 | 59.8 | 50 | 55.6 | 26.71 | 0.0712 | 0.36 | 14.16 | 1
March | 8 | 4PM to 5PM | 75 | 59.8 | 50 | 55.6 | 26.71 | 0.0712 | 0.36 | 14.16 | 1
March | 8 | 5PM to 6PM | 73 | 59.1 | 50 | 55.6 | 26.23 | 0.0715 | 0.36 | 14.1 | 1
March | 8 | 6PM to 7PM | 71.1 | 57.9 | 48.9 | 53.4 | 25.4 | 0.0717 | 0.35 | 14.04 | 1
March | 8 | 7PM to 8PM | 68 | 57.3 | 50 | 55.6 | 25 | 0.0722 | 0.36 | 13.97 | 1
March | 8 | 8PM to 9PM | 66 | 56.5 | 50 | 55.6 | 24.52 | 0.0724 | 0.36 | 13.92 | 1
March | 8 | 9PM to 10PM | 64.9 | 56.1 | 50 | 55.6 | 24.25 | 0.0726 | 0.36 | 13.89 | 1
March | 8 | 10PM to 11PM | 64 | 56.8 | 52 | 59.9 | 24.7 | 0.0727 | 0.39 | 13.88 | 1
March | 8 | 11PM to 12AM | 63 | 57 | 53.1 | 62.4 | 24.82 | 0.0728 | 0.41 | 13.86 | 1
March | 9 | 12AM to 1AM | 63 | 57 | 53.1 | 62.4 | 24.82 | 0.0728 | 0.41 | 13.86 | 1
March | 9 | 1AM to 2AM | 63 | 57.5 | 54 | 64.5 | 25.15 | 0.0728 | 0.42 | 13.86 | 1
March | 9 | 2AM to 3AM | 61 | 56.7 | 54 | 64.5 | 24.67 | 0.0731 | 0.42 | 13.81 | 1
March | 9 | 3AM to 4AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
March | 9 | 4AM to 5AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
March | 9 | 5AM to 6AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
March | 9 | 6AM to 7AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
March | 9 | 7AM to 8AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
March | 9 | 8AM to 9AM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
March | 9 | 9AM to 10AM | 66.9 | 60.6 | 57 | 72.3 | 27.32 | 0.0722 | 0.47 | 13.99 | 1
March | 9 | 10AM to 11AM | 70 | 61.7 | 57 | 72.3 | 28.07 | 0.0718 | 0.47 | 14.07 | 1
March | 9 | 11AM to 12PM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
March | 9 | 12PM to 1PM | 71.1 | 62.1 | 57 | 72.3 | 28.34 | 0.0716 | 0.47 | 14.1 | 1
March | 9 | 1PM to 2PM | 71.1 | 62.1 | 57 | 72.3 | 28.34 | 0.0716 | 0.47 | 14.1 | 1
March | 9 | 2PM to 3PM | 71.1 | 61.5 | 55.9 | 69.4 | 27.9 | 0.0717 | 0.45 | 14.09 | 1
March | 9 | 3PM to 4PM | 69.1 | 60.8 | 55.9 | 69.4 | 27.41 | 0.0719 | 0.45 | 14.04 | 1
March | 9 | 4PM to 5PM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
March | 9 | 5PM to 6PM | 64 | 56.8 | 52 | 59.9 | 24.7 | 0.0727 | 0.39 | 13.88 | 1
March | 9 | 6PM to 7PM | 63 | 55.3 | 50 | 55.6 | 23.77 | 0.0728 | 0.36 | 13.84 | 1
March | 9 | 7PM to 8PM | 60.1 | 52.6 | 46.9 | 49.6 | 22.12 | 0.0733 | 0.32 | 13.74 | 1
March | 9 | 8PM to 9PM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
March | 9 | 9PM to 10PM | 57 | 50 | 44.1 | 44.4 | 20.57 | 0.0738 | 0.29 | 13.64 | 1
March | 9 | 10PM to 11PM | 55.9 | 47.7 | 39.9 | 37.8 | 19.29 | 0.074 | 0.25 | 13.6 | 1
March | 9 | 11PM to 12AM | 54 | 45.6 | 37 | 33.7 | 18.18 | 0.0743 | 0.22 | 13.53 | 1
March | 10 | 12AM to 1AM | 52 | 42.7 | 32 | 27.5 | 16.74 | 0.0746 | 0.18 | 13.46 | 1
March | 10 | 1AM to 2AM | 51.1 | 41.5 | 30 | 25.1 | 16.15 | 0.0747 | 0.16 | 13.43 | 1
March | 10 | 2AM to 3AM | 48.9 | 40.4 | 30 | 25.1 | 15.63 | 0.0751 | 0.16 | 13.37 | 1
March | 10 | 3AM to 4AM | 48 | 39.6 | 28.9 | 23.9 | 15.22 | 0.0752 | 0.16 | 13.34 | 1
March | 10 | 4AM to 5AM | 48 | 38.9 | 27 | 21.8 | 14.9 | 0.0752 | 0.14 | 13.34 | 1
March | 10 | 5AM to 6AM | 48 | 38.2 | 25 | 19.8 | 14.6 | 0.0752 | 0.13 | 13.33 | 1
March | 10 | 6AM to 7AM | 48.9 | 38.7 | 25 | 19.8 | 14.81 | 0.0751 | 0.13 | 13.36 | 1
March | 10 | 7AM to 8AM | 48.9 | 38.4 | 24.1 | 19 | 14.68 | 0.0751 | 0.12 | 13.35 | 1
March | 10 | 8AM to 9AM | 51.1 | 40.2 | 26.1 | 20.9 | 15.49 | 0.0748 | 0.14 | 13.42 | 1
March | 10 | 9AM to 10AM | 54 | 41.6 | 26.1 | 20.9 | 16.19 | 0.0743 | 0.14 | 13.49 | 1
March | 10 | 10AM to 11AM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
March | 10 | 11AM to 12PM | 60.1 | 44.3 | 25 | 19.8 | 17.51 | 0.0735 | 0.13 | 13.65 | 1
March | 10 | 12PM to 1PM | 62.1 | 45.2 | 25 | 19.8 | 17.98 | 0.0732 | 0.13 | 13.7 | 1
March | 10 | 1PM to 2PM | 64.9 | 45.6 | 21 | 16.4 | 18.15 | 0.0728 | 0.11 | 13.77 | 1
March | 10 | 2PM to 3PM | 66.9 | 47 | 23 | 18.1 | 18.88 | 0.0725 | 0.12 | 13.82 | 1
March | 10 | 3PM to 4PM | 68 | 47.5 | 23 | 18.1 | 19.14 | 0.0724 | 0.12 | 13.85 | 1
March | 10 | 4PM to 5PM | 69.1 | 47.7 | 21.9 | 17.1 | 19.26 | 0.0722 | 0.11 | 13.88 | 1
March | 10 | 5PM to 6PM | 69.1 | 48.2 | 24.1 | 19 | 19.55 | 0.0722 | 0.12 | 13.88 | 1
March | 10 | 6PM to 7PM | 66 | 47.4 | 26.1 | 20.9 | 19.1 | 0.0726 | 0.14 | 13.81 | 1
March | 10 | 7PM to 8PM | 66.9 | 47.8 | 26.1 | 20.9 | 19.32 | 0.0725 | 0.14 | 13.83 | 1
March | 10 | 8PM to 9PM | 64 | 46.5 | 26.1 | 20.9 | 18.62 | 0.0729 | 0.14 | 13.76 | 1
March | 10 | 9PM to 10PM | 62.1 | 45.8 | 27 | 21.8 | 18.28 | 0.0732 | 0.14 | 13.71 | 1
March | 10 | 10PM to 11PM | 60.1 | 44.9 | 27 | 21.8 | 17.81 | 0.0735 | 0.14 | 13.65 | 1
March | 10 | 11PM to 12AM | 57 | 44.1 | 28.9 | 23.9 | 17.4 | 0.0739 | 0.16 | 13.58 | 1
March | 11 | 12AM to 1AM | 55.9 | 45 | 33.1 | 28.8 | 17.89 | 0.074 | 0.19 | 13.57 | 1
March | 11 | 1AM to 2AM | 55 | 43.8 | 30.9 | 26.2 | 17.27 | 0.0742 | 0.17 | 13.54 | 1
March | 11 | 2AM to 3AM | 55 | 44.2 | 32 | 27.5 | 17.48 | 0.0741 | 0.18 | 13.54 | 1
March | 11 | 3AM to 4AM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
March | 11 | 4AM to 5AM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
March | 11 | 5AM to 6AM | 53.1 | 43.3 | 32 | 27.5 | 17 | 0.0744 | 0.18 | 13.49 | 1
March | 11 | 6AM to 7AM | 52 | 42.7 | 32 | 27.5 | 16.74 | 0.0746 | 0.18 | 13.46 | 1
March | 11 | 7AM to 8AM | 53.1 | 44.4 | 35.1 | 31.1 | 17.56 | 0.0744 | 0.2 | 13.5 | 1
March | 11 | 8AM to 9AM | 55 | 47.3 | 39.9 | 37.8 | 19.07 | 0.0741 | 0.25 | 13.57 | 1
March | 11 | 9AM to 10AM | 60.1 | 51.7 | 45 | 45.9 | 21.56 | 0.0733 | 0.3 | 13.73 | 1
March | 11 | 10AM to 11AM | 64.9 | 54.6 | 46.9 | 49.6 | 23.3 | 0.0726 | 0.32 | 13.87 | 1
March | 11 | 11AM to 12PM | 71.1 | 57.5 | 48 | 51.6 | 25.12 | 0.0718 | 0.34 | 14.04 | 1
March | 11 | 12PM to 1PM | 73.9 | 58.5 | 48 | 51.6 | 25.82 | 0.0714 | 0.34 | 14.11 | 1
March | 11 | 1PM to 2PM | 77 | 61 | 51.1 | 58 | 27.55 | 0.0709 | 0.38 | 14.22 | 1
March | 11 | 2PM to 3PM | 79 | 61.7 | 51.1 | 58 | 28.03 | 0.0707 | 0.38 | 14.27 | 1
March | 11 | 3PM to 4PM | 79 | 61.2 | 50 | 55.6 | 27.67 | 0.0707 | 0.36 | 14.26 | 1
March | 11 | 4PM to 5PM | 78.1 | 61.4 | 51.1 | 58 | 27.81 | 0.0708 | 0.38 | 14.24 | 1
March | 11 | 5PM to 6PM | 75.9 | 59.3 | 48 | 51.6 | 26.3 | 0.0711 | 0.34 | 14.17 | 1
March | 11 | 6PM to 7PM | 73.9 | 58.9 | 48.9 | 53.4 | 26.1 | 0.0714 | 0.35 | 14.12 | 1
March | 11 | 7PM to 8PM | 72 | 58.7 | 50 | 55.6 | 25.96 | 0.0716 | 0.36 | 14.07 | 1
March | 11 | 8PM to 9PM | 71.1 | 59.4 | 52 | 59.9 | 26.41 | 0.0717 | 0.39 | 14.06 | 1
March | 11 | 9PM to 10PM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
March | 11 | 10PM to 11PM | 66.9 | 59.5 | 55 | 67.2 | 26.53 | 0.0722 | 0.44 | 13.98 | 1
March | 11 | 11PM to 12AM | 66 | 58.6 | 54 | 64.5 | 25.9 | 0.0724 | 0.42 | 13.95 | 1
March | 12 | 12AM to 1AM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
March | 12 | 1AM to 2AM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
March | 12 | 2AM to 3AM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
March | 12 | 3AM to 4AM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
March | 12 | 4AM to 5AM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
March | 12 | 5AM to 6AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
March | 12 | 6AM to 7AM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
March | 12 | 7AM to 8AM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
March | 12 | 8AM to 9AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
March | 12 | 9AM to 10AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
March | 12 | 10AM to 11AM | 61 | 52.1 | 45 | 45.9 | 21.78 | 0.0732 | 0.3 | 13.75 | 1
March | 12 | 11AM to 12PM | 64 | 50.4 | 37.9 | 34.9 | 20.81 | 0.0728 | 0.23 | 13.8 | 1
March | 12 | 12PM to 1PM | 64 | 50.9 | 39 | 36.4 | 21.05 | 0.0728 | 0.24 | 13.8 | 1
March | 12 | 1PM to 2PM | 64 | 49.4 | 35.1 | 31.1 | 20.22 | 0.0728 | 0.2 | 13.79 | 1
March | 12 | 2PM to 3PM | 63 | 46.6 | 28 | 22.9 | 18.68 | 0.0731 | 0.15 | 13.73 | 1
March | 12 | 3PM to 4PM | 63 | 46 | 26.1 | 20.9 | 18.36 | 0.0731 | 0.14 | 13.73 | 1
March | 12 | 4PM to 5PM | 62.1 | 45.8 | 27 | 21.8 | 18.28 | 0.0732 | 0.14 | 13.71 | 1
March | 12 | 5PM to 6PM | 61 | 45 | 26.1 | 20.9 | 17.88 | 0.0733 | 0.14 | 13.68 | 1
March | 12 | 6PM to 7PM | 57.9 | 44.2 | 28 | 22.9 | 17.46 | 0.0738 | 0.15 | 13.6 | 1
March | 12 | 7PM to 8PM | 55.9 | 42.6 | 26.1 | 20.9 | 16.67 | 0.0741 | 0.14 | 13.54 | 1
March | 12 | 8PM to 9PM | 54 | 41.6 | 26.1 | 20.9 | 16.19 | 0.0743 | 0.14 | 13.49 | 1
March | 12 | 9PM to 10PM | 53.1 | 41.2 | 26.1 | 20.9 | 15.97 | 0.0745 | 0.14 | 13.47 | 1
March | 12 | 10PM to 11PM | 51.1 | 40.2 | 26.1 | 20.9 | 15.49 | 0.0748 | 0.14 | 13.42 | 1
March | 12 | 11PM to 12AM | 50 | 39.6 | 26.1 | 20.9 | 15.23 | 0.0749 | 0.14 | 13.39 | 1
March | 13 | 12AM to 1AM | 48 | 38.6 | 26.1 | 20.9 | 14.76 | 0.0752 | 0.14 | 13.34 | 1
March | 13 | 1AM to 2AM | 46.9 | 38 | 26.1 | 20.9 | 14.5 | 0.0754 | 0.14 | 13.31 | 1
March | 13 | 2AM to 3AM | 46 | 37.5 | 26.1 | 20.9 | 14.28 | 0.0755 | 0.14 | 13.28 | 1
March | 13 | 3AM to 4AM | 45 | 37.2 | 27 | 21.8 | 14.16 | 0.0757 | 0.14 | 13.26 | 1
March | 13 | 4AM to 5AM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
March | 13 | 5AM to 6AM | 44.1 | 37.1 | 28 | 22.9 | 14.11 | 0.0758 | 0.15 | 13.24 | 1
March | 13 | 6AM to 7AM | 42.1 | 36.1 | 28 | 22.9 | 13.64 | 0.0761 | 0.15 | 13.19 | 1
March | 13 | 7AM to 8AM | 46 | 38.5 | 28.9 | 23.9 | 14.74 | 0.0755 | 0.16 | 13.29 | 1
March | 13 | 8AM to 9AM | 52 | 41.3 | 28 | 22.9 | 16.03 | 0.0746 | 0.15 | 13.45 | 1
March | 13 | 9AM to 10AM | 55.9 | 42.9 | 27 | 21.8 | 16.81 | 0.0741 | 0.14 | 13.55 | 1
March | 13 | 10AM to 11AM | 61 | 45.3 | 27 | 21.8 | 18.02 | 0.0733 | 0.14 | 13.68 | 1
March | 13 | 11AM to 12PM | 64.9 | 47.2 | 27 | 21.8 | 18.98 | 0.0728 | 0.14 | 13.78 | 1
March | 13 | 12PM to 1PM | 69.1 | 50.2 | 30.9 | 26.2 | 20.67 | 0.0722 | 0.17 | 13.91 | 1
March | 13 | 1PM to 2PM | 72 | 52.8 | 35.1 | 31.1 | 22.14 | 0.0718 | 0.2 | 14 | 1
March | 13 | 2PM to 3PM | 75 | 55.3 | 39 | 36.4 | 23.71 | 0.0713 | 0.24 | 14.09 | 1
March | 13 | 3PM to 4PM | 75.9 | 57.2 | 43 | 42.5 | 24.88 | 0.0712 | 0.28 | 14.14 | 1
March | 13 | 4PM to 5PM | 75.9 | 58.8 | 46.9 | 49.6 | 25.97 | 0.0711 | 0.32 | 14.16 | 1
March | 13 | 5PM to 6PM | 75 | 59.3 | 48.9 | 53.4 | 26.36 | 0.0712 | 0.35 | 14.15 | 1
March | 13 | 6PM to 7PM | 73 | 58.6 | 48.9 | 53.4 | 25.88 | 0.0715 | 0.35 | 14.1 | 1
March | 13 | 7PM to 8PM | 73 | 58.6 | 48.9 | 53.4 | 25.88 | 0.0715 | 0.35 | 14.1 | 1
March | 13 | 8PM to 9PM | 70 | 57.5 | 48.9 | 53.4 | 25.13 | 0.0719 | 0.35 | 14.02 | 1
March | 13 | 9PM to 10PM | 69.1 | 58.2 | 51.1 | 58 | 25.62 | 0.072 | 0.38 | 14.01 | 1
March | 13 | 10PM to 11PM | 66 | 57.1 | 51.1 | 58 | 24.88 | 0.0724 | 0.38 | 13.92 | 1
March | 13 | 11PM to 12AM | 64 | 55.8 | 50 | 55.6 | 24.03 | 0.0727 | 0.36 | 13.87 | 1
March | 14 | 12AM to 1AM | 62.1 | 54.4 | 48.9 | 53.4 | 23.21 | 0.073 | 0.35 | 13.81 | 1
March | 14 | 1AM to 2AM | 60.1 | 53.6 | 48.9 | 53.4 | 22.72 | 0.0733 | 0.35 | 13.75 | 1
March | 14 | 2AM to 3AM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
March | 14 | 3AM to 4AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
March | 14 | 4AM to 5AM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
March | 14 | 5AM to 6AM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
March | 14 | 6AM to 7AM | 57.9 | 53.9 | 51.1 | 58 | 22.9 | 0.0735 | 0.38 | 13.71 | 1
March | 14 | 7AM to 8AM | 57.9 | 53.9 | 51.1 | 58 | 22.9 | 0.0735 | 0.38 | 13.71 | 1
March | 14 | 8AM to 9AM | 61 | 56.2 | 53.1 | 62.4 | 24.34 | 0.0731 | 0.41 | 13.81 | 1
March | 14 | 9AM to 10AM | 64 | 57.9 | 54 | 64.5 | 25.42 | 0.0726 | 0.42 | 13.89 | 1
March | 14 | 10AM to 11AM | 69.1 | 59.7 | 54 | 64.5 | 26.65 | 0.072 | 0.42 | 14.03 | 1
March | 14 | 11AM to 12PM | 71.1 | 61 | 55 | 67.2 | 27.54 | 0.0717 | 0.44 | 14.09 | 1
March | 14 | 12PM to 1PM | 72 | 60.3 | 53.1 | 62.4 | 27.02 | 0.0716 | 0.41 | 14.1 | 1
March | 14 | 1PM to 2PM | 69.1 | 58.7 | 52 | 59.9 | 25.93 | 0.072 | 0.39 | 14.01 | 1
March | 14 | 2PM to 3PM | 69.1 | 58.2 | 51.1 | 58 | 25.62 | 0.072 | 0.38 | 14.01 | 1
March | 14 | 3PM to 4PM | 68 | 57.3 | 50 | 55.6 | 25 | 0.0722 | 0.36 | 13.97 | 1
March | 14 | 4PM to 5PM | 69.1 | 57.1 | 48.9 | 53.4 | 24.91 | 0.072 | 0.35 | 13.99 | 1
March | 14 | 5PM to 6PM | 64 | 53.8 | 46 | 47.9 | 22.82 | 0.0727 | 0.31 | 13.84 | 1
March | 14 | 6PM to 7PM | 60.1 | 50.8 | 43 | 42.5 | 21.03 | 0.0733 | 0.28 | 13.72 | 1
March | 14 | 7PM to 8PM | 57.9 | 47.7 | 37.9 | 34.9 | 19.33 | 0.0737 | 0.23 | 13.64 | 1
March | 14 | 8PM to 9PM | 53.1 | 46 | 39 | 36.4 | 18.39 | 0.0744 | 0.24 | 13.52 | 1
March | 14 | 9PM to 10PM | 52 | 45.8 | 39.9 | 37.8 | 18.33 | 0.0745 | 0.25 | 13.49 | 1
March | 14 | 10PM to 11PM | 51.1 | 45.4 | 39.9 | 37.8 | 18.11 | 0.0747 | 0.25 | 13.47 | 1
March | 14 | 11PM to 12AM | 48 | 42.7 | 37 | 33.7 | 16.74 | 0.0751 | 0.22 | 13.37 | 1
March | 15 | 12AM to 1AM | 46.9 | 41.4 | 35.1 | 31.1 | 16.08 | 0.0753 | 0.2 | 13.34 | 1
March | 15 | 1AM to 2AM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
March | 15 | 2AM to 3AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
March | 15 | 3AM to 4AM | 46.9 | 39.8 | 30.9 | 26.2 | 15.32 | 0.0753 | 0.17 | 13.32 | 1
March | 15 | 4AM to 5AM | 46.9 | 39.4 | 30 | 25.1 | 15.15 | 0.0753 | 0.16 | 13.32 | 1
March | 15 | 5AM to 6AM | 46 | 38.9 | 30 | 25.1 | 14.93 | 0.0755 | 0.16 | 13.3 | 1
March | 15 | 6AM to 7AM | 45 | 37.6 | 28 | 22.9 | 14.33 | 0.0757 | 0.15 | 13.26 | 1
March | 15 | 7AM to 8AM | 46 | 38.5 | 28.9 | 23.9 | 14.74 | 0.0755 | 0.16 | 13.29 | 1
March | 15 | 8AM to 9AM | 48.9 | 39.3 | 27 | 21.8 | 15.11 | 0.0751 | 0.14 | 13.36 | 1
March | 15 | 9AM to 10AM | 51.1 | 40.2 | 26.1 | 20.9 | 15.49 | 0.0748 | 0.14 | 13.42 | 1
March | 15 | 10AM to 11AM | 54 | 41.6 | 26.1 | 20.9 | 16.19 | 0.0743 | 0.14 | 13.49 | 1
March | 15 | 11AM to 12PM | 55.9 | 43.2 | 28 | 22.9 | 16.98 | 0.074 | 0.15 | 13.55 | 1
March | 15 | 12PM to 1PM | 57.9 | 44.2 | 28 | 22.9 | 17.46 | 0.0738 | 0.15 | 13.6 | 1
March | 15 | 1PM to 2PM | 62.1 | 46.4 | 28.9 | 23.9 | 18.61 | 0.0732 | 0.16 | 13.71 | 1
March | 15 | 2PM to 3PM | 63 | 46.6 | 28 | 22.9 | 18.68 | 0.0731 | 0.15 | 13.73 | 1
March | 15 | 3PM to 4PM | 64 | 47.1 | 28 | 22.9 | 18.94 | 0.0729 | 0.15 | 13.76 | 1
March | 15 | 4PM to 5PM | 64 | 46.7 | 27 | 21.8 | 18.76 | 0.0729 | 0.14 | 13.76 | 1
March | 15 | 5PM to 6PM | 64 | 46.7 | 27 | 21.8 | 18.76 | 0.0729 | 0.14 | 13.76 | 1
March | 15 | 6PM to 7PM | 63 | 46 | 26.1 | 20.9 | 18.36 | 0.0731 | 0.14 | 13.73 | 1
March | 15 | 7PM to 8PM | 61 | 45.7 | 28 | 22.9 | 18.2 | 0.0733 | 0.15 | 13.68 | 1
March | 15 | 8PM to 9PM | 55.9 | 44.2 | 30.9 | 26.2 | 17.49 | 0.074 | 0.17 | 13.56 | 1
March | 15 | 9PM to 10PM | 55 | 43.1 | 28.9 | 23.9 | 16.92 | 0.0742 | 0.16 | 13.53 | 1
March | 15 | 10PM to 11PM | 53.1 | 41.8 | 28 | 22.9 | 16.29 | 0.0745 | 0.15 | 13.47 | 1
March | 15 | 11PM to 12AM | 53.1 | 41.8 | 28 | 22.9 | 16.29 | 0.0745 | 0.15 | 13.47 | 1
March | 16 | 12AM to 1AM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
March | 16 | 1AM to 2AM | 50 | 41.3 | 30.9 | 26.2 | 16.06 | 0.0749 | 0.17 | 13.4 | 1
March | 16 | 2AM to 3AM | 48.9 | 41.2 | 32 | 27.5 | 16 | 0.075 | 0.18 | 13.38 | 1
March | 16 | 3AM to 4AM | 48 | 40.8 | 32 | 27.5 | 15.78 | 0.0752 | 0.18 | 13.36 | 1
March | 16 | 4AM to 5AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
March | 16 | 5AM to 6AM | 46.9 | 39.8 | 30.9 | 26.2 | 15.32 | 0.0753 | 0.17 | 13.32 | 1
March | 16 | 6AM to 7AM | 46 | 39.3 | 30.9 | 26.2 | 15.1 | 0.0755 | 0.17 | 13.3 | 1
March | 16 | 7AM to 8AM | 46 | 39.3 | 30.9 | 26.2 | 15.1 | 0.0755 | 0.17 | 13.3 | 1
March | 16 | 8AM to 9AM | 46.9 | 39.8 | 30.9 | 26.2 | 15.32 | 0.0753 | 0.17 | 13.32 | 1
March | 16 | 9AM to 10AM | 50 | 41.8 | 32 | 27.5 | 16.26 | 0.0749 | 0.18 | 13.41 | 1
March | 16 | 10AM to 11AM | 53.1 | 42.8 | 30.9 | 26.2 | 16.8 | 0.0744 | 0.17 | 13.48 | 1
March | 16 | 11AM to 12PM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
March | 16 | 12PM to 1PM | 55 | 44.2 | 32 | 27.5 | 17.48 | 0.0741 | 0.18 | 13.54 | 1
March | 16 | 1PM to 2PM | 55 | 44.2 | 32 | 27.5 | 17.48 | 0.0741 | 0.18 | 13.54 | 1
March | 16 | 2PM to 3PM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
March | 16 | 3PM to 4PM | 53.1 | 42.8 | 30.9 | 26.2 | 16.8 | 0.0744 | 0.17 | 13.48 | 1
March | 16 | 4PM to 5PM | 53.1 | 43.6 | 33.1 | 28.8 | 17.19 | 0.0744 | 0.19 | 13.49 | 1
March | 16 | 5PM to 6PM | 52 | 43.9 | 35.1 | 31.1 | 17.3 | 0.0746 | 0.2 | 13.47 | 1
March | 16 | 6PM to 7PM | 51.1 | 43.8 | 36 | 32.3 | 17.26 | 0.0747 | 0.21 | 13.45 | 1
March | 16 | 7PM to 8PM | 51.1 | 44.2 | 37 | 33.7 | 17.48 | 0.0747 | 0.22 | 13.45 | 1
March | 16 | 8PM to 9PM | 48.9 | 43.5 | 37.9 | 34.9 | 17.15 | 0.075 | 0.23 | 13.4 | 1
March | 16 | 9PM to 10PM | 48.9 | 43.5 | 37.9 | 34.9 | 17.15 | 0.075 | 0.23 | 13.4 | 1
March | 16 | 10PM to 11PM | 48.9 | 44 | 39 | 36.4 | 17.38 | 0.075 | 0.24 | 13.41 | 1
March | 16 | 11PM to 12AM | 48.9 | 43.5 | 37.9 | 34.9 | 17.15 | 0.075 | 0.23 | 13.4 | 1
March | 17 | 12AM to 1AM | 48.9 | 43.5 | 37.9 | 34.9 | 17.15 | 0.075 | 0.23 | 13.4 | 1
March | 17 | 1AM to 2AM | 48.9 | 44 | 39 | 36.4 | 17.38 | 0.075 | 0.24 | 13.41 | 1
March | 17 | 2AM to 3AM | 48 | 44 | 39.9 | 37.8 | 17.37 | 0.0751 | 0.25 | 13.39 | 1
March | 17 | 3AM to 4AM | 48 | 43.6 | 39 | 36.4 | 17.16 | 0.0751 | 0.24 | 13.38 | 1
March | 17 | 4AM to 5AM | 48 | 43.1 | 37.9 | 34.9 | 16.93 | 0.0751 | 0.23 | 13.38 | 1
March | 17 | 5AM to 6AM | 46.9 | 42.2 | 37 | 33.7 | 16.48 | 0.0753 | 0.22 | 13.35 | 1
March | 17 | 6AM to 7AM | 46.9 | 41.7 | 36 | 32.3 | 16.26 | 0.0753 | 0.21 | 13.34 | 1
March | 17 | 7AM to 8AM | 46.9 | 41.7 | 36 | 32.3 | 16.26 | 0.0753 | 0.21 | 13.34 | 1
March | 17 | 8AM to 9AM | 50 | 42.9 | 35.1 | 31.1 | 16.82 | 0.0749 | 0.2 | 13.42 | 1
March | 17 | 9AM to 10AM | 53.1 | 42.8 | 30.9 | 26.2 | 16.8 | 0.0744 | 0.17 | 13.48 | 1
March | 17 | 10AM to 11AM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
March | 17 | 11AM to 12PM | 55 | 42.2 | 26.1 | 20.9 | 16.45 | 0.0742 | 0.14 | 13.52 | 1
March | 17 | 12PM to 1PM | 55.9 | 42.9 | 27 | 21.8 | 16.81 | 0.0741 | 0.14 | 13.55 | 1
March | 17 | 1PM to 2PM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
March | 17 | 2PM to 3PM | 61 | 44.2 | 23 | 18.1 | 17.45 | 0.0734 | 0.12 | 13.67 | 1
March | 17 | 3PM to 4PM | 62.1 | 44 | 19.9 | 15.6 | 17.32 | 0.0732 | 0.1 | 13.69 | 1
March | 17 | 4PM to 5PM | 62.1 | 43.7 | 19 | 14.9 | 17.22 | 0.0732 | 0.1 | 13.69 | 1
March | 17 | 5PM to 6PM | 60.1 | 42.5 | 18 | 14.2 | 16.62 | 0.0735 | 0.09 | 13.63 | 1
March | 17 | 6PM to 7PM | 57 | 41.7 | 21 | 16.4 | 16.24 | 0.0739 | 0.11 | 13.56 | 1
March | 17 | 7PM to 8PM | 53.1 | 39.2 | 19 | 14.9 | 15.05 | 0.0745 | 0.1 | 13.45 | 1
March | 17 | 8PM to 9PM | 50 | 37.3 | 18 | 14.2 | 14.2 | 0.075 | 0.09 | 13.37 | 1
March | 17 | 9PM to 10PM | 48.9 | 37.2 | 19.9 | 15.6 | 14.16 | 0.0751 | 0.1 | 13.34 | 1
March | 17 | 10PM to 11PM | 46.9 | 35.9 | 19 | 14.9 | 13.58 | 0.0754 | 0.1 | 13.29 | 1
March | 17 | 11PM to 12AM | 45 | 34.3 | 17.1 | 13.6 | 12.89 | 0.0757 | 0.09 | 13.23 | 1
March | 18 | 12AM to 1AM | 44.1 | 33.6 | 16 | 12.9 | 12.56 | 0.0759 | 0.08 | 13.21 | 1
March | 18 | 1AM to 2AM | 42.1 | 32.9 | 18 | 14.2 | 12.29 | 0.0761 | 0.09 | 13.16 | 1
March | 18 | 2AM to 3AM | 39.9 | 31.6 | 19.9 | 15.6 | 11.99 | 0.0765 | 0.1 | 13.11 | 1
March | 18 | 3AM to 4AM | 39 | 31.1 | 19.9 | 15.6 | 11.77 | 0.0766 | 0.1 | 13.08 | 1
March | 18 | 4AM to 5AM | 37.9 | 31.2 | 21.9 | 17.1 | 11.75 | 0.0768 | 0.11 | 13.06 | 1
March | 18 | 5AM to 6AM | 37 | 30.7 | 21.9 | 17.1 | 11.53 | 0.0769 | 0.11 | 13.04 | 1
March | 18 | 6AM to 7AM | 36 | 29.8 | 21 | 16.4 | 11.16 | 0.0771 | 0.11 | 13.01 | 1
March | 18 | 7AM to 8AM | 37 | 30.4 | 21 | 16.4 | 11.42 | 0.0769 | 0.11 | 13.03 | 1
March | 18 | 8AM to 9AM | 39 | 31.1 | 19.9 | 15.6 | 11.77 | 0.0766 | 0.1 | 13.08 | 1
March | 18 | 9AM to 10AM | 41 | 30.9 | 15.1 | 12.3 | 11.74 | 0.0763 | 0.08 | 13.12 | 1
March | 18 | 10AM to 11AM | 44.1 | 32.5 | 10.9 | 10 | 12.12 | 0.0759 | 0.07 | 13.2 | 1
March | 18 | 11AM to 12PM | 46 | 34 | 12.9 | 11.1 | 12.76 | 0.0756 | 0.07 | 13.25 | 1
March | 18 | 12PM to 1PM | 48.9 | 35.1 | 10 | 9.6 | 13.23 | 0.0752 | 0.06 | 13.32 | 1
March | 18 | 1PM to 2PM | 50 | 36.1 | 12 | 10.6 | 13.64 | 0.075 | 0.07 | 13.36 | 1
March | 18 | 2PM to 3PM | 52 | 37 | 10.9 | 10 | 14.03 | 0.0747 | 0.07 | 13.41 | 1
March | 18 | 3PM to 4PM | 53.1 | 37.2 | 9 | 9.1 | 14.14 | 0.0746 | 0.06 | 13.43 | 1
March | 18 | 4PM to 5PM | 52 | 36.6 | 9 | 9.1 | 13.88 | 0.0747 | 0.06 | 13.4 | 1
March | 18 | 5PM to 6PM | 52 | 36.8 | 10 | 9.6 | 13.96 | 0.0747 | 0.06 | 13.4 | 1
March | 18 | 6PM to 7PM | 48.9 | 35.1 | 10 | 9.6 | 13.23 | 0.0752 | 0.06 | 13.32 | 1
March | 18 | 7PM to 8PM | 46.9 | 34.5 | 12.9 | 11.1 | 12.98 | 0.0754 | 0.07 | 13.28 | 1
March | 18 | 8PM to 9PM | 46 | 34.5 | 15.1 | 12.3 | 12.95 | 0.0756 | 0.08 | 13.26 | 1
March | 18 | 9PM to 10PM | 43 | 33.2 | 17.1 | 13.6 | 12.41 | 0.076 | 0.09 | 13.18 | 1
March | 18 | 10PM to 11PM | 39 | 31.1 | 19.9 | 15.6 | 11.77 | 0.0766 | 0.1 | 13.08 | 1
March | 18 | 11PM to 12AM | 39.9 | 31.4 | 19 | 14.9 | 11.89 | 0.0765 | 0.1 | 13.1 | 1
March | 19 | 12AM to 1AM | 39 | 30.9 | 19 | 14.9 | 11.67 | 0.0766 | 0.1 | 13.08 | 1
March | 19 | 1AM to 2AM | 37.9 | 30.3 | 19 | 14.9 | 11.41 | 0.0768 | 0.1 | 13.05 | 1
March | 19 | 2AM to 3AM | 37.9 | 29.5 | 16 | 12.9 | 11.09 | 0.0768 | 0.08 | 13.05 | 1
March | 19 | 3AM to 4AM | 35.1 | 29 | 19.9 | 15.6 | 10.82 | 0.0772 | 0.1 | 12.98 | 1
March | 19 | 4AM to 5AM | 36 | 29.2 | 19 | 14.9 | 10.93 | 0.0771 | 0.1 | 13 | 1
March | 19 | 5AM to 6AM | 35.1 | 29 | 19.9 | 15.6 | 10.82 | 0.0772 | 0.1 | 12.98 | 1
March | 19 | 6AM to 7AM | 34 | 28.7 | 21 | 16.4 | 10.68 | 0.0774 | 0.11 | 12.95 | 1
March | 19 | 7AM to 8AM | 39 | 30.9 | 19 | 14.9 | 11.67 | 0.0766 | 0.1 | 13.08 | 1
March | 19 | 8AM to 9AM | 43 | 32 | 15.1 | 12.3 | 12.22 | 0.076 | 0.08 | 13.18 | 1
March | 19 | 9AM to 10AM | 46 | 33.5 | 10 | 9.6 | 12.53 | 0.0756 | 0.06 | 13.25 | 1
March | 19 | 10AM to 11AM | 48.9 | 35.3 | 10.9 | 10 | 13.29 | 0.0752 | 0.07 | 13.33 | 1
March | 19 | 11AM to 12PM | 53.1 | 37.5 | 10.9 | 10 | 14.29 | 0.0745 | 0.07 | 13.43 | 1
March | 19 | 12PM to 1PM | 55 | 38.5 | 10 | 9.6 | 14.7 | 0.0743 | 0.06 | 13.48 | 1
March | 19 | 1PM to 2PM | 59 | 40.7 | 10.9 | 10 | 15.72 | 0.0737 | 0.07 | 13.59 | 1
March | 19 | 2PM to 3PM | 61 | 41.8 | 12 | 10.6 | 16.28 | 0.0734 | 0.07 | 13.64 | 1
March | 19 | 3PM to 4PM | 62.1 | 42.5 | 12.9 | 11.1 | 16.62 | 0.0733 | 0.07 | 13.67 | 1
March | 19 | 4PM to 5PM | 62.1 | 42.9 | 15.1 | 12.3 | 16.81 | 0.0732 | 0.08 | 13.68 | 1
March | 19 | 5PM to 6PM | 61 | 42.4 | 15.1 | 12.3 | 16.55 | 0.0734 | 0.08 | 13.65 | 1
March | 19 | 6PM to 7PM | 59 | 41.4 | 15.1 | 12.3 | 16.07 | 0.0737 | 0.08 | 13.6 | 1
March | 19 | 7PM to 8PM | 57.9 | 40.6 | 14 | 11.7 | 15.72 | 0.0738 | 0.08 | 13.57 | 1
March | 19 | 8PM to 9PM | 55.9 | 39.8 | 15.1 | 12.3 | 15.34 | 0.0741 | 0.08 | 13.52 | 1
March | 19 | 9PM to 10PM | 54 | 39 | 16 | 12.9 | 14.95 | 0.0744 | 0.08 | 13.47 | 1
March | 19 | 10PM to 11PM | 51.1 | 37.7 | 17.1 | 13.6 | 14.36 | 0.0748 | 0.09 | 13.39 | 1
March | 19 | 11PM to 12AM | 48 | 36.2 | 18 | 14.2 | 13.72 | 0.0753 | 0.09 | 13.31 | 1
March | 20 | 12AM to 1AM | 46.9 | 35.7 | 18 | 14.2 | 13.46 | 0.0754 | 0.09 | 13.29 | 1
March | 20 | 1AM to 2AM | 46.9 | 35.7 | 18 | 14.2 | 13.46 | 0.0754 | 0.09 | 13.29 | 1
March | 20 | 2AM to 3AM | 45 | 34.3 | 17.1 | 13.6 | 12.89 | 0.0757 | 0.09 | 13.23 | 1
March | 20 | 3AM to 4AM | 44.1 | 33.8 | 17.1 | 13.6 | 12.67 | 0.0759 | 0.09 | 13.21 | 1
March | 20 | 4AM to 5AM | 41 | 33.4 | 21.9 | 17.1 | 12.49 | 0.0763 | 0.11 | 13.14 | 1
March | 20 | 5AM to 6AM | 41 | 33.7 | 23 | 18.1 | 12.63 | 0.0763 | 0.12 | 13.14 | 1
March | 20 | 6AM to 7AM | 41 | 34.1 | 24.1 | 19 | 12.77 | 0.0763 | 0.12 | 13.15 | 1
March | 20 | 7AM to 8AM | 42.1 | 34.7 | 24.1 | 19 | 13.03 | 0.0761 | 0.12 | 13.17 | 1
March | 20 | 8AM to 9AM | 46.9 | 38 | 26.1 | 20.9 | 14.5 | 0.0754 | 0.14 | 13.31 | 1
March | 20 | 9AM to 10AM | 53.1 | 41.8 | 28 | 22.9 | 16.29 | 0.0745 | 0.15 | 13.47 | 1
March | 20 | 10AM to 11AM | 59 | 43.8 | 25 | 19.8 | 17.24 | 0.0736 | 0.13 | 13.62 | 1
March | 20 | 11AM to 12PM | 64 | 46.2 | 25 | 19.8 | 18.46 | 0.0729 | 0.13 | 13.75 | 1
March | 20 | 12PM to 1PM | 64.9 | 46.1 | 23 | 18.1 | 18.4 | 0.0728 | 0.12 | 13.77 | 1
March | 20 | 1PM to 2PM | 66 | 46.3 | 21.9 | 17.1 | 18.52 | 0.0727 | 0.11 | 13.8 | 1
March | 20 | 2PM to 3PM | 68 | 47.2 | 21.9 | 17.1 | 19 | 0.0724 | 0.11 | 13.85 | 1
March | 20 | 3PM to 4PM | 68 | 47.5 | 23 | 18.1 | 19.14 | 0.0724 | 0.12 | 13.85 | 1
March | 20 | 4PM to 5PM | 66.9 | 47 | 23 | 18.1 | 18.88 | 0.0725 | 0.12 | 13.82 | 1
March | 20 | 5PM to 6PM | 66 | 46.8 | 24.1 | 19 | 18.81 | 0.0727 | 0.12 | 13.8 | 1
March | 20 | 6PM to 7PM | 64 | 46.5 | 26.1 | 20.9 | 18.62 | 0.0729 | 0.14 | 13.76 | 1
March | 20 | 7PM to 8PM | 62.1 | 47.1 | 30.9 | 26.2 | 18.97 | 0.0732 | 0.17 | 13.72 | 1
March | 20 | 8PM to 9PM | 61 | 47 | 32 | 27.5 | 18.92 | 0.0733 | 0.18 | 13.7 | 1
March | 20 | 9PM to 10PM | 60.1 | 46.6 | 32 | 27.5 | 18.7 | 0.0734 | 0.18 | 13.67 | 1
March | 20 | 10PM to 11PM | 59 | 46.1 | 32 | 27.5 | 18.44 | 0.0736 | 0.18 | 13.64 | 1
March | 20 | 11PM to 12AM | 59 | 46.1 | 32 | 27.5 | 18.44 | 0.0736 | 0.18 | 13.64 | 1
March | 21 | 12AM to 1AM | 59 | 46.5 | 33.1 | 28.8 | 18.63 | 0.0736 | 0.19 | 13.65 | 1
March | 21 | 1AM to 2AM | 57.9 | 47.7 | 37.9 | 34.9 | 19.33 | 0.0737 | 0.23 | 13.64 | 1
March | 21 | 2AM to 3AM | 55.9 | 47.3 | 39 | 36.4 | 19.08 | 0.074 | 0.24 | 13.59 | 1
March | 21 | 3AM to 4AM | 55.9 | 47.7 | 39.9 | 37.8 | 19.29 | 0.074 | 0.25 | 13.6 | 1
March | 21 | 4AM to 5AM | 53.1 | 48.7 | 45 | 45.9 | 19.85 | 0.0743 | 0.3 | 13.54 | 1
March | 21 | 5AM to 6AM | 51.1 | 48.8 | 46.9 | 49.6 | 19.93 | 0.0746 | 0.32 | 13.5 | 1
March | 21 | 6AM to 7AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
March | 21 | 7AM to 8AM | 51.1 | 48.8 | 46.9 | 49.6 | 19.93 | 0.0746 | 0.32 | 13.5 | 1
March | 21 | 8AM to 9AM | 51.1 | 48.8 | 46.9 | 49.6 | 19.93 | 0.0746 | 0.32 | 13.5 | 1
March | 21 | 9AM to 10AM | 52 | 49.8 | 48 | 51.6 | 20.48 | 0.0744 | 0.34 | 13.53 | 1
March | 21 | 10AM to 11AM | 53.1 | 50.2 | 48 | 51.6 | 20.74 | 0.0743 | 0.34 | 13.56 | 1
March | 21 | 11AM to 12PM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
March | 21 | 12PM to 1PM | 55 | 51.6 | 48.9 | 53.4 | 21.5 | 0.074 | 0.35 | 13.62 | 1
March | 21 | 1PM to 2PM | 55 | 51.6 | 48.9 | 53.4 | 21.5 | 0.074 | 0.35 | 13.62 | 1
March | 21 | 2PM to 3PM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
March | 21 | 3PM to 4PM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
March | 21 | 4PM to 5PM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
March | 21 | 5PM to 6PM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
March | 21 | 6PM to 7PM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
March | 21 | 7PM to 8PM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
March | 21 | 8PM to 9PM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
March | 21 | 9PM to 10PM | 51.1 | 49.9 | 48.9 | 53.4 | 20.53 | 0.0746 | 0.35 | 13.52 | 1
March | 21 | 10PM to 11PM | 48 | 47.4 | 46.9 | 49.6 | 19.19 | 0.075 | 0.32 | 13.42 | 1
March | 21 | 11PM to 12AM | 46.9 | 46.5 | 46 | 47.9 | 18.67 | 0.0752 | 0.31 | 13.39 | 1
March | 22 | 12AM to 1AM | 46.9 | 45.4 | 44.1 | 44.4 | 18.13 | 0.0752 | 0.29 | 13.38 | 1
March | 22 | 1AM to 2AM | 46 | 44.5 | 43 | 42.5 | 17.63 | 0.0754 | 0.28 | 13.35 | 1
March | 22 | 2AM to 3AM | 45 | 43.5 | 42.1 | 41.1 | 17.14 | 0.0755 | 0.27 | 13.32 | 1
March | 22 | 3AM to 4AM | 44.1 | 42.5 | 41 | 39.4 | 16.66 | 0.0757 | 0.26 | 13.29 | 1
March | 22 | 4AM to 5AM | 43 | 41.5 | 39.9 | 37.8 | 16.15 | 0.0759 | 0.25 | 13.25 | 1
March | 22 | 5AM to 6AM | 42.1 | 40.1 | 37.9 | 34.9 | 15.49 | 0.076 | 0.23 | 13.22 | 1
March | 22 | 6AM to 7AM | 41 | 39.6 | 37.9 | 34.9 | 15.23 | 0.0762 | 0.23 | 13.19 | 1
March | 22 | 7AM to 8AM | 41 | 39.6 | 37.9 | 34.9 | 15.23 | 0.0762 | 0.23 | 13.19 | 1
March | 22 | 8AM to 9AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
March | 22 | 9AM to 10AM | 39.9 | 38.6 | 37 | 33.7 | 14.78 | 0.0763 | 0.22 | 13.16 | 1
March | 22 | 10AM to 11AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
March | 22 | 11AM to 12PM | 39.9 | 38.6 | 37 | 33.7 | 14.78 | 0.0763 | 0.22 | 13.16 | 1
March | 22 | 12PM to 1PM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
March | 22 | 1PM to 2PM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
March | 22 | 2PM to 3PM | 41 | 39.6 | 37.9 | 34.9 | 15.23 | 0.0762 | 0.23 | 13.19 | 1
March | 22 | 3PM to 4PM | 42.1 | 40.1 | 37.9 | 34.9 | 15.49 | 0.076 | 0.23 | 13.22 | 1
March | 22 | 4PM to 5PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
March | 22 | 5PM to 6PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
March | 22 | 6PM to 7PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
March | 22 | 7PM to 8PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
March | 22 | 8PM to 9PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
March | 22 | 9PM to 10PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
March | 22 | 10PM to 11PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
March | 22 | 11PM to 12AM | 41 | 40 | 39 | 36.4 | 15.46 | 0.0762 | 0.24 | 13.2 | 1
March | 23 | 12AM to 1AM | 41 | 40 | 39 | 36.4 | 15.46 | 0.0762 | 0.24 | 13.2 | 1
March | 23 | 1AM to 2AM | 41 | 40 | 39 | 36.4 | 15.46 | 0.0762 | 0.24 | 13.2 | 1
March | 23 | 2AM to 3AM | 41 | 40 | 39 | 36.4 | 15.46 | 0.0762 | 0.24 | 13.2 | 1
March | 23 | 3AM to 4AM | 41 | 40 | 39 | 36.4 | 15.46 | 0.0762 | 0.24 | 13.2 | 1
March | 23 | 4AM to 5AM | 43 | 41.5 | 39.9 | 37.8 | 16.15 | 0.0759 | 0.25 | 13.25 | 1
March | 23 | 5AM to 6AM | 43 | 41.5 | 39.9 | 37.8 | 16.15 | 0.0759 | 0.25 | 13.25 | 1
March | 23 | 6AM to 7AM | 43 | 42 | 41 | 39.4 | 16.4 | 0.0758 | 0.26 | 13.26 | 1
March | 23 | 7AM to 8AM | 44.1 | 42.5 | 41 | 39.4 | 16.66 | 0.0757 | 0.26 | 13.29 | 1
March | 23 | 8AM to 9AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
March | 23 | 9AM to 10AM | 50 | 47.9 | 46 | 47.9 | 19.41 | 0.0747 | 0.31 | 13.47 | 1
March | 23 | 10AM to 11AM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
March | 23 | 11AM to 12PM | 57.9 | 50.8 | 45 | 45.9 | 21.04 | 0.0736 | 0.3 | 13.67 | 1
March | 23 | 12PM to 1PM | 57.9 | 51.3 | 46 | 47.9 | 21.34 | 0.0736 | 0.31 | 13.68 | 1
March | 23 | 1PM to 2PM | 59 | 51.8 | 46 | 47.9 | 21.6 | 0.0735 | 0.31 | 13.71 | 1
March | 23 | 2PM to 3PM | 63 | 52.5 | 44.1 | 44.4 | 22.02 | 0.0729 | 0.29 | 13.8 | 1
March | 23 | 3PM to 4PM | 64 | 52.9 | 44.1 | 44.4 | 22.28 | 0.0728 | 0.29 | 13.83 | 1
March | 23 | 4PM to 5PM | 64.9 | 52.5 | 42.1 | 41.1 | 21.99 | 0.0727 | 0.27 | 13.84 | 1
March | 23 | 5PM to 6PM | 64 | 52.5 | 43 | 42.5 | 22 | 0.0728 | 0.28 | 13.82 | 1
March | 23 | 6PM to 7PM | 61 | 51.2 | 43 | 42.5 | 21.25 | 0.0732 | 0.28 | 13.74 | 1
March | 23 | 7PM to 8PM | 61 | 50.8 | 42.1 | 41.1 | 21.03 | 0.0732 | 0.27 | 13.74 | 1
March | 23 | 8PM to 9PM | 60.1 | 50.8 | 43 | 42.5 | 21.03 | 0.0733 | 0.28 | 13.72 | 1
March | 23 | 9PM to 10PM | 57.9 | 50.4 | 44.1 | 44.4 | 20.79 | 0.0736 | 0.29 | 13.67 | 1
March | 23 | 10PM to 11PM | 57.9 | 50.8 | 45 | 45.9 | 21.04 | 0.0736 | 0.3 | 13.67 | 1
March | 23 | 11PM to 12AM | 57.9 | 51.3 | 46 | 47.9 | 21.34 | 0.0736 | 0.31 | 13.68 | 1
March | 24 | 12AM to 1AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
March | 24 | 1AM to 2AM | 54 | 51.1 | 48.9 | 53.4 | 21.23 | 0.0741 | 0.35 | 13.59 | 1
March | 24 | 2AM to 3AM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
March | 24 | 3AM to 4AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
March | 24 | 4AM to 5AM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
March | 24 | 5AM to 6AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
March | 24 | 6AM to 7AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
March | 24 | 7AM to 8AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
March | 24 | 8AM to 9AM | 53.1 | 50.2 | 48 | 51.6 | 20.74 | 0.0743 | 0.34 | 13.56 | 1
March | 24 | 9AM to 10AM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
March | 24 | 10AM to 11AM | 57 | 49.1 | 42.1 | 41.1 | 20.07 | 0.0738 | 0.27 | 13.63 | 1
March | 24 | 11AM to 12PM | 55.9 | 48.6 | 42.1 | 41.1 | 19.8 | 0.0739 | 0.27 | 13.61 | 1
March | 24 | 12PM to 1PM | 60.1 | 50.4 | 42.1 | 41.1 | 20.81 | 0.0733 | 0.27 | 13.71 | 1
March | 24 | 1PM to 2PM | 61 | 49.5 | 39 | 36.4 | 20.3 | 0.0732 | 0.24 | 13.72 | 1
March | 24 | 2PM to 3PM | 63 | 49.6 | 37 | 33.7 | 20.36 | 0.073 | 0.22 | 13.77 | 1
March | 24 | 3PM to 4PM | 63 | 48.9 | 35.1 | 31.1 | 19.96 | 0.073 | 0.2 | 13.76 | 1
March | 24 | 4PM to 5PM | 63 | 48.9 | 35.1 | 31.1 | 19.96 | 0.073 | 0.2 | 13.76 | 1
March | 24 | 5PM to 6PM | 62.1 | 48.2 | 34 | 29.8 | 19.54 | 0.0731 | 0.2 | 13.73 | 1
March | 24 | 6PM to 7PM | 60.1 | 47.6 | 35.1 | 31.1 | 19.26 | 0.0734 | 0.2 | 13.68 | 1
March | 24 | 7PM to 8PM | 57 | 45.5 | 33.1 | 28.8 | 18.15 | 0.0739 | 0.19 | 13.6 | 1
March | 24 | 8PM to 9PM | 55.9 | 44.7 | 32 | 27.5 | 17.7 | 0.074 | 0.18 | 13.56 | 1
March | 24 | 9PM to 10PM | 54 | 43 | 30 | 25.1 | 16.85 | 0.0743 | 0.16 | 13.5 | 1
March | 24 | 10PM to 11PM | 51.1 | 41.1 | 28.9 | 23.9 | 15.96 | 0.0747 | 0.16 | 13.42 | 1
March | 24 | 11PM to 12AM | 48.9 | 40 | 28.9 | 23.9 | 15.44 | 0.0751 | 0.16 | 13.37 | 1
March | 25 | 12AM to 1AM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
March | 25 | 1AM to 2AM | 44.1 | 38.2 | 30.9 | 26.2 | 14.62 | 0.0758 | 0.17 | 13.25 | 1
March | 25 | 2AM to 3AM | 43 | 38.1 | 32 | 27.5 | 14.57 | 0.0759 | 0.18 | 13.22 | 1
March | 25 | 3AM to 4AM | 42.1 | 37.2 | 30.9 | 26.2 | 14.14 | 0.0761 | 0.17 | 13.2 | 1
March | 25 | 4AM to 5AM | 41 | 36.6 | 30.9 | 26.2 | 13.88 | 0.0762 | 0.17 | 13.17 | 1
March | 25 | 5AM to 6AM | 39.9 | 36 | 30.9 | 26.2 | 13.62 | 0.0764 | 0.17 | 13.14 | 1
March | 25 | 6AM to 7AM | 42.1 | 37.2 | 30.9 | 26.2 | 14.14 | 0.0761 | 0.17 | 13.2 | 1
March | 25 | 7AM to 8AM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
March | 25 | 8AM to 9AM | 50 | 41.8 | 32 | 27.5 | 16.26 | 0.0749 | 0.18 | 13.41 | 1
March | 25 | 9AM to 10AM | 52 | 43.1 | 33.1 | 28.8 | 16.93 | 0.0746 | 0.19 | 13.46 | 1
March | 25 | 10AM to 11AM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
March | 25 | 11AM to 12PM | 55 | 44.2 | 32 | 27.5 | 17.48 | 0.0741 | 0.18 | 13.54 | 1
March | 25 | 12PM to 1PM | 57 | 44.1 | 28.9 | 23.9 | 17.4 | 0.0739 | 0.16 | 13.58 | 1
March | 25 | 1PM to 2PM | 59 | 45 | 28.9 | 23.9 | 17.87 | 0.0736 | 0.16 | 13.63 | 1
March | 25 | 2PM to 3PM | 61 | 45.9 | 28.9 | 23.9 | 18.35 | 0.0733 | 0.16 | 13.68 | 1
March | 25 | 3PM to 4PM | 62.1 | 46.4 | 28.9 | 23.9 | 18.61 | 0.0732 | 0.16 | 13.71 | 1
March | 25 | 4PM to 5PM | 62.1 | 45.6 | 26.1 | 20.9 | 18.14 | 0.0732 | 0.14 | 13.7 | 1
March | 25 | 5PM to 6PM | 61 | 45.3 | 27 | 21.8 | 18.02 | 0.0733 | 0.14 | 13.68 | 1
March | 25 | 6PM to 7PM | 59 | 45 | 28.9 | 23.9 | 17.87 | 0.0736 | 0.16 | 13.63 | 1
March | 25 | 7PM to 8PM | 55.9 | 44.2 | 30.9 | 26.2 | 17.49 | 0.074 | 0.17 | 13.56 | 1
March | 25 | 8PM to 9PM | 55 | 44.2 | 32 | 27.5 | 17.48 | 0.0741 | 0.18 | 13.54 | 1
March | 25 | 9PM to 10PM | 52 | 42.7 | 32 | 27.5 | 16.74 | 0.0746 | 0.18 | 13.46 | 1
March | 25 | 10PM to 11PM | 48.9 | 41.2 | 32 | 27.5 | 16 | 0.075 | 0.18 | 13.38 | 1
March | 25 | 11PM to 12AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
March | 26 | 12AM to 1AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
March | 26 | 1AM to 2AM | 46 | 40.1 | 33.1 | 28.8 | 15.5 | 0.0755 | 0.19 | 13.31 | 1
March | 26 | 2AM to 3AM | 46 | 40.1 | 33.1 | 28.8 | 15.5 | 0.0755 | 0.19 | 13.31 | 1
March | 26 | 3AM to 4AM | 46 | 40.1 | 33.1 | 28.8 | 15.5 | 0.0755 | 0.19 | 13.31 | 1
March | 26 | 4AM to 5AM | 44.1 | 38.7 | 32 | 27.5 | 14.83 | 0.0758 | 0.18 | 13.25 | 1
March | 26 | 5AM to 6AM | 43 | 38.5 | 33.1 | 28.8 | 14.76 | 0.0759 | 0.19 | 13.23 | 1
March | 26 | 6AM to 7AM | 42.1 | 37.2 | 30.9 | 26.2 | 14.14 | 0.0761 | 0.17 | 13.2 | 1
March | 26 | 7AM to 8AM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
March | 26 | 8AM to 9AM | 48.9 | 41.2 | 32 | 27.5 | 16 | 0.075 | 0.18 | 13.38 | 1
March | 26 | 9AM to 10AM | 54 | 44.1 | 33.1 | 28.8 | 17.41 | 0.0743 | 0.19 | 13.52 | 1
March | 26 | 10AM to 11AM | 57.9 | 46 | 33.1 | 28.8 | 18.37 | 0.0737 | 0.19 | 13.62 | 1
March | 26 | 11AM to 12PM | 62.1 | 46.4 | 28.9 | 23.9 | 18.61 | 0.0732 | 0.16 | 13.71 | 1
March | 26 | 12PM to 1PM | 64 | 47.7 | 30 | 25.1 | 19.28 | 0.0729 | 0.16 | 13.77 | 1
March | 26 | 1PM to 2PM | 66 | 47.6 | 27 | 21.8 | 19.24 | 0.0726 | 0.14 | 13.81 | 1
March | 26 | 2PM to 3PM | 68 | 48.8 | 28 | 22.9 | 19.89 | 0.0724 | 0.15 | 13.87 | 1
March | 26 | 3PM to 4PM | 69.1 | 49 | 27 | 21.8 | 19.98 | 0.0722 | 0.14 | 13.89 | 1
March | 26 | 4PM to 5PM | 68 | 48.5 | 27 | 21.8 | 19.72 | 0.0724 | 0.14 | 13.86 | 1
March | 26 | 5PM to 6PM | 68 | 48.5 | 27 | 21.8 | 19.72 | 0.0724 | 0.14 | 13.86 | 1
March | 26 | 6PM to 7PM | 66 | 48 | 28 | 22.9 | 19.42 | 0.0726 | 0.15 | 13.81 | 1
March | 26 | 7PM to 8PM | 64.9 | 47.5 | 28 | 22.9 | 19.16 | 0.0728 | 0.15 | 13.79 | 1
March | 26 | 8PM to 9PM | 62.1 | 46.2 | 28 | 22.9 | 18.46 | 0.0732 | 0.15 | 13.71 | 1
March | 26 | 9PM to 10PM | 59 | 45 | 28.9 | 23.9 | 17.87 | 0.0736 | 0.16 | 13.63 | 1
March | 26 | 10PM to 11PM | 55.9 | 44.2 | 30.9 | 26.2 | 17.49 | 0.074 | 0.17 | 13.56 | 1
March | 26 | 11PM to 12AM | 55 | 43.8 | 30.9 | 26.2 | 17.27 | 0.0742 | 0.17 | 13.54 | 1
March | 27 | 12AM to 1AM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
March | 27 | 1AM to 2AM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
March | 27 | 2AM to 3AM | 51.1 | 41.5 | 30 | 25.1 | 16.15 | 0.0747 | 0.16 | 13.43 | 1
March | 27 | 3AM to 4AM | 50 | 41.3 | 30.9 | 26.2 | 16.06 | 0.0749 | 0.17 | 13.4 | 1
March | 27 | 4AM to 5AM | 48 | 40.3 | 30.9 | 26.2 | 15.58 | 0.0752 | 0.17 | 13.35 | 1
March | 27 | 5AM to 6AM | 50 | 41.3 | 30.9 | 26.2 | 16.06 | 0.0749 | 0.17 | 13.4 | 1
March | 27 | 6AM to 7AM | 48 | 41.1 | 33.1 | 28.8 | 15.97 | 0.0752 | 0.19 | 13.36 | 1
March | 27 | 7AM to 8AM | 51.1 | 45 | 39 | 36.4 | 17.91 | 0.0747 | 0.24 | 13.46 | 1
March | 27 | 8AM to 9AM | 55 | 48.2 | 42.1 | 41.1 | 19.58 | 0.0741 | 0.27 | 13.58 | 1
March | 27 | 9AM to 10AM | 60.1 | 51.3 | 44.1 | 44.4 | 21.32 | 0.0733 | 0.29 | 13.73 | 1
March | 27 | 10AM to 11AM | 64.9 | 51.6 | 39.9 | 37.8 | 21.47 | 0.0727 | 0.25 | 13.83 | 1
March | 27 | 11AM to 12PM | 69.1 | 52.6 | 37.9 | 34.9 | 22.03 | 0.0721 | 0.23 | 13.93 | 1
March | 27 | 12PM to 1PM | 71.1 | 53.8 | 39 | 36.4 | 22.75 | 0.0719 | 0.24 | 13.99 | 1
March | 27 | 1PM to 2PM | 70 | 54.1 | 41 | 39.4 | 22.94 | 0.072 | 0.26 | 13.97 | 1
March | 27 | 2PM to 3PM | 71.1 | 55.3 | 43 | 42.5 | 23.7 | 0.0718 | 0.28 | 14.01 | 1
March | 27 | 3PM to 4PM | 71.1 | 56.6 | 46 | 47.9 | 24.53 | 0.0718 | 0.31 | 14.03 | 1
March | 27 | 4PM to 5PM | 70 | 56.2 | 46 | 47.9 | 24.27 | 0.0719 | 0.31 | 14 | 1
March | 27 | 5PM to 6PM | 66 | 56 | 48.9 | 53.4 | 24.17 | 0.0724 | 0.35 | 13.91 | 1
March | 27 | 6PM to 7PM | 64 | 56.3 | 51.1 | 58 | 24.39 | 0.0727 | 0.38 | 13.87 | 1
March | 27 | 7PM to 8PM | 64.9 | 56.7 | 51.1 | 58 | 24.61 | 0.0726 | 0.38 | 13.9 | 1
March | 27 | 8PM to 9PM | 64.9 | 56.7 | 51.1 | 58 | 24.61 | 0.0726 | 0.38 | 13.9 | 1
March | 27 | 9PM to 10PM | 64.9 | 56.7 | 51.1 | 58 | 24.61 | 0.0726 | 0.38 | 13.9 | 1
March | 27 | 10PM to 11PM | 64.9 | 56.7 | 51.1 | 58 | 24.61 | 0.0726 | 0.38 | 13.9 | 1
March | 27 | 11PM to 12AM | 64.9 | 57.7 | 53.1 | 62.4 | 25.31 | 0.0725 | 0.41 | 13.91 | 1
March | 28 | 12AM to 1AM | 64 | 57.9 | 54 | 64.5 | 25.42 | 0.0726 | 0.42 | 13.89 | 1
March | 28 | 1AM to 2AM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
March | 28 | 2AM to 3AM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
March | 28 | 3AM to 4AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
March | 28 | 4AM to 5AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
March | 28 | 5AM to 6AM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
March | 28 | 6AM to 7AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
March | 28 | 7AM to 8AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
March | 28 | 8AM to 9AM | 60.1 | 58.2 | 57 | 72.3 | 25.65 | 0.0731 | 0.47 | 13.81 | 1
March | 28 | 9AM to 10AM | 62.1 | 58.9 | 57 | 72.3 | 26.13 | 0.0729 | 0.47 | 13.86 | 1
March | 28 | 10AM to 11AM | 64 | 59.6 | 57 | 72.3 | 26.62 | 0.0726 | 0.47 | 13.92 | 1
March | 28 | 11AM to 12PM | 66.9 | 61.8 | 59 | 77.7 | 28.17 | 0.0722 | 0.5 | 14.01 | 1
March | 28 | 12PM to 1PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
March | 28 | 1PM to 2PM | 73.9 | 63 | 57 | 72.3 | 29.04 | 0.0712 | 0.47 | 14.18 | 1
March | 28 | 2PM to 3PM | 73.9 | 63 | 57 | 72.3 | 29.04 | 0.0712 | 0.47 | 14.18 | 1
March | 28 | 3PM to 4PM | 75 | 63.4 | 57 | 72.3 | 29.3 | 0.0711 | 0.47 | 14.21 | 1
March | 28 | 4PM to 5PM | 77 | 64.5 | 57.9 | 74.7 | 30.17 | 0.0708 | 0.48 | 14.27 | 1
March | 28 | 5PM to 6PM | 75.9 | 64.2 | 57.9 | 74.7 | 29.9 | 0.071 | 0.48 | 14.24 | 1
March | 28 | 6PM to 7PM | 75 | 63.9 | 57.9 | 74.7 | 29.68 | 0.0711 | 0.48 | 14.22 | 1
March | 28 | 7PM to 8PM | 73.9 | 63.5 | 57.9 | 74.7 | 29.42 | 0.0712 | 0.48 | 14.19 | 1
March | 28 | 8PM to 9PM | 72 | 62.9 | 57.9 | 74.7 | 28.93 | 0.0715 | 0.48 | 14.14 | 1
March | 28 | 9PM to 10PM | 70 | 62.2 | 57.9 | 74.7 | 28.45 | 0.0718 | 0.48 | 14.08 | 1
March | 28 | 10PM to 11PM | 69.1 | 60.8 | 55.9 | 69.4 | 27.41 | 0.0719 | 0.45 | 14.04 | 1
March | 28 | 11PM to 12AM | 66.9 | 60 | 55.9 | 69.4 | 26.88 | 0.0722 | 0.45 | 13.98 | 1
March | 29 | 12AM to 1AM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
March | 29 | 1AM to 2AM | 64 | 59.6 | 57 | 72.3 | 26.62 | 0.0726 | 0.47 | 13.92 | 1
March | 29 | 2AM to 3AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
March | 29 | 3AM to 4AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
March | 29 | 4AM to 5AM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
March | 29 | 5AM to 6AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
March | 29 | 6AM to 7AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
March | 29 | 7AM to 8AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
March | 29 | 8AM to 9AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
March | 29 | 9AM to 10AM | 68 | 62.2 | 59 | 77.7 | 28.43 | 0.072 | 0.5 | 14.04 | 1
March | 29 | 10AM to 11AM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
March | 29 | 11AM to 12PM | 70 | 62.2 | 57.9 | 74.7 | 28.45 | 0.0718 | 0.48 | 14.08 | 1
March | 29 | 12PM to 1PM | 73.9 | 63.5 | 57.9 | 74.7 | 29.42 | 0.0712 | 0.48 | 14.19 | 1
March | 29 | 1PM to 2PM | 75.9 | 63.7 | 57 | 72.3 | 29.52 | 0.071 | 0.47 | 14.23 | 1
March | 29 | 2PM to 3PM | 78.1 | 63.8 | 55.9 | 69.4 | 29.61 | 0.0707 | 0.45 | 14.28 | 1
March | 29 | 3PM to 4PM | 80.1 | 64.5 | 55.9 | 69.4 | 30.1 | 0.0705 | 0.45 | 14.33 | 1
March | 29 | 4PM to 5PM | 78.1 | 63.8 | 55.9 | 69.4 | 29.61 | 0.0707 | 0.45 | 14.28 | 1
March | 29 | 5PM to 6PM | 78.1 | 63.8 | 55.9 | 69.4 | 29.61 | 0.0707 | 0.45 | 14.28 | 1
March | 29 | 6PM to 7PM | 77 | 63.5 | 55.9 | 69.4 | 29.35 | 0.0709 | 0.45 | 14.25 | 1
March | 29 | 7PM to 8PM | 75 | 62.8 | 55.9 | 69.4 | 28.86 | 0.0711 | 0.45 | 14.2 | 1
March | 29 | 8PM to 9PM | 73 | 62.7 | 57 | 72.3 | 28.82 | 0.0714 | 0.47 | 14.16 | 1
March | 29 | 9PM to 10PM | 71.1 | 62.1 | 57 | 72.3 | 28.34 | 0.0716 | 0.47 | 14.1 | 1
March | 29 | 10PM to 11PM | 69.1 | 60.8 | 55.9 | 69.4 | 27.41 | 0.0719 | 0.45 | 14.04 | 1
March | 29 | 11PM to 12AM | 69.1 | 60.8 | 55.9 | 69.4 | 27.41 | 0.0719 | 0.45 | 14.04 | 1
March | 30 | 12AM to 1AM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
March | 30 | 1AM to 2AM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
March | 30 | 2AM to 3AM | 64 | 59 | 55.9 | 69.4 | 26.18 | 0.0726 | 0.45 | 13.91 | 1
March | 30 | 3AM to 4AM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
March | 30 | 4AM to 5AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
March | 30 | 5AM to 6AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
March | 30 | 6AM to 7AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
March | 30 | 7AM to 8AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
March | 30 | 8AM to 9AM | 66 | 61.5 | 59 | 77.7 | 27.95 | 0.0723 | 0.5 | 13.99 | 1
March | 30 | 9AM to 10AM | 68 | 62.2 | 59 | 77.7 | 28.43 | 0.072 | 0.5 | 14.04 | 1
March | 30 | 10AM to 11AM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
March | 30 | 11AM to 12PM | 77 | 64.5 | 57.9 | 74.7 | 30.17 | 0.0708 | 0.48 | 14.27 | 1
March | 30 | 12PM to 1PM | 80.1 | 64.5 | 55.9 | 69.4 | 30.1 | 0.0705 | 0.45 | 14.33 | 1
March | 30 | 1PM to 2PM | 82 | 64.1 | 54 | 64.5 | 29.81 | 0.0702 | 0.42 | 14.37 | 1
March | 30 | 2PM to 3PM | 82 | 62.8 | 51.1 | 58 | 28.78 | 0.0703 | 0.38 | 14.35 | 1
March | 30 | 3PM to 4PM | 82 | 63.2 | 52 | 59.9 | 29.09 | 0.0703 | 0.39 | 14.36 | 1
March | 30 | 4PM to 5PM | 80.1 | 64 | 55 | 67.2 | 29.74 | 0.0705 | 0.44 | 14.33 | 1
March | 30 | 5PM to 6PM | 79 | 63.7 | 55 | 67.2 | 29.48 | 0.0706 | 0.44 | 14.3 | 1
March | 30 | 6PM to 7PM | 78.1 | 63.4 | 55 | 67.2 | 29.26 | 0.0707 | 0.44 | 14.27 | 1
March | 30 | 7PM to 8PM | 75.9 | 62.6 | 55 | 67.2 | 28.73 | 0.071 | 0.44 | 14.22 | 1
March | 30 | 8PM to 9PM | 75 | 62.3 | 55 | 67.2 | 28.51 | 0.0711 | 0.44 | 14.19 | 1
March | 30 | 9PM to 10PM | 73 | 61.7 | 55 | 67.2 | 28.03 | 0.0714 | 0.44 | 14.14 | 1
March | 30 | 10PM to 11PM | 71.1 | 60.4 | 54 | 64.5 | 27.13 | 0.0717 | 0.42 | 14.08 | 1
March | 30 | 11PM to 12AM | 68 | 59.3 | 54 | 64.5 | 26.38 | 0.0721 | 0.42 | 14 | 1
March | 31 | 12AM to 1AM | 66 | 58.6 | 54 | 64.5 | 25.9 | 0.0724 | 0.42 | 13.95 | 1
March | 31 | 1AM to 2AM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
March | 31 | 2AM to 3AM | 64 | 59 | 55.9 | 69.4 | 26.18 | 0.0726 | 0.45 | 13.91 | 1
March | 31 | 3AM to 4AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
March | 31 | 4AM to 5AM | 62.1 | 58.9 | 57 | 72.3 | 26.13 | 0.0729 | 0.47 | 13.86 | 1
March | 31 | 5AM to 6AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
March | 31 | 6AM to 7AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
March | 31 | 7AM to 8AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
March | 31 | 8AM to 9AM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
March | 31 | 9AM to 10AM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
March | 31 | 10AM to 11AM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
March | 31 | 11AM to 12PM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
March | 31 | 12PM to 1PM | 57 | 54.7 | 53.1 | 62.4 | 23.37 | 0.0736 | 0.41 | 13.7 | 1
March | 31 | 1PM to 2PM | 55.9 | 54.2 | 53.1 | 62.4 | 23.11 | 0.0738 | 0.41 | 13.67 | 1
March | 31 | 2PM to 3PM | 59 | 54.8 | 52 | 59.9 | 23.47 | 0.0734 | 0.39 | 13.74 | 1
March | 31 | 3PM to 4PM | 63 | 57 | 53.1 | 62.4 | 24.82 | 0.0728 | 0.41 | 13.86 | 1
March | 31 | 4PM to 5PM | 64.9 | 55.6 | 48.9 | 53.4 | 23.91 | 0.0726 | 0.35 | 13.88 | 1
March | 31 | 5PM to 6PM | 64 | 50.4 | 37.9 | 34.9 | 20.81 | 0.0728 | 0.23 | 13.8 | 1
March | 31 | 6PM to 7PM | 62.1 | 49.2 | 37 | 33.7 | 20.14 | 0.0731 | 0.22 | 13.74 | 1
March | 31 | 7PM to 8PM | 57.9 | 47.4 | 37 | 33.7 | 19.14 | 0.0737 | 0.22 | 13.63 | 1
March | 31 | 8PM to 9PM | 55 | 46.4 | 37.9 | 34.9 | 18.63 | 0.0741 | 0.23 | 13.56 | 1
March | 31 | 9PM to 10PM | 54.7 | 46.3 | 38.1 | 35.2 | 18.58 | 0.0741 | 0.23 | 13.55 | 1
March | 31 | 10PM to 11PM | 54.1 | 46.2 | 38.3 | 35.4 | 18.49 | 0.0742 | 0.23 | 13.54 | 1
March | 31 | 11PM to 12AM | 53.8 | 46.1 | 38.5 | 35.7 | 18.44 | 0.0743 | 0.23 | 13.53 | 1
April | 1 | 12AM to 1AM | 53.2 | 45.8 | 38.5 | 35.7 | 18.31 | 0.0744 | 0.23 | 13.52 | 1
April | 1 | 1AM to 2AM | 52.9 | 45.7 | 38.7 | 35.9 | 18.26 | 0.0744 | 0.24 | 13.51 | 1
April | 1 | 2AM to 3AM | 52.3 | 45.5 | 38.8 | 36.2 | 18.17 | 0.0745 | 0.24 | 13.5 | 1
April | 1 | 3AM to 4AM | 52 | 45.5 | 39 | 36.4 | 18.12 | 0.0745 | 0.24 | 13.49 | 1
April | 1 | 4AM to 5AM | 54 | 46.4 | 39 | 36.4 | 18.6 | 0.0742 | 0.24 | 13.54 | 1
April | 1 | 5AM to 6AM | 55 | 47.3 | 39.9 | 37.8 | 19.07 | 0.0741 | 0.25 | 13.57 | 1
April | 1 | 6AM to 7AM | 55 | 46.9 | 39 | 36.4 | 18.87 | 0.0741 | 0.24 | 13.57 | 1
April | 1 | 7AM to 8AM | 51.1 | 48.3 | 46 | 47.9 | 19.67 | 0.0746 | 0.31 | 13.5 | 1
April | 1 | 8AM to 9AM | 55 | 47.7 | 41 | 39.4 | 19.32 | 0.0741 | 0.26 | 13.58 | 1
April | 1 | 9AM to 10AM | 55.9 | 46.8 | 37.9 | 34.9 | 18.85 | 0.074 | 0.23 | 13.59 | 1
April | 1 | 10AM to 11AM | 55.9 | 48.1 | 41 | 39.4 | 19.54 | 0.0739 | 0.26 | 13.6 | 1
April | 1 | 11AM to 12PM | 60.1 | 49.9 | 41 | 39.4 | 20.54 | 0.0734 | 0.26 | 13.71 | 1
April | 1 | 12PM to 1PM | 61 | 50.8 | 42.1 | 41.1 | 21.03 | 0.0732 | 0.27 | 13.74 | 1
April | 1 | 1PM to 2PM | 63 | 52 | 43 | 42.5 | 21.73 | 0.0729 | 0.28 | 13.8 | 1
April | 1 | 2PM to 3PM | 63 | 52.5 | 44.1 | 44.4 | 22.02 | 0.0729 | 0.29 | 13.8 | 1
April | 1 | 3PM to 4PM | 63 | 52.5 | 44.1 | 44.4 | 22.02 | 0.0729 | 0.29 | 13.8 | 1
April | 1 | 4PM to 5PM | 64 | 53.8 | 46 | 47.9 | 22.82 | 0.0727 | 0.31 | 13.84 | 1
April | 1 | 5PM to 6PM | 63 | 53.4 | 46 | 47.9 | 22.56 | 0.0729 | 0.31 | 13.81 | 1
April | 1 | 6PM to 7PM | 63 | 53.4 | 46 | 47.9 | 22.56 | 0.0729 | 0.31 | 13.81 | 1
April | 1 | 7PM to 8PM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
April | 1 | 8PM to 9PM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
April | 1 | 9PM to 10PM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
April | 1 | 10PM to 11PM | 57.9 | 52.3 | 48 | 51.6 | 21.92 | 0.0736 | 0.34 | 13.69 | 1
April | 1 | 11PM to 12AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
April | 2 | 12AM to 1AM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
April | 2 | 1AM to 2AM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
April | 2 | 2AM to 3AM | 59 | 53.8 | 50 | 55.6 | 22.81 | 0.0734 | 0.36 | 13.73 | 1
April | 2 | 3AM to 4AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
April | 2 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 62.4 | 23.11 | 0.0738 | 0.41 | 13.67 | 1
April | 2 | 5AM to 6AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
April | 2 | 6AM to 7AM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
April | 2 | 7AM to 8AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 2 | 8AM to 9AM | 60.1 | 59.4 | 59 | 77.7 | 26.49 | 0.0731 | 0.5 | 13.83 | 1
April | 2 | 9AM to 10AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
April | 2 | 10AM to 11AM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
April | 2 | 11AM to 12PM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
April | 2 | 12PM to 1PM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
April | 2 | 1PM to 2PM | 73 | 65.7 | 62.1 | 86.8 | 31.09 | 0.0713 | 0.56 | 14.2 | 1
April | 2 | 2PM to 3PM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
April | 2 | 3PM to 4PM | 75 | 66.3 | 62.1 | 86.8 | 31.58 | 0.071 | 0.56 | 14.26 | 1
April | 2 | 4PM to 5PM | 77 | 66.9 | 62.1 | 86.8 | 32.06 | 0.0708 | 0.56 | 14.31 | 1
April | 2 | 5PM to 6PM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
April | 2 | 6PM to 7PM | 73.9 | 65.3 | 61 | 83.5 | 30.79 | 0.0712 | 0.54 | 14.22 | 1
April | 2 | 7PM to 8PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
April | 2 | 8PM to 9PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
April | 2 | 9PM to 10PM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
April | 2 | 10PM to 11PM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
April | 2 | 11PM to 12AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
April | 3 | 12AM to 1AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
April | 3 | 1AM to 2AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
April | 3 | 2AM to 3AM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
April | 3 | 3AM to 4AM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
April | 3 | 4AM to 5AM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
April | 3 | 5AM to 6AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
April | 3 | 6AM to 7AM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
April | 3 | 7AM to 8AM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
April | 3 | 8AM to 9AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
April | 3 | 9AM to 10AM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
April | 3 | 10AM to 11AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
April | 3 | 11AM to 12PM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
April | 3 | 12PM to 1PM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
April | 3 | 1PM to 2PM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
April | 3 | 2PM to 3PM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
April | 3 | 3PM to 4PM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
April | 3 | 4PM to 5PM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
April | 3 | 5PM to 6PM | 62.1 | 58.9 | 57 | 72.3 | 26.13 | 0.0729 | 0.47 | 13.86 | 1
April | 3 | 6PM to 7PM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
April | 3 | 7PM to 8PM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
April | 3 | 8PM to 9PM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
April | 3 | 9PM to 10PM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
April | 3 | 10PM to 11PM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
April | 3 | 11PM to 12AM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
April | 4 | 12AM to 1AM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
April | 4 | 1AM to 2AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
April | 4 | 2AM to 3AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
April | 4 | 3AM to 4AM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
April | 4 | 4AM to 5AM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
April | 4 | 5AM to 6AM | 60.1 | 59.4 | 59 | 77.7 | 26.49 | 0.0731 | 0.5 | 13.83 | 1
April | 4 | 6AM to 7AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
April | 4 | 7AM to 8AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
April | 4 | 8AM to 9AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
April | 4 | 9AM to 10AM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
April | 4 | 10AM to 11AM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
April | 4 | 11AM to 12PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
April | 4 | 12PM to 1PM | 73.9 | 67.2 | 64 | 93.2 | 32.31 | 0.0711 | 0.6 | 14.25 | 1
April | 4 | 1PM to 2PM | 77 | 68.1 | 64 | 93.2 | 33.06 | 0.0707 | 0.6 | 14.33 | 1
April | 4 | 2PM to 3PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
April | 4 | 3PM to 4PM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
April | 4 | 4PM to 5PM | 78.1 | 66.1 | 60.1 | 80.8 | 31.39 | 0.0706 | 0.52 | 14.32 | 1
April | 4 | 5PM to 6PM | 77 | 65.8 | 60.1 | 80.8 | 31.12 | 0.0708 | 0.52 | 14.29 | 1
April | 4 | 6PM to 7PM | 75.9 | 64.8 | 59 | 77.7 | 30.37 | 0.071 | 0.5 | 14.25 | 1
April | 4 | 7PM to 8PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
April | 4 | 8PM to 9PM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
April | 4 | 9PM to 10PM | 62.1 | 60.8 | 60.1 | 80.8 | 27.46 | 0.0728 | 0.52 | 13.89 | 1
April | 4 | 10PM to 11PM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
April | 4 | 11PM to 12AM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
April | 5 | 12AM to 1AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
April | 5 | 1AM to 2AM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
April | 5 | 2AM to 3AM | 54 | 52.8 | 52 | 59.9 | 22.25 | 0.0741 | 0.39 | 13.61 | 1
April | 5 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 58 | 21.72 | 0.0742 | 0.38 | 13.58 | 1
April | 5 | 4AM to 5AM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
April | 5 | 5AM to 6AM | 50 | 45.9 | 42.1 | 41.1 | 18.36 | 0.0748 | 0.27 | 13.45 | 1
April | 5 | 6AM to 7AM | 48 | 43.6 | 39 | 36.4 | 17.16 | 0.0751 | 0.24 | 13.38 | 1
April | 5 | 7AM to 8AM | 48.9 | 43.5 | 37.9 | 34.9 | 17.15 | 0.075 | 0.23 | 13.4 | 1
April | 5 | 8AM to 9AM | 50 | 44.1 | 37.9 | 34.9 | 17.41 | 0.0748 | 0.23 | 13.43 | 1
April | 5 | 9AM to 10AM | 51.1 | 44.6 | 37.9 | 34.9 | 17.67 | 0.0747 | 0.23 | 13.46 | 1
April | 5 | 10AM to 11AM | 46 | 42.1 | 37.9 | 34.9 | 16.45 | 0.0754 | 0.23 | 13.33 | 1
April | 5 | 11AM to 12PM | 50 | 42.9 | 35.1 | 31.1 | 16.82 | 0.0749 | 0.2 | 13.42 | 1
April | 5 | 12PM to 1PM | 50 | 40.3 | 28 | 22.9 | 15.55 | 0.0749 | 0.15 | 13.39 | 1
April | 5 | 1PM to 2PM | 51.1 | 40.8 | 28 | 22.9 | 15.81 | 0.0748 | 0.15 | 13.42 | 1
April | 5 | 2PM to 3PM | 50 | 39.9 | 27 | 21.8 | 15.37 | 0.0749 | 0.14 | 13.39 | 1
April | 5 | 3PM to 4PM | 50 | 39.6 | 26.1 | 20.9 | 15.23 | 0.0749 | 0.14 | 13.39 | 1
April | 5 | 4PM to 5PM | 50 | 39.6 | 26.1 | 20.9 | 15.23 | 0.0749 | 0.14 | 13.39 | 1
April | 5 | 5PM to 6PM | 48 | 38.2 | 25 | 19.8 | 14.6 | 0.0752 | 0.13 | 13.33 | 1
April | 5 | 6PM to 7PM | 46 | 36.5 | 23 | 18.1 | 13.84 | 0.0755 | 0.12 | 13.27 | 1
April | 5 | 7PM to 8PM | 42.1 | 34.7 | 24.1 | 19 | 13.03 | 0.0761 | 0.12 | 13.17 | 1
April | 5 | 8PM to 9PM | 39 | 33.6 | 26.1 | 20.9 | 12.58 | 0.0766 | 0.14 | 13.1 | 1
April | 5 | 9PM to 10PM | 37.9 | 33.3 | 27 | 21.8 | 12.46 | 0.0767 | 0.14 | 13.07 | 1
April | 5 | 10PM to 11PM | 35.1 | 31.4 | 27 | 21.8 | 11.77 | 0.0772 | 0.14 | 13 | 1
April | 5 | 11PM to 12AM | 35.1 | 31.4 | 27 | 21.8 | 11.77 | 0.0772 | 0.14 | 13 | 1
April | 6 | 12AM to 1AM | 36 | 31.9 | 27 | 21.8 | 11.98 | 0.077 | 0.14 | 13.02 | 1
April | 6 | 1AM to 2AM | 35.1 | 31.4 | 27 | 21.8 | 11.77 | 0.0772 | 0.14 | 13 | 1
April | 6 | 2AM to 3AM | 33.1 | 30.4 | 27 | 21.8 | 11.29 | 0.0775 | 0.14 | 12.95 | 1
April | 6 | 3AM to 4AM | 34 | 30.8 | 27 | 21.8 | 11.51 | 0.0773 | 0.14 | 12.97 | 1
April | 6 | 4AM to 5AM | 32 | 29.8 | 27 | 21.8 | 11.03 | 0.0777 | 0.14 | 12.92 | 1
April | 6 | 5AM to 6AM | 34 | 30.8 | 27 | 21.8 | 11.51 | 0.0773 | 0.14 | 12.97 | 1
April | 6 | 6AM to 7AM | 35.1 | 31.4 | 27 | 21.8 | 11.77 | 0.0772 | 0.14 | 13 | 1
April | 6 | 7AM to 8AM | 41 | 35.8 | 28.9 | 23.9 | 13.53 | 0.0762 | 0.16 | 13.16 | 1
April | 6 | 8AM to 9AM | 45 | 37.9 | 28.9 | 23.9 | 14.48 | 0.0757 | 0.16 | 13.26 | 1
April | 6 | 9AM to 10AM | 50 | 39 | 24.1 | 19 | 14.95 | 0.0749 | 0.12 | 13.38 | 1
April | 6 | 10AM to 11AM | 53.1 | 40.6 | 24.1 | 19 | 15.68 | 0.0745 | 0.12 | 13.46 | 1
April | 6 | 11AM to 12PM | 55.9 | 42.6 | 26.1 | 20.9 | 16.67 | 0.0741 | 0.14 | 13.54 | 1
April | 6 | 12PM to 1PM | 57.9 | 44.2 | 28 | 22.9 | 17.46 | 0.0738 | 0.15 | 13.6 | 1
April | 6 | 1PM to 2PM | 59 | 44.7 | 28 | 22.9 | 17.72 | 0.0736 | 0.15 | 13.63 | 1
April | 6 | 2PM to 3PM | 60.1 | 45.2 | 28 | 22.9 | 17.98 | 0.0735 | 0.15 | 13.66 | 1
April | 6 | 3PM to 4PM | 60.1 | 45.2 | 28 | 22.9 | 17.98 | 0.0735 | 0.15 | 13.66 | 1
April | 6 | 4PM to 5PM | 60.1 | 45.5 | 28.9 | 23.9 | 18.13 | 0.0734 | 0.16 | 13.66 | 1
April | 6 | 5PM to 6PM | 59 | 44.7 | 28 | 22.9 | 17.72 | 0.0736 | 0.15 | 13.63 | 1
April | 6 | 6PM to 7PM | 55 | 43.1 | 28.9 | 23.9 | 16.92 | 0.0742 | 0.16 | 13.53 | 1
April | 6 | 7PM to 8PM | 53.1 | 42.1 | 28.9 | 23.9 | 16.44 | 0.0745 | 0.16 | 13.48 | 1
April | 6 | 8PM to 9PM | 48.9 | 40 | 28.9 | 23.9 | 15.44 | 0.0751 | 0.16 | 13.37 | 1
April | 6 | 9PM to 10PM | 44.1 | 37.5 | 28.9 | 23.9 | 14.27 | 0.0758 | 0.16 | 13.24 | 1
April | 6 | 10PM to 11PM | 43 | 37.3 | 30 | 25.1 | 14.19 | 0.0759 | 0.16 | 13.22 | 1
April | 6 | 11PM to 12AM | 41 | 36.2 | 30 | 25.1 | 13.72 | 0.0762 | 0.16 | 13.16 | 1
April | 7 | 12AM to 1AM | 39 | 35.1 | 30 | 25.1 | 13.24 | 0.0765 | 0.16 | 13.11 | 1
April | 7 | 1AM to 2AM | 39 | 35.1 | 30 | 25.1 | 13.24 | 0.0765 | 0.16 | 13.11 | 1
April | 7 | 2AM to 3AM | 39.9 | 36 | 30.9 | 26.2 | 13.62 | 0.0764 | 0.17 | 13.14 | 1
April | 7 | 3AM to 4AM | 39 | 35.5 | 30.9 | 26.2 | 13.4 | 0.0765 | 0.17 | 13.11 | 1
April | 7 | 4AM to 5AM | 37.9 | 34.5 | 30 | 25.1 | 12.98 | 0.0767 | 0.16 | 13.08 | 1
April | 7 | 5AM to 6AM | 37 | 34.9 | 32 | 27.5 | 13.13 | 0.0768 | 0.18 | 13.07 | 1
April | 7 | 6AM to 7AM | 37 | 34.9 | 32 | 27.5 | 13.13 | 0.0768 | 0.18 | 13.07 | 1
April | 7 | 7AM to 8AM | 45 | 40.4 | 35.1 | 31.1 | 15.6 | 0.0756 | 0.2 | 13.29 | 1
April | 7 | 8AM to 9AM | 53.1 | 44 | 34 | 29.8 | 17.36 | 0.0744 | 0.2 | 13.49 | 1
April | 7 | 9AM to 10AM | 60.1 | 48 | 36 | 32.3 | 19.44 | 0.0734 | 0.21 | 13.69 | 1
April | 7 | 10AM to 11AM | 64 | 49.7 | 36 | 32.3 | 20.4 | 0.0728 | 0.21 | 13.79 | 1
April | 7 | 11AM to 12PM | 66.9 | 52.4 | 39.9 | 37.8 | 21.95 | 0.0724 | 0.25 | 13.88 | 1
April | 7 | 12PM to 1PM | 71.1 | 54.5 | 41 | 39.4 | 23.21 | 0.0718 | 0.26 | 14 | 1
April | 7 | 1PM to 2PM | 72 | 56.1 | 44.1 | 44.4 | 24.2 | 0.0717 | 0.29 | 14.04 | 1
April | 7 | 2PM to 3PM | 75.9 | 56.8 | 42.1 | 41.1 | 24.65 | 0.0712 | 0.27 | 14.13 | 1
April | 7 | 3PM to 4PM | 75.9 | 57.6 | 44.1 | 44.4 | 25.16 | 0.0712 | 0.29 | 14.14 | 1
April | 7 | 4PM to 5PM | 75.9 | 56.4 | 41 | 39.4 | 24.39 | 0.0712 | 0.26 | 14.13 | 1
April | 7 | 5PM to 6PM | 75 | 56.8 | 43 | 42.5 | 24.66 | 0.0713 | 0.28 | 14.11 | 1
April | 7 | 6PM to 7PM | 70 | 54.9 | 43 | 42.5 | 23.44 | 0.072 | 0.28 | 13.98 | 1
April | 7 | 7PM to 8PM | 62.1 | 52.5 | 45 | 45.9 | 22.04 | 0.073 | 0.3 | 13.78 | 1
April | 7 | 8PM to 9PM | 61 | 51.7 | 44.1 | 44.4 | 21.54 | 0.0732 | 0.29 | 13.75 | 1
April | 7 | 9PM to 10PM | 59 | 51.8 | 46 | 47.9 | 21.6 | 0.0735 | 0.31 | 13.71 | 1
April | 7 | 10PM to 11PM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
April | 7 | 11PM to 12AM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
April | 8 | 12AM to 1AM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
April | 8 | 1AM to 2AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
April | 8 | 2AM to 3AM | 55.9 | 49.9 | 45 | 45.9 | 20.55 | 0.0739 | 0.3 | 13.62 | 1
April | 8 | 3AM to 4AM | 55 | 49.5 | 45 | 45.9 | 20.34 | 0.074 | 0.3 | 13.6 | 1
April | 8 | 4AM to 5AM | 53.1 | 48.7 | 45 | 45.9 | 19.85 | 0.0743 | 0.3 | 13.54 | 1
April | 8 | 5AM to 6AM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
April | 8 | 6AM to 7AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
April | 8 | 7AM to 8AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
April | 8 | 8AM to 9AM | 63 | 53.8 | 46.9 | 49.6 | 22.82 | 0.0729 | 0.32 | 13.82 | 1
April | 8 | 9AM to 10AM | 69.1 | 57.7 | 50 | 55.6 | 25.26 | 0.072 | 0.36 | 14 | 1
April | 8 | 10AM to 11AM | 72 | 57.8 | 48 | 51.6 | 25.34 | 0.0716 | 0.34 | 14.06 | 1
April | 8 | 11AM to 12PM | 75 | 58.1 | 46 | 47.9 | 25.49 | 0.0713 | 0.31 | 14.13 | 1
April | 8 | 12PM to 1PM | 75.9 | 57.2 | 43 | 42.5 | 24.88 | 0.0712 | 0.28 | 14.14 | 1
April | 8 | 1PM to 2PM | 78.1 | 55.5 | 36 | 32.3 | 23.8 | 0.0709 | 0.21 | 14.16 | 1
April | 8 | 2PM to 3PM | 78.1 | 55.8 | 37 | 33.7 | 24.02 | 0.0709 | 0.22 | 14.17 | 1
April | 8 | 3PM to 4PM | 78.1 | 55.5 | 36 | 32.3 | 23.8 | 0.0709 | 0.21 | 14.16 | 1
April | 8 | 4PM to 5PM | 78.1 | 56.1 | 37.9 | 34.9 | 24.21 | 0.0709 | 0.23 | 14.17 | 1
April | 8 | 5PM to 6PM | 75.9 | 54.6 | 36 | 32.3 | 23.27 | 0.0712 | 0.21 | 14.1 | 1
April | 8 | 6PM to 7PM | 71.1 | 52.7 | 36 | 32.3 | 22.1 | 0.0719 | 0.21 | 13.98 | 1
April | 8 | 7PM to 8PM | 69.1 | 50.2 | 30.9 | 26.2 | 20.67 | 0.0722 | 0.17 | 13.91 | 1
April | 8 | 8PM to 9PM | 64 | 47.7 | 30 | 25.1 | 19.28 | 0.0729 | 0.16 | 13.77 | 1
April | 8 | 9PM to 10PM | 62.1 | 46.8 | 30 | 25.1 | 18.8 | 0.0732 | 0.16 | 13.72 | 1
April | 8 | 10PM to 11PM | 57.9 | 45.2 | 30.9 | 26.2 | 17.97 | 0.0737 | 0.17 | 13.61 | 1
April | 8 | 11PM to 12AM | 55.9 | 43.9 | 30 | 25.1 | 17.33 | 0.074 | 0.16 | 13.56 | 1
April | 9 | 12AM to 1AM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
April | 9 | 1AM to 2AM | 52 | 42 | 30 | 25.1 | 16.37 | 0.0746 | 0.16 | 13.45 | 1
April | 9 | 2AM to 3AM | 52 | 41.6 | 28.9 | 23.9 | 16.18 | 0.0746 | 0.16 | 13.45 | 1
April | 9 | 3AM to 4AM | 48 | 40 | 30 | 25.1 | 15.41 | 0.0752 | 0.16 | 13.35 | 1
April | 9 | 4AM to 5AM | 46 | 39.3 | 30.9 | 26.2 | 15.1 | 0.0755 | 0.17 | 13.3 | 1
April | 9 | 5AM to 6AM | 44.1 | 38.2 | 30.9 | 26.2 | 14.62 | 0.0758 | 0.17 | 13.25 | 1
April | 9 | 6AM to 7AM | 48 | 40 | 30 | 25.1 | 15.41 | 0.0752 | 0.16 | 13.35 | 1
April | 9 | 7AM to 8AM | 52 | 42.3 | 30.9 | 26.2 | 16.53 | 0.0746 | 0.17 | 13.46 | 1
April | 9 | 8AM to 9AM | 55.9 | 43.9 | 30 | 25.1 | 17.33 | 0.074 | 0.16 | 13.56 | 1
April | 9 | 9AM to 10AM | 60.1 | 45.2 | 28 | 22.9 | 17.98 | 0.0735 | 0.15 | 13.66 | 1
April | 9 | 10AM to 11AM | 62.1 | 46.4 | 28.9 | 23.9 | 18.61 | 0.0732 | 0.16 | 13.71 | 1
April | 9 | 11AM to 12PM | 64.9 | 47.5 | 28 | 22.9 | 19.16 | 0.0728 | 0.15 | 13.79 | 1
April | 9 | 12PM to 1PM | 68 | 49.5 | 30 | 25.1 | 20.24 | 0.0723 | 0.16 | 13.87 | 1
April | 9 | 1PM to 2PM | 69.1 | 51.2 | 34 | 29.8 | 21.23 | 0.0722 | 0.2 | 13.92 | 1
April | 9 | 2PM to 3PM | 71.1 | 52.4 | 35.1 | 31.1 | 21.92 | 0.0719 | 0.2 | 13.97 | 1
April | 9 | 3PM to 4PM | 71.1 | 50.8 | 30 | 25.1 | 20.98 | 0.0719 | 0.16 | 13.95 | 1
April | 9 | 4PM to 5PM | 71.1 | 51.1 | 30.9 | 26.2 | 21.15 | 0.0719 | 0.17 | 13.96 | 1
April | 9 | 5PM to 6PM | 70 | 51.9 | 35.1 | 31.1 | 21.66 | 0.072 | 0.2 | 13.94 | 1
April | 9 | 6PM to 7PM | 63 | 50 | 37.9 | 34.9 | 20.55 | 0.073 | 0.23 | 13.77 | 1
April | 9 | 7PM to 8PM | 57 | 47 | 37 | 33.7 | 18.92 | 0.0738 | 0.22 | 13.61 | 1
April | 9 | 8PM to 9PM | 55.9 | 46.5 | 37 | 33.7 | 18.66 | 0.074 | 0.22 | 13.58 | 1
April | 9 | 9PM to 10PM | 53.1 | 46 | 39 | 36.4 | 18.39 | 0.0744 | 0.24 | 13.52 | 1
April | 9 | 10PM to 11PM | 54 | 45.6 | 37 | 33.7 | 18.18 | 0.0743 | 0.22 | 13.53 | 1
April | 9 | 11PM to 12AM | 53.1 | 44 | 34 | 29.8 | 17.36 | 0.0744 | 0.2 | 13.49 | 1
April | 10 | 12AM to 1AM | 53.1 | 44 | 34 | 29.8 | 17.36 | 0.0744 | 0.2 | 13.49 | 1
April | 10 | 1AM to 2AM | 50 | 42.9 | 35.1 | 31.1 | 16.82 | 0.0749 | 0.2 | 13.42 | 1
April | 10 | 2AM to 3AM | 51.1 | 43.4 | 35.1 | 31.1 | 17.08 | 0.0747 | 0.2 | 13.45 | 1
April | 10 | 3AM to 4AM | 48 | 42.7 | 37 | 33.7 | 16.74 | 0.0751 | 0.22 | 13.37 | 1
April | 10 | 4AM to 5AM | 48 | 43.1 | 37.9 | 34.9 | 16.93 | 0.0751 | 0.23 | 13.38 | 1
April | 10 | 5AM to 6AM | 46.9 | 41.7 | 36 | 32.3 | 16.26 | 0.0753 | 0.21 | 13.34 | 1
April | 10 | 6AM to 7AM | 48 | 41.9 | 35.1 | 31.1 | 16.34 | 0.0751 | 0.2 | 13.37 | 1
April | 10 | 7AM to 8AM | 54 | 47.2 | 41 | 39.4 | 19.06 | 0.0742 | 0.26 | 13.55 | 1
April | 10 | 8AM to 9AM | 60.1 | 49.1 | 39 | 36.4 | 20.09 | 0.0734 | 0.24 | 13.7 | 1
April | 10 | 9AM to 10AM | 64.9 | 50.8 | 37.9 | 34.9 | 21.03 | 0.0727 | 0.23 | 13.82 | 1
April | 10 | 10AM to 11AM | 68 | 52.1 | 37.9 | 34.9 | 21.77 | 0.0723 | 0.23 | 13.9 | 1
April | 10 | 11AM to 12PM | 71.1 | 53.8 | 39 | 36.4 | 22.75 | 0.0719 | 0.24 | 13.99 | 1
April | 10 | 12PM to 1PM | 73.9 | 54.9 | 39 | 36.4 | 23.44 | 0.0715 | 0.24 | 14.07 | 1
April | 10 | 1PM to 2PM | 77 | 56.4 | 39.9 | 37.8 | 24.39 | 0.071 | 0.25 | 14.15 | 1
April | 10 | 2PM to 3PM | 78.1 | 56.8 | 39.9 | 37.8 | 24.65 | 0.0709 | 0.25 | 14.18 | 1
April | 10 | 3PM to 4PM | 78.1 | 57.2 | 41 | 39.4 | 24.91 | 0.0709 | 0.26 | 14.18 | 1
April | 10 | 4PM to 5PM | 77 | 59.6 | 48 | 51.6 | 26.56 | 0.071 | 0.34 | 14.2 | 1
April | 10 | 5PM to 6PM | 73.9 | 58.1 | 46.9 | 49.6 | 25.49 | 0.0714 | 0.32 | 14.11 | 1
April | 10 | 6PM to 7PM | 68 | 55.8 | 46.9 | 49.6 | 24.05 | 0.0722 | 0.32 | 13.95 | 1
April | 10 | 7PM to 8PM | 66 | 54.6 | 46 | 47.9 | 23.31 | 0.0725 | 0.31 | 13.89 | 1
April | 10 | 8PM to 9PM | 64.9 | 54.2 | 46 | 47.9 | 23.04 | 0.0726 | 0.31 | 13.86 | 1
April | 10 | 9PM to 10PM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
April | 10 | 10PM to 11PM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
April | 10 | 11PM to 12AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
April | 11 | 12AM to 1AM | 54 | 49.6 | 46 | 47.9 | 20.37 | 0.0742 | 0.31 | 13.57 | 1
April | 11 | 1AM to 2AM | 54 | 49.6 | 46 | 47.9 | 20.37 | 0.0742 | 0.31 | 13.57 | 1
April | 11 | 2AM to 3AM | 54 | 49.1 | 45 | 45.9 | 20.07 | 0.0742 | 0.3 | 13.57 | 1
April | 11 | 3AM to 4AM | 54 | 49.1 | 45 | 45.9 | 20.07 | 0.0742 | 0.3 | 13.57 | 1
April | 11 | 4AM to 5AM | 52 | 47.2 | 43 | 42.5 | 19.07 | 0.0745 | 0.28 | 13.51 | 1
April | 11 | 5AM to 6AM | 52 | 47.8 | 44.1 | 44.4 | 19.35 | 0.0745 | 0.29 | 13.51 | 1
April | 11 | 6AM to 7AM | 53.1 | 48.7 | 45 | 45.9 | 19.85 | 0.0743 | 0.3 | 13.54 | 1
April | 11 | 7AM to 8AM | 63 | 53.8 | 46.9 | 49.6 | 22.82 | 0.0729 | 0.32 | 13.82 | 1
April | 11 | 8AM to 9AM | 66.9 | 55.4 | 46.9 | 49.6 | 23.79 | 0.0723 | 0.32 | 13.92 | 1
April | 11 | 9AM to 10AM | 71.1 | 56.6 | 46 | 47.9 | 24.53 | 0.0718 | 0.31 | 14.03 | 1
April | 11 | 10AM to 11AM | 73.9 | 58.1 | 46.9 | 49.6 | 25.49 | 0.0714 | 0.32 | 14.11 | 1
April | 11 | 11AM to 12PM | 77 | 60 | 48.9 | 53.4 | 26.84 | 0.071 | 0.35 | 14.2 | 1
April | 11 | 12PM to 1PM | 80.1 | 60.7 | 48 | 51.6 | 27.31 | 0.0706 | 0.34 | 14.28 | 1
April | 11 | 1PM to 2PM | 80.1 | 59.5 | 45 | 45.9 | 26.41 | 0.0706 | 0.3 | 14.26 | 1
April | 11 | 2PM to 3PM | 82 | 61.4 | 48 | 51.6 | 27.79 | 0.0703 | 0.34 | 14.33 | 1
April | 11 | 3PM to 4PM | 81 | 60.2 | 46 | 47.9 | 26.94 | 0.0705 | 0.31 | 14.29 | 1
April | 11 | 4PM to 5PM | 81 | 61 | 48 | 51.6 | 27.53 | 0.0704 | 0.34 | 14.3 | 1
April | 11 | 5PM to 6PM | 77 | 59.2 | 46.9 | 49.6 | 26.24 | 0.071 | 0.32 | 14.19 | 1
April | 11 | 6PM to 7PM | 71.1 | 57.5 | 48 | 51.6 | 25.12 | 0.0718 | 0.34 | 14.04 | 1
April | 11 | 7PM to 8PM | 70 | 56.6 | 46.9 | 49.6 | 24.53 | 0.0719 | 0.32 | 14 | 1
April | 11 | 8PM to 9PM | 70 | 57.1 | 48 | 51.6 | 24.85 | 0.0719 | 0.34 | 14.01 | 1
April | 11 | 9PM to 10PM | 63 | 54.8 | 48.9 | 53.4 | 23.43 | 0.0729 | 0.35 | 13.83 | 1
April | 11 | 10PM to 11PM | 59 | 53.8 | 50 | 55.6 | 22.81 | 0.0734 | 0.36 | 13.73 | 1
April | 11 | 11PM to 12AM | 59 | 53.8 | 50 | 55.6 | 22.81 | 0.0734 | 0.36 | 13.73 | 1
April | 12 | 12AM to 1AM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
April | 12 | 1AM to 2AM | 57 | 51.9 | 48 | 51.6 | 21.7 | 0.0737 | 0.34 | 13.67 | 1
April | 12 | 2AM to 3AM | 57 | 51.9 | 48 | 51.6 | 21.7 | 0.0737 | 0.34 | 13.67 | 1
April | 12 | 3AM to 4AM | 57.9 | 51.7 | 46.9 | 49.6 | 21.6 | 0.0736 | 0.32 | 13.68 | 1
April | 12 | 4AM to 5AM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
April | 12 | 5AM to 6AM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
April | 12 | 6AM to 7AM | 61 | 52.6 | 46 | 47.9 | 22.08 | 0.0732 | 0.31 | 13.76 | 1
April | 12 | 7AM to 8AM | 64.9 | 55.6 | 48.9 | 53.4 | 23.91 | 0.0726 | 0.35 | 13.88 | 1
April | 12 | 8AM to 9AM | 66 | 56.5 | 50 | 55.6 | 24.52 | 0.0724 | 0.36 | 13.92 | 1
April | 12 | 9AM to 10AM | 72 | 59.7 | 52 | 59.9 | 26.63 | 0.0716 | 0.39 | 14.09 | 1
April | 12 | 10AM to 11AM | 77 | 61.5 | 52 | 59.9 | 27.86 | 0.0709 | 0.39 | 14.22 | 1
April | 12 | 11AM to 12PM | 79 | 62.2 | 52 | 59.9 | 28.35 | 0.0707 | 0.39 | 14.27 | 1
April | 12 | 12PM to 1PM | 82 | 61.4 | 48 | 51.6 | 27.79 | 0.0703 | 0.34 | 14.33 | 1
April | 12 | 1PM to 2PM | 84 | 62.5 | 48.9 | 53.4 | 28.55 | 0.07 | 0.35 | 14.39 | 1
April | 12 | 2PM to 3PM | 82.9 | 62.1 | 48.9 | 53.4 | 28.29 | 0.0702 | 0.35 | 14.36 | 1
April | 12 | 3PM to 4PM | 82 | 60.6 | 46 | 47.9 | 27.2 | 0.0703 | 0.31 | 14.32 | 1
April | 12 | 4PM to 5PM | 81 | 60.6 | 46.9 | 49.6 | 27.2 | 0.0705 | 0.32 | 14.29 | 1
April | 12 | 5PM to 6PM | 75 | 59.8 | 50 | 55.6 | 26.71 | 0.0712 | 0.36 | 14.16 | 1
April | 12 | 6PM to 7PM | 73 | 59.6 | 51.1 | 58 | 26.59 | 0.0715 | 0.38 | 14.11 | 1
April | 12 | 7PM to 8PM | 70 | 57.1 | 48 | 51.6 | 24.85 | 0.0719 | 0.34 | 14.01 | 1
April | 12 | 8PM to 9PM | 66.9 | 56.3 | 48.9 | 53.4 | 24.39 | 0.0723 | 0.35 | 13.93 | 1
April | 12 | 9PM to 10PM | 64 | 55.8 | 50 | 55.6 | 24.03 | 0.0727 | 0.36 | 13.87 | 1
April | 12 | 10PM to 11PM | 64.9 | 55.1 | 48 | 51.6 | 23.63 | 0.0726 | 0.34 | 13.88 | 1
April | 12 | 11PM to 12AM | 63 | 54.3 | 48 | 51.6 | 23.15 | 0.0729 | 0.34 | 13.82 | 1
April | 13 | 12AM to 1AM | 62.1 | 54 | 48 | 51.6 | 22.93 | 0.073 | 0.34 | 13.8 | 1
April | 13 | 1AM to 2AM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
April | 13 | 2AM to 3AM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
April | 13 | 3AM to 4AM | 57.9 | 52.3 | 48 | 51.6 | 21.92 | 0.0736 | 0.34 | 13.69 | 1
April | 13 | 4AM to 5AM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
April | 13 | 5AM to 6AM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
April | 13 | 6AM to 7AM | 54 | 51.1 | 48.9 | 53.4 | 21.23 | 0.0741 | 0.35 | 13.59 | 1
April | 13 | 7AM to 8AM | 60.1 | 55.9 | 53.1 | 62.4 | 24.12 | 0.0732 | 0.41 | 13.78 | 1
April | 13 | 8AM to 9AM | 64.9 | 58.2 | 54 | 64.5 | 25.64 | 0.0725 | 0.42 | 13.92 | 1
April | 13 | 9AM to 10AM | 70 | 60.6 | 55 | 67.2 | 27.28 | 0.0718 | 0.44 | 14.06 | 1
April | 13 | 10AM to 11AM | 75.9 | 62.6 | 55 | 67.2 | 28.73 | 0.071 | 0.44 | 14.22 | 1
April | 13 | 11AM to 12PM | 79 | 62.7 | 53.1 | 62.4 | 28.73 | 0.0706 | 0.41 | 14.28 | 1
April | 13 | 12PM to 1PM | 80.1 | 61.1 | 48.9 | 53.4 | 27.59 | 0.0706 | 0.35 | 14.28 | 1
April | 13 | 1PM to 2PM | 80.1 | 60.3 | 46.9 | 49.6 | 26.98 | 0.0706 | 0.32 | 14.27 | 1
April | 13 | 2PM to 3PM | 81 | 59.8 | 45 | 45.9 | 26.63 | 0.0705 | 0.3 | 14.28 | 1
April | 13 | 3PM to 4PM | 80.1 | 58.7 | 43 | 42.5 | 25.88 | 0.0706 | 0.28 | 14.25 | 1
April | 13 | 4PM to 5PM | 79 | 59.5 | 46 | 47.9 | 26.46 | 0.0707 | 0.31 | 14.24 | 1
April | 13 | 5PM to 6PM | 75 | 59.8 | 50 | 55.6 | 26.71 | 0.0712 | 0.36 | 14.16 | 1
April | 13 | 6PM to 7PM | 70 | 57.5 | 48.9 | 53.4 | 25.13 | 0.0719 | 0.35 | 14.02 | 1
April | 13 | 7PM to 8PM | 68 | 56.7 | 48.9 | 53.4 | 24.65 | 0.0722 | 0.35 | 13.96 | 1
April | 13 | 8PM to 9PM | 66 | 56 | 48.9 | 53.4 | 24.17 | 0.0724 | 0.35 | 13.91 | 1
April | 13 | 9PM to 10PM | 64 | 55.2 | 48.9 | 53.4 | 23.69 | 0.0727 | 0.35 | 13.86 | 1
April | 13 | 10PM to 11PM | 64.9 | 55.1 | 48 | 51.6 | 23.63 | 0.0726 | 0.34 | 13.88 | 1
April | 13 | 11PM to 12AM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
April | 14 | 12AM to 1AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
April | 14 | 1AM to 2AM | 57.9 | 51.7 | 46.9 | 49.6 | 21.6 | 0.0736 | 0.32 | 13.68 | 1
April | 14 | 2AM to 3AM | 57 | 50.9 | 46 | 47.9 | 21.12 | 0.0737 | 0.31 | 13.66 | 1
April | 14 | 3AM to 4AM | 57 | 50.9 | 46 | 47.9 | 21.12 | 0.0737 | 0.31 | 13.66 | 1
April | 14 | 4AM to 5AM | 55 | 49.5 | 45 | 45.9 | 20.34 | 0.074 | 0.3 | 13.6 | 1
April | 14 | 5AM to 6AM | 53.1 | 48.2 | 44.1 | 44.4 | 19.61 | 0.0743 | 0.29 | 13.54 | 1
April | 14 | 6AM to 7AM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
April | 14 | 7AM to 8AM | 61 | 55.6 | 52 | 59.9 | 23.96 | 0.0731 | 0.39 | 13.8 | 1
April | 14 | 8AM to 9AM | 66.9 | 57.4 | 51.1 | 58 | 25.1 | 0.0723 | 0.38 | 13.95 | 1
April | 14 | 9AM to 10AM | 70 | 58.5 | 51.1 | 58 | 25.84 | 0.0719 | 0.38 | 14.03 | 1
April | 14 | 10AM to 11AM | 75 | 60.4 | 51.1 | 58 | 27.07 | 0.0712 | 0.38 | 14.16 | 1
April | 14 | 11AM to 12PM | 79 | 61.2 | 50 | 55.6 | 27.67 | 0.0707 | 0.36 | 14.26 | 1
April | 14 | 12PM to 1PM | 80.1 | 59.5 | 45 | 45.9 | 26.41 | 0.0706 | 0.3 | 14.26 | 1
April | 14 | 1PM to 2PM | 81 | 59.8 | 45 | 45.9 | 26.63 | 0.0705 | 0.3 | 14.28 | 1
April | 14 | 2PM to 3PM | 81 | 60.6 | 46.9 | 49.6 | 27.2 | 0.0705 | 0.32 | 14.29 | 1
April | 14 | 3PM to 4PM | 81 | 60.2 | 46 | 47.9 | 26.94 | 0.0705 | 0.31 | 14.29 | 1
April | 14 | 4PM to 5PM | 80.1 | 59.9 | 46 | 47.9 | 26.72 | 0.0706 | 0.31 | 14.26 | 1
April | 14 | 5PM to 6PM | 77 | 60 | 48.9 | 53.4 | 26.84 | 0.071 | 0.35 | 14.2 | 1
April | 14 | 6PM to 7PM | 71.1 | 57.5 | 48 | 51.6 | 25.12 | 0.0718 | 0.34 | 14.04 | 1
April | 14 | 7PM to 8PM | 70 | 56.6 | 46.9 | 49.6 | 24.53 | 0.0719 | 0.32 | 14 | 1
April | 14 | 8PM to 9PM | 68 | 56.3 | 48 | 51.6 | 24.37 | 0.0722 | 0.34 | 13.96 | 1
April | 14 | 9PM to 10PM | 63 | 54.3 | 48 | 51.6 | 23.15 | 0.0729 | 0.34 | 13.82 | 1
April | 14 | 10PM to 11PM | 62.1 | 53.5 | 46.9 | 49.6 | 22.6 | 0.073 | 0.32 | 13.79 | 1
April | 14 | 11PM to 12AM | 59 | 50.8 | 44.1 | 44.4 | 21.05 | 0.0735 | 0.29 | 13.7 | 1
April | 15 | 12AM to 1AM | 57.9 | 50.4 | 44.1 | 44.4 | 20.79 | 0.0736 | 0.29 | 13.67 | 1
April | 15 | 1AM to 2AM | 55 | 48.2 | 42.1 | 41.1 | 19.58 | 0.0741 | 0.27 | 13.58 | 1
April | 15 | 2AM to 3AM | 57.9 | 49 | 41 | 39.4 | 20.02 | 0.0737 | 0.26 | 13.65 | 1
April | 15 | 3AM to 4AM | 54 | 46.8 | 39.9 | 37.8 | 18.81 | 0.0742 | 0.25 | 13.54 | 1
April | 15 | 4AM to 5AM | 53.1 | 47.3 | 42.1 | 41.1 | 19.1 | 0.0743 | 0.27 | 13.53 | 1
April | 15 | 5AM to 6AM | 53.1 | 47.3 | 42.1 | 41.1 | 19.1 | 0.0743 | 0.27 | 13.53 | 1
April | 15 | 6AM to 7AM | 57 | 49.5 | 43 | 42.5 | 20.29 | 0.0738 | 0.28 | 13.64 | 1
April | 15 | 7AM to 8AM | 64.9 | 54.2 | 46 | 47.9 | 23.04 | 0.0726 | 0.31 | 13.86 | 1
April | 15 | 8AM to 9AM | 69.1 | 54.5 | 43 | 42.5 | 23.22 | 0.0721 | 0.28 | 13.96 | 1
April | 15 | 9AM to 10AM | 73.9 | 56.4 | 43 | 42.5 | 24.4 | 0.0714 | 0.28 | 14.09 | 1
April | 15 | 10AM to 11AM | 78.1 | 58 | 43 | 42.5 | 25.4 | 0.0709 | 0.28 | 14.19 | 1
April | 15 | 11AM to 12PM | 80.1 | 58.7 | 43 | 42.5 | 25.88 | 0.0706 | 0.28 | 14.25 | 1
April | 15 | 12PM to 1PM | 80.1 | 58.7 | 43 | 42.5 | 25.88 | 0.0706 | 0.28 | 14.25 | 1
April | 15 | 1PM to 2PM | 82 | 59.1 | 42.1 | 41.1 | 26.14 | 0.0704 | 0.27 | 14.29 | 1
April | 15 | 2PM to 3PM | 82 | 60.2 | 45 | 45.9 | 26.89 | 0.0703 | 0.3 | 14.31 | 1
April | 15 | 3PM to 4PM | 82.9 | 60.9 | 46 | 47.9 | 27.42 | 0.0702 | 0.31 | 14.34 | 1
April | 15 | 4PM to 5PM | 80.1 | 59.5 | 45 | 45.9 | 26.41 | 0.0706 | 0.3 | 14.26 | 1
April | 15 | 5PM to 6PM | 77 | 59.6 | 48 | 51.6 | 26.56 | 0.071 | 0.34 | 14.2 | 1
April | 15 | 6PM to 7PM | 73.9 | 59.5 | 50 | 55.6 | 26.45 | 0.0713 | 0.36 | 14.13 | 1
April | 15 | 7PM to 8PM | 71.1 | 57 | 46.9 | 49.6 | 24.79 | 0.0718 | 0.32 | 14.03 | 1
April | 15 | 8PM to 9PM | 66.9 | 55.4 | 46.9 | 49.6 | 23.79 | 0.0723 | 0.32 | 13.92 | 1
April | 15 | 9PM to 10PM | 66.9 | 54.5 | 45 | 45.9 | 23.22 | 0.0724 | 0.3 | 13.91 | 1
April | 15 | 10PM to 11PM | 66.9 | 55.4 | 46.9 | 49.6 | 23.79 | 0.0723 | 0.32 | 13.92 | 1
April | 15 | 11PM to 12AM | 64.9 | 54.2 | 46 | 47.9 | 23.04 | 0.0726 | 0.31 | 13.86 | 1
April | 16 | 12AM to 1AM | 62.1 | 52.5 | 45 | 45.9 | 22.04 | 0.073 | 0.3 | 13.78 | 1
April | 16 | 1AM to 2AM | 64 | 54.2 | 46.9 | 49.6 | 23.09 | 0.0727 | 0.32 | 13.85 | 1
April | 16 | 2AM to 3AM | 60.1 | 52.2 | 46 | 47.9 | 21.86 | 0.0733 | 0.31 | 13.74 | 1
April | 16 | 3AM to 4AM | 59 | 51.2 | 45 | 45.9 | 21.3 | 0.0735 | 0.3 | 13.7 | 1
April | 16 | 4AM to 5AM | 55.9 | 49.5 | 44.1 | 44.4 | 20.31 | 0.0739 | 0.29 | 13.62 | 1
April | 16 | 5AM to 6AM | 55.9 | 49.5 | 44.1 | 44.4 | 20.31 | 0.0739 | 0.29 | 13.62 | 1
April | 16 | 6AM to 7AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
April | 16 | 7AM to 8AM | 64.9 | 55.6 | 48.9 | 53.4 | 23.91 | 0.0726 | 0.35 | 13.88 | 1
April | 16 | 8AM to 9AM | 70 | 57.5 | 48.9 | 53.4 | 25.13 | 0.0719 | 0.35 | 14.02 | 1
April | 16 | 9AM to 10AM | 72 | 58.2 | 48.9 | 53.4 | 25.62 | 0.0716 | 0.35 | 14.07 | 1
April | 16 | 10AM to 11AM | 79 | 59.9 | 46.9 | 49.6 | 26.72 | 0.0707 | 0.32 | 14.24 | 1
April | 16 | 11AM to 12PM | 81 | 60.2 | 46 | 47.9 | 26.94 | 0.0705 | 0.31 | 14.29 | 1
April | 16 | 12PM to 1PM | 82.9 | 60.9 | 46 | 47.9 | 27.42 | 0.0702 | 0.31 | 14.34 | 1
April | 16 | 1PM to 2PM | 84 | 60.9 | 45 | 45.9 | 27.38 | 0.0701 | 0.3 | 14.36 | 1
April | 16 | 2PM to 3PM | 81 | 60.2 | 46 | 47.9 | 26.94 | 0.0705 | 0.31 | 14.29 | 1
April | 16 | 3PM to 4PM | 80.1 | 61.1 | 48.9 | 53.4 | 27.59 | 0.0706 | 0.35 | 14.28 | 1
April | 16 | 4PM to 5PM | 80.1 | 59.9 | 46 | 47.9 | 26.72 | 0.0706 | 0.31 | 14.26 | 1
April | 16 | 5PM to 6PM | 78.1 | 61.4 | 51.1 | 58 | 27.81 | 0.0708 | 0.38 | 14.24 | 1
April | 16 | 6PM to 7PM | 72 | 59.7 | 52 | 59.9 | 26.63 | 0.0716 | 0.39 | 14.09 | 1
April | 16 | 7PM to 8PM | 72 | 57.3 | 46.9 | 49.6 | 25.01 | 0.0717 | 0.32 | 14.06 | 1
April | 16 | 8PM to 9PM | 71.1 | 58.4 | 50 | 55.6 | 25.74 | 0.0717 | 0.36 | 14.05 | 1
April | 16 | 9PM to 10PM | 66.9 | 56.9 | 50 | 55.6 | 24.74 | 0.0723 | 0.36 | 13.94 | 1
April | 16 | 10PM to 11PM | 63 | 57 | 53.1 | 62.4 | 24.82 | 0.0728 | 0.41 | 13.86 | 1
April | 16 | 11PM to 12AM | 61 | 55.1 | 51.1 | 58 | 23.65 | 0.0731 | 0.38 | 13.79 | 1
April | 17 | 12AM to 1AM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
April | 17 | 1AM to 2AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
April | 17 | 2AM to 3AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
April | 17 | 3AM to 4AM | 57.9 | 50.8 | 45 | 45.9 | 21.04 | 0.0736 | 0.3 | 13.67 | 1
April | 17 | 4AM to 5AM | 59 | 51.2 | 45 | 45.9 | 21.3 | 0.0735 | 0.3 | 13.7 | 1
April | 17 | 5AM to 6AM | 55.9 | 50.5 | 46 | 47.9 | 20.86 | 0.0739 | 0.31 | 13.63 | 1
April | 17 | 6AM to 7AM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
April | 17 | 7AM to 8AM | 64 | 55.2 | 48.9 | 53.4 | 23.69 | 0.0727 | 0.35 | 13.86 | 1
April | 17 | 8AM to 9AM | 68 | 57.8 | 51.1 | 58 | 25.36 | 0.0721 | 0.38 | 13.98 | 1
April | 17 | 9AM to 10AM | 73 | 59.6 | 51.1 | 58 | 26.59 | 0.0715 | 0.38 | 14.11 | 1
April | 17 | 10AM to 11AM | 78.1 | 61.4 | 51.1 | 58 | 27.81 | 0.0708 | 0.38 | 14.24 | 1
April | 17 | 11AM to 12PM | 80.1 | 62.1 | 51.1 | 58 | 28.3 | 0.0705 | 0.38 | 14.3 | 1
April | 17 | 12PM to 1PM | 82 | 62.3 | 50 | 55.6 | 28.42 | 0.0703 | 0.36 | 14.34 | 1
April | 17 | 1PM to 2PM | 84 | 61.7 | 46.9 | 49.6 | 27.94 | 0.0701 | 0.32 | 14.37 | 1
April | 17 | 2PM to 3PM | 84 | 61.3 | 46 | 47.9 | 27.68 | 0.0701 | 0.31 | 14.37 | 1
April | 17 | 3PM to 4PM | 84 | 61.3 | 46 | 47.9 | 27.68 | 0.0701 | 0.31 | 14.37 | 1
April | 17 | 4PM to 5PM | 82.9 | 61.7 | 48 | 51.6 | 28.01 | 0.0702 | 0.34 | 14.35 | 1
April | 17 | 5PM to 6PM | 80.1 | 60.7 | 48 | 51.6 | 27.31 | 0.0706 | 0.34 | 14.28 | 1
April | 17 | 6PM to 7PM | 77 | 60.5 | 50 | 55.6 | 27.19 | 0.0709 | 0.36 | 14.21 | 1
April | 17 | 7PM to 8PM | 73 | 59.6 | 51.1 | 58 | 26.59 | 0.0715 | 0.38 | 14.11 | 1
April | 17 | 8PM to 9PM | 68 | 57.3 | 50 | 55.6 | 25 | 0.0722 | 0.36 | 13.97 | 1
April | 17 | 9PM to 10PM | 68 | 56.7 | 48.9 | 53.4 | 24.65 | 0.0722 | 0.35 | 13.96 | 1
April | 17 | 10PM to 11PM | 64.9 | 56.1 | 50 | 55.6 | 24.25 | 0.0726 | 0.36 | 13.89 | 1
April | 17 | 11PM to 12AM | 64 | 56.3 | 51.1 | 58 | 24.39 | 0.0727 | 0.38 | 13.87 | 1
April | 18 | 12AM to 1AM | 62.1 | 55.5 | 51.1 | 58 | 23.91 | 0.073 | 0.38 | 13.82 | 1
April | 18 | 1AM to 2AM | 60.1 | 55.3 | 52 | 59.9 | 23.74 | 0.0732 | 0.39 | 13.77 | 1
April | 18 | 2AM to 3AM | 62.1 | 56 | 52 | 59.9 | 24.22 | 0.0729 | 0.39 | 13.83 | 1
April | 18 | 3AM to 4AM | 60.1 | 55.3 | 52 | 59.9 | 23.74 | 0.0732 | 0.39 | 13.77 | 1
April | 18 | 4AM to 5AM | 57.9 | 53.9 | 51.1 | 58 | 22.9 | 0.0735 | 0.38 | 13.71 | 1
April | 18 | 5AM to 6AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
April | 18 | 6AM to 7AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
April | 18 | 7AM to 8AM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
April | 18 | 8AM to 9AM | 72 | 60.3 | 53.1 | 62.4 | 27.02 | 0.0716 | 0.41 | 14.1 | 1
April | 18 | 9AM to 10AM | 75.9 | 60.7 | 51.1 | 58 | 27.29 | 0.0711 | 0.38 | 14.19 | 1
April | 18 | 10AM to 11AM | 79 | 62.7 | 53.1 | 62.4 | 28.73 | 0.0706 | 0.41 | 14.28 | 1
April | 18 | 11AM to 12PM | 81 | 62.8 | 52 | 59.9 | 28.83 | 0.0704 | 0.39 | 14.33 | 1
April | 18 | 12PM to 1PM | 82 | 61.4 | 48 | 51.6 | 27.79 | 0.0703 | 0.34 | 14.33 | 1
April | 18 | 1PM to 2PM | 81 | 60.6 | 46.9 | 49.6 | 27.2 | 0.0705 | 0.32 | 14.29 | 1
April | 18 | 2PM to 3PM | 78.1 | 62.4 | 53.1 | 62.4 | 28.51 | 0.0708 | 0.41 | 14.26 | 1
April | 18 | 3PM to 4PM | 78.1 | 62.4 | 53.1 | 62.4 | 28.51 | 0.0708 | 0.41 | 14.26 | 1
April | 18 | 4PM to 5PM | 78.1 | 62.4 | 53.1 | 62.4 | 28.51 | 0.0708 | 0.41 | 14.26 | 1
April | 18 | 5PM to 6PM | 75.9 | 62.6 | 55 | 67.2 | 28.73 | 0.071 | 0.44 | 14.22 | 1
April | 18 | 6PM to 7PM | 73 | 59.6 | 51.1 | 58 | 26.59 | 0.0715 | 0.38 | 14.11 | 1
April | 18 | 7PM to 8PM | 71.1 | 61 | 55 | 67.2 | 27.54 | 0.0717 | 0.44 | 14.09 | 1
April | 18 | 8PM to 9PM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
April | 18 | 9PM to 10PM | 66.9 | 57.9 | 52 | 59.9 | 25.41 | 0.0723 | 0.39 | 13.95 | 1
April | 18 | 10PM to 11PM | 66 | 57.5 | 52 | 59.9 | 25.19 | 0.0724 | 0.39 | 13.93 | 1
April | 18 | 11PM to 12AM | 64.9 | 57.7 | 53.1 | 62.4 | 25.31 | 0.0725 | 0.41 | 13.91 | 1
April | 19 | 12AM to 1AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
April | 19 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
April | 19 | 2AM to 3AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
April | 19 | 3AM to 4AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
April | 19 | 4AM to 5AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
April | 19 | 5AM to 6AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
April | 19 | 6AM to 7AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
April | 19 | 7AM to 8AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
April | 19 | 8AM to 9AM | 66.9 | 60 | 55.9 | 69.4 | 26.88 | 0.0722 | 0.45 | 13.98 | 1
April | 19 | 9AM to 10AM | 71.1 | 62.1 | 57 | 72.3 | 28.34 | 0.0716 | 0.47 | 14.1 | 1
April | 19 | 10AM to 11AM | 75 | 63.4 | 57 | 72.3 | 29.3 | 0.0711 | 0.47 | 14.21 | 1
April | 19 | 11AM to 12PM | 77 | 64.1 | 57 | 72.3 | 29.79 | 0.0708 | 0.47 | 14.26 | 1
April | 19 | 12PM to 1PM | 77 | 64.1 | 57 | 72.3 | 29.79 | 0.0708 | 0.47 | 14.26 | 1
April | 19 | 1PM to 2PM | 78.1 | 63.4 | 55 | 67.2 | 29.26 | 0.0707 | 0.44 | 14.27 | 1
April | 19 | 2PM to 3PM | 80.1 | 63.5 | 54 | 64.5 | 29.33 | 0.0705 | 0.42 | 14.32 | 1
April | 19 | 3PM to 4PM | 80.1 | 62.1 | 51.1 | 58 | 28.3 | 0.0705 | 0.38 | 14.3 | 1
April | 19 | 4PM to 5PM | 79 | 61.7 | 51.1 | 58 | 28.03 | 0.0707 | 0.38 | 14.27 | 1
April | 19 | 5PM to 6PM | 77 | 60 | 48.9 | 53.4 | 26.84 | 0.071 | 0.35 | 14.2 | 1
April | 19 | 6PM to 7PM | 73 | 60.6 | 53.1 | 62.4 | 27.28 | 0.0714 | 0.41 | 14.12 | 1
April | 19 | 7PM to 8PM | 69.1 | 61.9 | 57.9 | 74.7 | 28.23 | 0.0719 | 0.48 | 14.06 | 1
April | 19 | 8PM to 9PM | 66 | 60.8 | 57.9 | 74.7 | 27.48 | 0.0723 | 0.48 | 13.98 | 1
April | 19 | 9PM to 10PM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
April | 19 | 10PM to 11PM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
April | 19 | 11PM to 12AM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
April | 20 | 12AM to 1AM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
April | 20 | 1AM to 2AM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
April | 20 | 2AM to 3AM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
April | 20 | 3AM to 4AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
April | 20 | 4AM to 5AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
April | 20 | 5AM to 6AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
April | 20 | 6AM to 7AM | 59 | 56.6 | 55 | 67.2 | 24.6 | 0.0733 | 0.44 | 13.77 | 1
April | 20 | 7AM to 8AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
April | 20 | 8AM to 9AM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
April | 20 | 9AM to 10AM | 69.1 | 60.3 | 55 | 67.2 | 27.06 | 0.0719 | 0.44 | 14.03 | 1
April | 20 | 10AM to 11AM | 72 | 60.7 | 54 | 64.5 | 27.35 | 0.0716 | 0.42 | 14.1 | 1
April | 20 | 11AM to 12PM | 75 | 61.3 | 53.1 | 62.4 | 27.77 | 0.0712 | 0.41 | 14.18 | 1
April | 20 | 12PM to 1PM | 75 | 61.3 | 53.1 | 62.4 | 27.77 | 0.0712 | 0.41 | 14.18 | 1
April | 20 | 1PM to 2PM | 75 | 61.8 | 54 | 64.5 | 28.1 | 0.0712 | 0.42 | 14.18 | 1
April | 20 | 2PM to 3PM | 75 | 61.8 | 54 | 64.5 | 28.1 | 0.0712 | 0.42 | 14.18 | 1
April | 20 | 3PM to 4PM | 75.9 | 62.6 | 55 | 67.2 | 28.73 | 0.071 | 0.44 | 14.22 | 1
April | 20 | 4PM to 5PM | 73.9 | 61.4 | 54 | 64.5 | 27.83 | 0.0713 | 0.42 | 14.16 | 1
April | 20 | 5PM to 6PM | 73 | 61.1 | 54 | 64.5 | 27.61 | 0.0714 | 0.42 | 14.13 | 1
April | 20 | 6PM to 7PM | 72 | 60.7 | 54 | 64.5 | 27.35 | 0.0716 | 0.42 | 14.1 | 1
April | 20 | 7PM to 8PM | 68 | 59.3 | 54 | 64.5 | 26.38 | 0.0721 | 0.42 | 14 | 1
April | 20 | 8PM to 9PM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
April | 20 | 9PM to 10PM | 66 | 59.7 | 55.9 | 69.4 | 26.66 | 0.0723 | 0.45 | 13.96 | 1
April | 20 | 10PM to 11PM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
April | 20 | 11PM to 12AM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
April | 21 | 12AM to 1AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
April | 21 | 1AM to 2AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
April | 21 | 2AM to 3AM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
April | 21 | 3AM to 4AM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
April | 21 | 4AM to 5AM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
April | 21 | 5AM to 6AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
April | 21 | 6AM to 7AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
April | 21 | 7AM to 8AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
April | 21 | 8AM to 9AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
April | 21 | 9AM to 10AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
April | 21 | 10AM to 11AM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
April | 21 | 11AM to 12PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
April | 21 | 12PM to 1PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
April | 21 | 1PM to 2PM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
April | 21 | 2PM to 3PM | 73 | 65.7 | 62.1 | 86.8 | 31.09 | 0.0713 | 0.56 | 14.2 | 1
April | 21 | 3PM to 4PM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
April | 21 | 4PM to 5PM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
April | 21 | 5PM to 6PM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
April | 21 | 6PM to 7PM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
April | 21 | 7PM to 8PM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
April | 21 | 8PM to 9PM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
April | 21 | 9PM to 10PM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
April | 21 | 10PM to 11PM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
April | 21 | 11PM to 12AM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
April | 22 | 12AM to 1AM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
April | 22 | 1AM to 2AM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
April | 22 | 2AM to 3AM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
April | 22 | 3AM to 4AM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
April | 22 | 4AM to 5AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
April | 22 | 5AM to 6AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
April | 22 | 6AM to 7AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
April | 22 | 7AM to 8AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
April | 22 | 8AM to 9AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
April | 22 | 9AM to 10AM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
April | 22 | 10AM to 11AM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
April | 22 | 11AM to 12PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
April | 22 | 12PM to 1PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
April | 22 | 1PM to 2PM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
April | 22 | 2PM to 3PM | 72 | 65.3 | 62.1 | 86.8 | 30.82 | 0.0714 | 0.56 | 14.17 | 1
April | 22 | 3PM to 4PM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
April | 22 | 4PM to 5PM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
April | 22 | 5PM to 6PM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
April | 22 | 6PM to 7PM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
April | 22 | 7PM to 8PM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
April | 22 | 8PM to 9PM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
April | 22 | 9PM to 10PM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
April | 22 | 10PM to 11PM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
April | 22 | 11PM to 12AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
April | 23 | 12AM to 1AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
April | 23 | 1AM to 2AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
April | 23 | 2AM to 3AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
April | 23 | 3AM to 4AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
April | 23 | 4AM to 5AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
April | 23 | 5AM to 6AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
April | 23 | 6AM to 7AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
April | 23 | 7AM to 8AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
April | 23 | 8AM to 9AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
April | 23 | 9AM to 10AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
April | 23 | 10AM to 11AM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
April | 23 | 11AM to 12PM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
April | 23 | 12PM to 1PM | 73 | 65.7 | 62.1 | 86.8 | 31.09 | 0.0713 | 0.56 | 14.2 | 1
April | 23 | 1PM to 2PM | 75 | 65.7 | 61 | 83.5 | 31.06 | 0.071 | 0.54 | 14.24 | 1
April | 23 | 2PM to 3PM | 75.9 | 65.4 | 60.1 | 80.8 | 30.86 | 0.0709 | 0.52 | 14.26 | 1
April | 23 | 3PM to 4PM | 75.9 | 65.4 | 60.1 | 80.8 | 30.86 | 0.0709 | 0.52 | 14.26 | 1
April | 23 | 4PM to 5PM | 77 | 65.8 | 60.1 | 80.8 | 31.12 | 0.0708 | 0.52 | 14.29 | 1
April | 23 | 5PM to 6PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
April | 23 | 6PM to 7PM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
April | 23 | 7PM to 8PM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
April | 23 | 8PM to 9PM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
April | 23 | 9PM to 10PM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
April | 23 | 10PM to 11PM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
April | 23 | 11PM to 12AM | 61 | 60.4 | 60.1 | 80.8 | 27.2 | 0.073 | 0.52 | 13.86 | 1
April | 24 | 12AM to 1AM | 60.1 | 59.4 | 59 | 77.7 | 26.49 | 0.0731 | 0.5 | 13.83 | 1
April | 24 | 1AM to 2AM | 60.1 | 59.4 | 59 | 77.7 | 26.49 | 0.0731 | 0.5 | 13.83 | 1
April | 24 | 2AM to 3AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
April | 24 | 3AM to 4AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
April | 24 | 4AM to 5AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
April | 24 | 5AM to 6AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 24 | 6AM to 7AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
April | 24 | 7AM to 8AM | 59 | 56.6 | 55 | 67.2 | 24.6 | 0.0733 | 0.44 | 13.77 | 1
April | 24 | 8AM to 9AM | 57.9 | 55 | 53.1 | 62.4 | 23.59 | 0.0735 | 0.41 | 13.72 | 1
April | 24 | 9AM to 10AM | 62.1 | 56 | 52 | 59.9 | 24.22 | 0.0729 | 0.39 | 13.83 | 1
April | 24 | 10AM to 11AM | 64.9 | 58.2 | 54 | 64.5 | 25.64 | 0.0725 | 0.42 | 13.92 | 1
April | 24 | 11AM to 12PM | 66 | 57.1 | 51.1 | 58 | 24.88 | 0.0724 | 0.38 | 13.92 | 1
April | 24 | 12PM to 1PM | 66 | 57.1 | 51.1 | 58 | 24.88 | 0.0724 | 0.38 | 13.92 | 1
April | 24 | 1PM to 2PM | 66 | 56 | 48.9 | 53.4 | 24.17 | 0.0724 | 0.35 | 13.91 | 1
April | 24 | 2PM to 3PM | 68 | 55.8 | 46.9 | 49.6 | 24.05 | 0.0722 | 0.32 | 13.95 | 1
April | 24 | 3PM to 4PM | 69.1 | 56.2 | 46.9 | 49.6 | 24.31 | 0.072 | 0.32 | 13.98 | 1
April | 24 | 4PM to 5PM | 70 | 56.2 | 46 | 47.9 | 24.27 | 0.0719 | 0.31 | 14 | 1
April | 24 | 5PM to 6PM | 69.1 | 56.2 | 46.9 | 49.6 | 24.31 | 0.072 | 0.32 | 13.98 | 1
April | 24 | 6PM to 7PM | 64.9 | 54.2 | 46 | 47.9 | 23.04 | 0.0726 | 0.31 | 13.86 | 1
April | 24 | 7PM to 8PM | 61 | 51.7 | 44.1 | 44.4 | 21.54 | 0.0732 | 0.29 | 13.75 | 1
April | 24 | 8PM to 9PM | 55.9 | 49.5 | 44.1 | 44.4 | 20.31 | 0.0739 | 0.29 | 13.62 | 1
April | 24 | 9PM to 10PM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
April | 24 | 10PM to 11PM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
April | 24 | 11PM to 12AM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
April | 25 | 12AM to 1AM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
April | 25 | 1AM to 2AM | 53.1 | 50.2 | 48 | 51.6 | 20.74 | 0.0743 | 0.34 | 13.56 | 1
April | 25 | 2AM to 3AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
April | 25 | 3AM to 4AM | 50 | 48.3 | 46.9 | 49.6 | 19.67 | 0.0747 | 0.32 | 13.47 | 1
April | 25 | 4AM to 5AM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
April | 25 | 5AM to 6AM | 48.9 | 47.4 | 46 | 47.9 | 19.15 | 0.0749 | 0.31 | 13.44 | 1
April | 25 | 6AM to 7AM | 48.9 | 47.4 | 46 | 47.9 | 19.15 | 0.0749 | 0.31 | 13.44 | 1
April | 25 | 7AM to 8AM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
April | 25 | 8AM to 9AM | 55 | 50.5 | 46.9 | 49.6 | 20.9 | 0.074 | 0.32 | 13.61 | 1
April | 25 | 9AM to 10AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
April | 25 | 10AM to 11AM | 61 | 52.1 | 45 | 45.9 | 21.78 | 0.0732 | 0.3 | 13.75 | 1
April | 25 | 11AM to 12PM | 63 | 50.7 | 39.9 | 37.8 | 20.99 | 0.073 | 0.25 | 13.78 | 1
April | 25 | 12PM to 1PM | 64.9 | 50.8 | 37.9 | 34.9 | 21.03 | 0.0727 | 0.23 | 13.82 | 1
April | 25 | 1PM to 2PM | 66 | 52 | 39.9 | 37.8 | 21.73 | 0.0725 | 0.25 | 13.86 | 1
April | 25 | 2PM to 3PM | 64.9 | 51.2 | 39 | 36.4 | 21.26 | 0.0727 | 0.24 | 13.83 | 1
April | 25 | 3PM to 4PM | 64 | 49.4 | 35.1 | 31.1 | 20.22 | 0.0728 | 0.2 | 13.79 | 1
April | 25 | 4PM to 5PM | 62.1 | 48.8 | 36 | 32.3 | 19.92 | 0.0731 | 0.21 | 13.74 | 1
April | 25 | 5PM to 6PM | 61 | 48 | 35.1 | 31.1 | 19.48 | 0.0733 | 0.2 | 13.71 | 1
April | 25 | 6PM to 7PM | 57.9 | 46.7 | 35.1 | 31.1 | 18.74 | 0.0737 | 0.2 | 13.63 | 1
April | 25 | 7PM to 8PM | 55 | 45.3 | 35.1 | 31.1 | 18.04 | 0.0741 | 0.2 | 13.55 | 1
April | 25 | 8PM to 9PM | 52 | 43.9 | 35.1 | 31.1 | 17.3 | 0.0746 | 0.2 | 13.47 | 1
April | 25 | 9PM to 10PM | 50 | 42.9 | 35.1 | 31.1 | 16.82 | 0.0749 | 0.2 | 13.42 | 1
April | 25 | 10PM to 11PM | 48.9 | 42.4 | 35.1 | 31.1 | 16.56 | 0.075 | 0.2 | 13.39 | 1
April | 25 | 11PM to 12AM | 46 | 40.9 | 35.1 | 31.1 | 15.86 | 0.0754 | 0.2 | 13.31 | 1
April | 26 | 12AM to 1AM | 43 | 39.3 | 35.1 | 31.1 | 15.12 | 0.0759 | 0.2 | 13.23 | 1
April | 26 | 1AM to 2AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
April | 26 | 2AM to 3AM | 39.9 | 37.3 | 34 | 29.8 | 14.18 | 0.0764 | 0.2 | 13.15 | 1
April | 26 | 3AM to 4AM | 39.9 | 37.3 | 34 | 29.8 | 14.18 | 0.0764 | 0.2 | 13.15 | 1
April | 26 | 4AM to 5AM | 37 | 35.7 | 34 | 29.8 | 13.48 | 0.0768 | 0.2 | 13.07 | 1
April | 26 | 5AM to 6AM | 37 | 35.7 | 34 | 29.8 | 13.48 | 0.0768 | 0.2 | 13.07 | 1
April | 26 | 6AM to 7AM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
April | 26 | 7AM to 8AM | 46 | 41.3 | 36 | 32.3 | 16.04 | 0.0754 | 0.21 | 13.32 | 1
April | 26 | 8AM to 9AM | 52 | 44.6 | 37 | 33.7 | 17.7 | 0.0745 | 0.22 | 13.48 | 1
April | 26 | 9AM to 10AM | 54 | 45.6 | 37 | 33.7 | 18.18 | 0.0743 | 0.22 | 13.53 | 1
April | 26 | 10AM to 11AM | 57 | 46.2 | 35.1 | 31.1 | 18.52 | 0.0738 | 0.2 | 13.6 | 1
April | 26 | 11AM to 12PM | 61 | 47 | 32 | 27.5 | 18.92 | 0.0733 | 0.18 | 13.7 | 1
April | 26 | 12PM to 1PM | 60.1 | 46.2 | 30.9 | 26.2 | 18.49 | 0.0734 | 0.17 | 13.67 | 1
April | 26 | 1PM to 2PM | 60.1 | 45.5 | 28.9 | 23.9 | 18.13 | 0.0734 | 0.16 | 13.66 | 1
April | 26 | 2PM to 3PM | 60.1 | 45.9 | 30 | 25.1 | 18.33 | 0.0734 | 0.16 | 13.67 | 1
April | 26 | 3PM to 4PM | 61 | 46.6 | 30.9 | 26.2 | 18.71 | 0.0733 | 0.17 | 13.69 | 1
April | 26 | 4PM to 5PM | 61 | 46.6 | 30.9 | 26.2 | 18.71 | 0.0733 | 0.17 | 13.69 | 1
April | 26 | 5PM to 6PM | 60.1 | 46.2 | 30.9 | 26.2 | 18.49 | 0.0734 | 0.17 | 13.67 | 1
April | 26 | 6PM to 7PM | 57.9 | 45.2 | 30.9 | 26.2 | 17.97 | 0.0737 | 0.17 | 13.61 | 1
April | 26 | 7PM to 8PM | 51.1 | 42.7 | 33.1 | 28.8 | 16.71 | 0.0747 | 0.19 | 13.44 | 1
April | 26 | 8PM to 9PM | 50 | 42.9 | 35.1 | 31.1 | 16.82 | 0.0749 | 0.2 | 13.42 | 1
April | 26 | 9PM to 10PM | 46.9 | 41.7 | 36 | 32.3 | 16.26 | 0.0753 | 0.21 | 13.34 | 1
April | 26 | 10PM to 11PM | 44.1 | 40.3 | 36 | 32.3 | 15.56 | 0.0757 | 0.21 | 13.27 | 1
April | 26 | 11PM to 12AM | 43 | 39.7 | 36 | 32.3 | 15.3 | 0.0759 | 0.21 | 13.24 | 1
April | 27 | 12AM to 1AM | 42.1 | 39.2 | 36 | 32.3 | 15.08 | 0.076 | 0.21 | 13.21 | 1
April | 27 | 1AM to 2AM | 42.1 | 39.2 | 36 | 32.3 | 15.08 | 0.076 | 0.21 | 13.21 | 1
April | 27 | 2AM to 3AM | 42.1 | 39.2 | 36 | 32.3 | 15.08 | 0.076 | 0.21 | 13.21 | 1
April | 27 | 3AM to 4AM | 42.1 | 39.2 | 36 | 32.3 | 15.08 | 0.076 | 0.21 | 13.21 | 1
April | 27 | 4AM to 5AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
April | 27 | 5AM to 6AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
April | 27 | 6AM to 7AM | 43 | 39.7 | 36 | 32.3 | 15.3 | 0.0759 | 0.21 | 13.24 | 1
April | 27 | 7AM to 8AM | 50 | 44.1 | 37.9 | 34.9 | 17.41 | 0.0748 | 0.23 | 13.43 | 1
April | 27 | 8AM to 9AM | 55.9 | 47.7 | 39.9 | 37.8 | 19.29 | 0.074 | 0.25 | 13.6 | 1
April | 27 | 9AM to 10AM | 61 | 49.9 | 39.9 | 37.8 | 20.51 | 0.0732 | 0.25 | 13.73 | 1
April | 27 | 10AM to 11AM | 64.9 | 51.2 | 39 | 36.4 | 21.26 | 0.0727 | 0.24 | 13.83 | 1
April | 27 | 11AM to 12PM | 66 | 51 | 37 | 33.7 | 21.1 | 0.0726 | 0.22 | 13.85 | 1
April | 27 | 12PM to 1PM | 69.1 | 52.2 | 37 | 33.7 | 21.84 | 0.0721 | 0.22 | 13.93 | 1
April | 27 | 1PM to 2PM | 71.1 | 53.4 | 37.9 | 34.9 | 22.51 | 0.0719 | 0.23 | 13.98 | 1
April | 27 | 2PM to 3PM | 71.1 | 53.8 | 39 | 36.4 | 22.75 | 0.0719 | 0.24 | 13.99 | 1
April | 27 | 3PM to 4PM | 72 | 54.1 | 39 | 36.4 | 22.96 | 0.0717 | 0.24 | 14.01 | 1
April | 27 | 4PM to 5PM | 72 | 54.1 | 39 | 36.4 | 22.96 | 0.0717 | 0.24 | 14.01 | 1
April | 27 | 5PM to 6PM | 71.1 | 53.8 | 39 | 36.4 | 22.75 | 0.0719 | 0.24 | 13.99 | 1
April | 27 | 6PM to 7PM | 66 | 52 | 39.9 | 37.8 | 21.73 | 0.0725 | 0.25 | 13.86 | 1
April | 27 | 7PM to 8PM | 60.1 | 50.4 | 42.1 | 41.1 | 20.81 | 0.0733 | 0.27 | 13.71 | 1
April | 27 | 8PM to 9PM | 57.9 | 49.9 | 43 | 42.5 | 20.51 | 0.0736 | 0.28 | 13.66 | 1
April | 27 | 9PM to 10PM | 55.9 | 48.6 | 42.1 | 41.1 | 19.8 | 0.0739 | 0.27 | 13.61 | 1
April | 27 | 10PM to 11PM | 52 | 46.8 | 42.1 | 41.1 | 18.84 | 0.0745 | 0.27 | 13.5 | 1
April | 27 | 11PM to 12AM | 54 | 47.7 | 42.1 | 41.1 | 19.32 | 0.0742 | 0.27 | 13.55 | 1
April | 28 | 12AM to 1AM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
April | 28 | 1AM to 2AM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
April | 28 | 2AM to 3AM | 52 | 45.8 | 39.9 | 37.8 | 18.33 | 0.0745 | 0.25 | 13.49 | 1
April | 28 | 3AM to 4AM | 48 | 44 | 39.9 | 37.8 | 17.37 | 0.0751 | 0.25 | 13.39 | 1
April | 28 | 4AM to 5AM | 48 | 44 | 39.9 | 37.8 | 17.37 | 0.0751 | 0.25 | 13.39 | 1
April | 28 | 5AM to 6AM | 46.9 | 43 | 39 | 36.4 | 16.9 | 0.0753 | 0.24 | 13.35 | 1
April | 28 | 6AM to 7AM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
April | 28 | 7AM to 8AM | 60.1 | 50.8 | 43 | 42.5 | 21.03 | 0.0733 | 0.28 | 13.72 | 1
April | 28 | 8AM to 9AM | 64.9 | 53.7 | 45 | 45.9 | 22.74 | 0.0726 | 0.3 | 13.86 | 1
April | 28 | 9AM to 10AM | 64.9 | 53.7 | 45 | 45.9 | 22.74 | 0.0726 | 0.3 | 13.86 | 1
April | 28 | 10AM to 11AM | 66.9 | 55 | 46 | 47.9 | 23.52 | 0.0723 | 0.31 | 13.92 | 1
April | 28 | 11AM to 12PM | 73.9 | 57.7 | 46 | 47.9 | 25.23 | 0.0714 | 0.31 | 14.1 | 1
April | 28 | 12PM to 1PM | 75 | 58.5 | 46.9 | 49.6 | 25.76 | 0.0712 | 0.32 | 14.14 | 1
April | 28 | 1PM to 2PM | 77 | 58.3 | 45 | 45.9 | 25.67 | 0.071 | 0.3 | 14.18 | 1
April | 28 | 2PM to 3PM | 78.1 | 60.4 | 48.9 | 53.4 | 27.11 | 0.0708 | 0.35 | 14.23 | 1
April | 28 | 3PM to 4PM | 77 | 60 | 48.9 | 53.4 | 26.84 | 0.071 | 0.35 | 14.2 | 1
April | 28 | 4PM to 5PM | 75 | 58.9 | 48 | 51.6 | 26.08 | 0.0712 | 0.34 | 14.14 | 1
April | 28 | 5PM to 6PM | 75 | 58.9 | 48 | 51.6 | 26.08 | 0.0712 | 0.34 | 14.14 | 1
April | 28 | 6PM to 7PM | 72 | 58.2 | 48.9 | 53.4 | 25.62 | 0.0716 | 0.35 | 14.07 | 1
April | 28 | 7PM to 8PM | 68 | 57.8 | 51.1 | 58 | 25.36 | 0.0721 | 0.38 | 13.98 | 1
April | 28 | 8PM to 9PM | 64.9 | 56.7 | 51.1 | 58 | 24.61 | 0.0726 | 0.38 | 13.9 | 1
April | 28 | 9PM to 10PM | 63 | 55.9 | 51.1 | 58 | 24.13 | 0.0728 | 0.38 | 13.84 | 1
April | 28 | 10PM to 11PM | 63 | 55.9 | 51.1 | 58 | 24.13 | 0.0728 | 0.38 | 13.84 | 1
April | 28 | 11PM to 12AM | 63 | 55.9 | 51.1 | 58 | 24.13 | 0.0728 | 0.38 | 13.84 | 1
April | 29 | 12AM to 1AM | 61 | 55.1 | 51.1 | 58 | 23.65 | 0.0731 | 0.38 | 13.79 | 1
April | 29 | 1AM to 2AM | 59 | 53.8 | 50 | 55.6 | 22.81 | 0.0734 | 0.36 | 13.73 | 1
April | 29 | 2AM to 3AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
April | 29 | 3AM to 4AM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
April | 29 | 4AM to 5AM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
April | 29 | 5AM to 6AM | 59 | 54.8 | 52 | 59.9 | 23.47 | 0.0734 | 0.39 | 13.74 | 1
April | 29 | 6AM to 7AM | 59 | 54.3 | 51.1 | 58 | 23.17 | 0.0734 | 0.38 | 13.74 | 1
April | 29 | 7AM to 8AM | 60.1 | 55.9 | 53.1 | 62.4 | 24.12 | 0.0732 | 0.41 | 13.78 | 1
April | 29 | 8AM to 9AM | 61 | 56.7 | 54 | 64.5 | 24.67 | 0.0731 | 0.42 | 13.81 | 1
April | 29 | 9AM to 10AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
April | 29 | 10AM to 11AM | 66 | 59.7 | 55.9 | 69.4 | 26.66 | 0.0723 | 0.45 | 13.96 | 1
April | 29 | 11AM to 12PM | 71.1 | 62.6 | 57.9 | 74.7 | 28.71 | 0.0716 | 0.48 | 14.11 | 1
April | 29 | 12PM to 1PM | 72 | 62.4 | 57 | 72.3 | 28.56 | 0.0715 | 0.47 | 14.13 | 1
April | 29 | 1PM to 2PM | 73.9 | 64.2 | 59 | 77.7 | 29.89 | 0.0712 | 0.5 | 14.2 | 1
April | 29 | 2PM to 3PM | 75 | 64.5 | 59 | 77.7 | 30.15 | 0.0711 | 0.5 | 14.23 | 1
April | 29 | 3PM to 4PM | 75 | 63.9 | 57.9 | 74.7 | 29.68 | 0.0711 | 0.48 | 14.22 | 1
April | 29 | 4PM to 5PM | 75 | 64.5 | 59 | 77.7 | 30.15 | 0.0711 | 0.5 | 14.23 | 1
April | 29 | 5PM to 6PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
April | 29 | 6PM to 7PM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
April | 29 | 7PM to 8PM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
April | 29 | 8PM to 9PM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
April | 29 | 9PM to 10PM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
April | 29 | 10PM to 11PM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
April | 29 | 11PM to 12AM | 60.1 | 58.2 | 57 | 72.3 | 25.65 | 0.0731 | 0.47 | 13.81 | 1
April | 30 | 12AM to 1AM | 57.9 | 57.4 | 57 | 72.3 | 25.12 | 0.0735 | 0.47 | 13.75 | 1
April | 30 | 1AM to 2AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 30 | 2AM to 3AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 30 | 3AM to 4AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 30 | 4AM to 5AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 30 | 5AM to 6AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 30 | 6AM to 7AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
April | 30 | 7AM to 8AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
April | 30 | 8AM to 9AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
April | 30 | 9AM to 10AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
April | 30 | 10AM to 11AM | 66 | 61.5 | 59 | 77.7 | 27.95 | 0.0723 | 0.5 | 13.99 | 1
April | 30 | 11AM to 12PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
April | 30 | 12PM to 1PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
April | 30 | 1PM to 2PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
April | 30 | 2PM to 3PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
April | 30 | 3PM to 4PM | 73 | 65.7 | 62.1 | 86.8 | 31.09 | 0.0713 | 0.56 | 14.2 | 1
April | 30 | 4PM to 5PM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
April | 30 | 5PM to 6PM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
April | 30 | 6PM to 7PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
April | 30 | 7PM to 8PM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
April | 30 | 8PM to 9PM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
April | 30 | 9PM to 10PM | 62.6 | 62.6 | 62.6 | 88.5 | 28.79 | 0.0727 | 0.57 | 13.93 | 1
April | 30 | 10PM to 11PM | 62.4 | 62.4 | 62.4 | 87.9 | 28.66 | 0.0727 | 0.57 | 13.92 | 1
April | 30 | 11PM to 12AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 1 | 12AM to 1AM | 61.9 | 61.9 | 61.9 | 86.2 | 28.26 | 0.0728 | 0.56 | 13.9 | 1
May | 1 | 1AM to 2AM | 61.5 | 61.5 | 61.5 | 85.1 | 28 | 0.0729 | 0.55 | 13.89 | 1
May | 1 | 2AM to 3AM | 61.3 | 61.3 | 61.3 | 84.6 | 27.87 | 0.0729 | 0.55 | 13.88 | 1
May | 1 | 3AM to 4AM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
May | 1 | 4AM to 5AM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
May | 1 | 5AM to 6AM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
May | 1 | 6AM to 7AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
May | 1 | 7AM to 8AM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
May | 1 | 8AM to 9AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
May | 1 | 9AM to 10AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
May | 1 | 10AM to 11AM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
May | 1 | 11AM to 12PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 1 | 12PM to 1PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
May | 1 | 1PM to 2PM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
May | 1 | 2PM to 3PM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
May | 1 | 3PM to 4PM | 73.9 | 64.2 | 59 | 77.7 | 29.89 | 0.0712 | 0.5 | 14.2 | 1
May | 1 | 4PM to 5PM | 75 | 63.9 | 57.9 | 74.7 | 29.68 | 0.0711 | 0.48 | 14.22 | 1
May | 1 | 5PM to 6PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
May | 1 | 6PM to 7PM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
May | 1 | 7PM to 8PM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
May | 1 | 8PM to 9PM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 1 | 9PM to 10PM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
May | 1 | 10PM to 11PM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
May | 1 | 11PM to 12AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 2 | 12AM to 1AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 2 | 1AM to 2AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 2 | 2AM to 3AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 2 | 3AM to 4AM | 60.1 | 60.1 | 60.1 | 80.8 | 26.98 | 0.0731 | 0.52 | 13.84 | 1
May | 2 | 4AM to 5AM | 60.1 | 60.1 | 60.1 | 80.8 | 26.98 | 0.0731 | 0.52 | 13.84 | 1
May | 2 | 5AM to 6AM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
May | 2 | 6AM to 7AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
May | 2 | 7AM to 8AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 2 | 8AM to 9AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 2 | 9AM to 10AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
May | 2 | 10AM to 11AM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
May | 2 | 11AM to 12PM | 73.9 | 66 | 62.1 | 86.8 | 31.31 | 0.0712 | 0.56 | 14.23 | 1
May | 2 | 12PM to 1PM | 75.9 | 65.4 | 60.1 | 80.8 | 30.86 | 0.0709 | 0.52 | 14.26 | 1
May | 2 | 1PM to 2PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
May | 2 | 2PM to 3PM | 75.9 | 64.8 | 59 | 77.7 | 30.37 | 0.071 | 0.5 | 14.25 | 1
May | 2 | 3PM to 4PM | 75.9 | 65.4 | 60.1 | 80.8 | 30.86 | 0.0709 | 0.52 | 14.26 | 1
May | 2 | 4PM to 5PM | 75 | 64.5 | 59 | 77.7 | 30.15 | 0.0711 | 0.5 | 14.23 | 1
May | 2 | 5PM to 6PM | 73.9 | 64.8 | 60.1 | 80.8 | 30.37 | 0.0712 | 0.52 | 14.21 | 1
May | 2 | 6PM to 7PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
May | 2 | 7PM to 8PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
May | 2 | 8PM to 9PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
May | 2 | 9PM to 10PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 2 | 10PM to 11PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 2 | 11PM to 12AM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 3 | 12AM to 1AM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 3 | 1AM to 2AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 3 | 2AM to 3AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
May | 3 | 3AM to 4AM | 61 | 60.4 | 60.1 | 80.8 | 27.2 | 0.073 | 0.52 | 13.86 | 1
May | 3 | 4AM to 5AM | 61 | 60.4 | 60.1 | 80.8 | 27.2 | 0.073 | 0.52 | 13.86 | 1
May | 3 | 5AM to 6AM | 61 | 60.4 | 60.1 | 80.8 | 27.2 | 0.073 | 0.52 | 13.86 | 1
May | 3 | 6AM to 7AM | 61 | 60.4 | 60.1 | 80.8 | 27.2 | 0.073 | 0.52 | 13.86 | 1
May | 3 | 7AM to 8AM | 62.1 | 60.8 | 60.1 | 80.8 | 27.46 | 0.0728 | 0.52 | 13.89 | 1
May | 3 | 8AM to 9AM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
May | 3 | 9AM to 10AM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
May | 3 | 10AM to 11AM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
May | 3 | 11AM to 12PM | 77 | 66.3 | 61 | 83.5 | 31.54 | 0.0708 | 0.54 | 14.3 | 1
May | 3 | 12PM to 1PM | 77 | 66.3 | 61 | 83.5 | 31.54 | 0.0708 | 0.54 | 14.3 | 1
May | 3 | 1PM to 2PM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
May | 3 | 2PM to 3PM | 79 | 68.7 | 64 | 93.2 | 33.55 | 0.0705 | 0.6 | 14.38 | 1
May | 3 | 3PM to 4PM | 77 | 65.8 | 60.1 | 80.8 | 31.12 | 0.0708 | 0.52 | 14.29 | 1
May | 3 | 4PM to 5PM | 77 | 65.1 | 59 | 77.7 | 30.64 | 0.0708 | 0.5 | 14.28 | 1
May | 3 | 5PM to 6PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
May | 3 | 6PM to 7PM | 70 | 62.8 | 59 | 77.7 | 28.92 | 0.0717 | 0.5 | 14.09 | 1
May | 3 | 7PM to 8PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
May | 3 | 8PM to 9PM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
May | 3 | 9PM to 10PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
May | 3 | 10PM to 11PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
May | 3 | 11PM to 12AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
May | 4 | 12AM to 1AM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
May | 4 | 1AM to 2AM | 61 | 60.4 | 60.1 | 80.8 | 27.2 | 0.073 | 0.52 | 13.86 | 1
May | 4 | 2AM to 3AM | 60.1 | 60.1 | 60.1 | 80.8 | 26.98 | 0.0731 | 0.52 | 13.84 | 1
May | 4 | 3AM to 4AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
May | 4 | 4AM to 5AM | 57.9 | 57.9 | 57.9 | 74.7 | 25.5 | 0.0734 | 0.48 | 13.76 | 1
May | 4 | 5AM to 6AM | 59 | 58.3 | 57.9 | 74.7 | 25.76 | 0.0733 | 0.48 | 13.79 | 1
May | 4 | 6AM to 7AM | 59 | 58.3 | 57.9 | 74.7 | 25.76 | 0.0733 | 0.48 | 13.79 | 1
May | 4 | 7AM to 8AM | 62.1 | 58.9 | 57 | 72.3 | 26.13 | 0.0729 | 0.47 | 13.86 | 1
May | 4 | 8AM to 9AM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
May | 4 | 9AM to 10AM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
May | 4 | 10AM to 11AM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
May | 4 | 11AM to 12PM | 78.1 | 66.1 | 60.1 | 80.8 | 31.39 | 0.0706 | 0.52 | 14.32 | 1
May | 4 | 12PM to 1PM | 79 | 65.2 | 57.9 | 74.7 | 30.65 | 0.0706 | 0.48 | 14.32 | 1
May | 4 | 1PM to 2PM | 79 | 65.2 | 57.9 | 74.7 | 30.65 | 0.0706 | 0.48 | 14.32 | 1
May | 4 | 2PM to 3PM | 80.1 | 65 | 57 | 72.3 | 30.54 | 0.0704 | 0.47 | 14.34 | 1
May | 4 | 3PM to 4PM | 80.1 | 65 | 57 | 72.3 | 30.54 | 0.0704 | 0.47 | 14.34 | 1
May | 4 | 4PM to 5PM | 79 | 64.1 | 55.9 | 69.4 | 29.83 | 0.0706 | 0.45 | 14.31 | 1
May | 4 | 5PM to 6PM | 78.1 | 64.4 | 57 | 72.3 | 30.05 | 0.0707 | 0.47 | 14.29 | 1
May | 4 | 6PM to 7PM | 73 | 63.2 | 57.9 | 74.7 | 29.2 | 0.0714 | 0.48 | 14.16 | 1
May | 4 | 7PM to 8PM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
May | 4 | 8PM to 9PM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
May | 4 | 9PM to 10PM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
May | 4 | 10PM to 11PM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
May | 4 | 11PM to 12AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
May | 5 | 12AM to 1AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
May | 5 | 1AM to 2AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
May | 5 | 2AM to 3AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
May | 5 | 3AM to 4AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
May | 5 | 4AM to 5AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
May | 5 | 5AM to 6AM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
May | 5 | 6AM to 7AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
May | 5 | 7AM to 8AM | 66.9 | 61.2 | 57.9 | 74.7 | 27.7 | 0.0722 | 0.48 | 14 | 1
May | 5 | 8AM to 9AM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
May | 5 | 9AM to 10AM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
May | 5 | 10AM to 11AM | 78.1 | 64.9 | 57.9 | 74.7 | 30.43 | 0.0707 | 0.48 | 14.3 | 1
May | 5 | 11AM to 12PM | 80.1 | 66.1 | 59 | 77.7 | 31.39 | 0.0704 | 0.5 | 14.36 | 1
May | 5 | 12PM to 1PM | 81 | 65.8 | 57.9 | 74.7 | 31.14 | 0.0703 | 0.48 | 14.37 | 1
May | 5 | 1PM to 2PM | 82 | 66.7 | 59 | 77.7 | 31.87 | 0.0702 | 0.5 | 14.41 | 1
May | 5 | 2PM to 3PM | 82 | 66.7 | 59 | 77.7 | 31.87 | 0.0702 | 0.5 | 14.41 | 1
May | 5 | 3PM to 4PM | 82 | 66.7 | 59 | 77.7 | 31.87 | 0.0702 | 0.5 | 14.41 | 1
May | 5 | 4PM to 5PM | 82.9 | 66.4 | 57.9 | 74.7 | 31.62 | 0.0701 | 0.48 | 14.43 | 1
May | 5 | 5PM to 6PM | 81 | 64.8 | 55.9 | 69.4 | 30.32 | 0.0703 | 0.45 | 14.36 | 1
May | 5 | 6PM to 7PM | 78.1 | 64.9 | 57.9 | 74.7 | 30.43 | 0.0707 | 0.48 | 14.3 | 1
May | 5 | 7PM to 8PM | 73 | 63.2 | 57.9 | 74.7 | 29.2 | 0.0714 | 0.48 | 14.16 | 1
May | 5 | 8PM to 9PM | 71.1 | 62.6 | 57.9 | 74.7 | 28.71 | 0.0716 | 0.48 | 14.11 | 1
May | 5 | 9PM to 10PM | 69.1 | 61.9 | 57.9 | 74.7 | 28.23 | 0.0719 | 0.48 | 14.06 | 1
May | 5 | 10PM to 11PM | 66.9 | 60 | 55.9 | 69.4 | 26.88 | 0.0722 | 0.45 | 13.98 | 1
May | 5 | 11PM to 12AM | 64.9 | 58.2 | 54 | 64.5 | 25.64 | 0.0725 | 0.42 | 13.92 | 1
May | 6 | 12AM to 1AM | 64.9 | 58.2 | 54 | 64.5 | 25.64 | 0.0725 | 0.42 | 13.92 | 1
May | 6 | 1AM to 2AM | 64 | 59 | 55.9 | 69.4 | 26.18 | 0.0726 | 0.45 | 13.91 | 1
May | 6 | 2AM to 3AM | 62.1 | 58.9 | 57 | 72.3 | 26.13 | 0.0729 | 0.47 | 13.86 | 1
May | 6 | 3AM to 4AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
May | 6 | 4AM to 5AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
May | 6 | 5AM to 6AM | 66 | 60.3 | 57 | 72.3 | 27.1 | 0.0723 | 0.47 | 13.97 | 1
May | 6 | 6AM to 7AM | 66 | 60.8 | 57.9 | 74.7 | 27.48 | 0.0723 | 0.48 | 13.98 | 1
May | 6 | 7AM to 8AM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
May | 6 | 8AM to 9AM | 75 | 65.7 | 61 | 83.5 | 31.06 | 0.071 | 0.54 | 14.24 | 1
May | 6 | 9AM to 10AM | 79 | 66.9 | 61 | 83.5 | 32.03 | 0.0705 | 0.54 | 14.35 | 1
May | 6 | 10AM to 11AM | 81 | 67.5 | 61 | 83.5 | 32.51 | 0.0703 | 0.54 | 14.4 | 1
May | 6 | 11AM to 12PM | 81 | 67 | 60.1 | 80.8 | 32.09 | 0.0703 | 0.52 | 14.39 | 1
May | 6 | 12PM to 1PM | 82.9 | 67 | 59 | 77.7 | 32.09 | 0.07 | 0.5 | 14.44 | 1
May | 6 | 1PM to 2PM | 82.9 | 67 | 59 | 77.7 | 32.09 | 0.07 | 0.5 | 14.44 | 1
May | 6 | 2PM to 3PM | 84 | 67.9 | 60.1 | 80.8 | 32.84 | 0.0699 | 0.52 | 14.48 | 1
May | 6 | 3PM to 4PM | 86 | 67.9 | 59 | 77.7 | 32.84 | 0.0696 | 0.5 | 14.52 | 1
May | 6 | 4PM to 5PM | 82 | 66.2 | 57.9 | 74.7 | 31.4 | 0.0702 | 0.48 | 14.4 | 1
May | 6 | 5PM to 6PM | 81 | 67.5 | 61 | 83.5 | 32.51 | 0.0703 | 0.54 | 14.4 | 1
May | 6 | 6PM to 7PM | 80.1 | 67.8 | 62.1 | 86.8 | 32.81 | 0.0704 | 0.56 | 14.39 | 1
May | 6 | 7PM to 8PM | 75 | 66.3 | 62.1 | 86.8 | 31.58 | 0.071 | 0.56 | 14.26 | 1
May | 6 | 8PM to 9PM | 73 | 65.7 | 62.1 | 86.8 | 31.09 | 0.0713 | 0.56 | 14.2 | 1
May | 6 | 9PM to 10PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
May | 6 | 10PM to 11PM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
May | 6 | 11PM to 12AM | 69.1 | 62.5 | 59 | 77.7 | 28.7 | 0.0719 | 0.5 | 14.07 | 1
May | 7 | 12AM to 1AM | 68 | 62.2 | 59 | 77.7 | 28.43 | 0.072 | 0.5 | 14.04 | 1
May | 7 | 1AM to 2AM | 66 | 60.3 | 57 | 72.3 | 27.1 | 0.0723 | 0.47 | 13.97 | 1
May | 7 | 2AM to 3AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
May | 7 | 3AM to 4AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
May | 7 | 4AM to 5AM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
May | 7 | 5AM to 6AM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
May | 7 | 6AM to 7AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
May | 7 | 7AM to 8AM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
May | 7 | 8AM to 9AM | 73.9 | 66.5 | 63 | 89.6 | 31.76 | 0.0711 | 0.58 | 14.24 | 1
May | 7 | 9AM to 10AM | 77 | 68.1 | 64 | 93.2 | 33.06 | 0.0707 | 0.6 | 14.33 | 1
May | 7 | 10AM to 11AM | 81 | 69.8 | 64.9 | 96.2 | 34.51 | 0.0702 | 0.62 | 14.44 | 1
May | 7 | 11AM to 12PM | 82 | 69 | 63 | 89.6 | 33.75 | 0.0701 | 0.58 | 14.45 | 1
May | 7 | 12PM to 1PM | 82.9 | 69.2 | 63 | 89.6 | 33.97 | 0.07 | 0.58 | 14.48 | 1
May | 7 | 1PM to 2PM | 66 | 62.7 | 61 | 83.5 | 28.85 | 0.0723 | 0.54 | 14.01 | 1
May | 7 | 2PM to 3PM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
May | 7 | 3PM to 4PM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
May | 7 | 4PM to 5PM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
May | 7 | 5PM to 6PM | 75.9 | 68.4 | 64.9 | 96.2 | 33.27 | 0.0708 | 0.62 | 14.31 | 1
May | 7 | 6PM to 7PM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
May | 7 | 7PM to 8PM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
May | 7 | 8PM to 9PM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
May | 7 | 9PM to 10PM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 7 | 10PM to 11PM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
May | 7 | 11PM to 12AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 8 | 12AM to 1AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
May | 8 | 1AM to 2AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
May | 8 | 2AM to 3AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
May | 8 | 3AM to 4AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
May | 8 | 4AM to 5AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 8 | 5AM to 6AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
May | 8 | 6AM to 7AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
May | 8 | 7AM to 8AM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
May | 8 | 8AM to 9AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
May | 8 | 9AM to 10AM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
May | 8 | 10AM to 11AM | 75.9 | 68.4 | 64.9 | 96.2 | 33.27 | 0.0708 | 0.62 | 14.31 | 1
May | 8 | 11AM to 12PM | 75.9 | 67.1 | 63 | 89.6 | 32.24 | 0.0709 | 0.58 | 14.29 | 1
May | 8 | 12PM to 1PM | 80.1 | 68.4 | 63 | 89.6 | 33.26 | 0.0703 | 0.58 | 14.4 | 1
May | 8 | 1PM to 2PM | 82 | 68.4 | 62.1 | 86.8 | 33.3 | 0.0701 | 0.56 | 14.44 | 1
May | 8 | 2PM to 3PM | 84 | 69.6 | 63 | 89.6 | 34.23 | 0.0698 | 0.58 | 14.5 | 1
May | 8 | 3PM to 4PM | 82 | 68.4 | 62.1 | 86.8 | 33.3 | 0.0701 | 0.56 | 14.44 | 1
May | 8 | 4PM to 5PM | 82 | 68.4 | 62.1 | 86.8 | 33.3 | 0.0701 | 0.56 | 14.44 | 1
May | 8 | 5PM to 6PM | 79 | 66.9 | 61 | 83.5 | 32.03 | 0.0705 | 0.54 | 14.35 | 1
May | 8 | 6PM to 7PM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
May | 8 | 7PM to 8PM | 73 | 64.5 | 60.1 | 80.8 | 30.15 | 0.0713 | 0.52 | 14.18 | 1
May | 8 | 8PM to 9PM | 69.1 | 62.5 | 59 | 77.7 | 28.7 | 0.0719 | 0.5 | 14.07 | 1
May | 8 | 9PM to 10PM | 68 | 61.5 | 57.9 | 74.7 | 27.96 | 0.072 | 0.48 | 14.03 | 1
May | 8 | 10PM to 11PM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
May | 8 | 11PM to 12AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
May | 9 | 12AM to 1AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
May | 9 | 1AM to 2AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
May | 9 | 2AM to 3AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
May | 9 | 3AM to 4AM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
May | 9 | 4AM to 5AM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
May | 9 | 5AM to 6AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
May | 9 | 6AM to 7AM | 59 | 55.9 | 54 | 64.5 | 24.19 | 0.0733 | 0.42 | 13.76 | 1
May | 9 | 7AM to 8AM | 62.1 | 56.6 | 53.1 | 62.4 | 24.6 | 0.0729 | 0.41 | 13.83 | 1
May | 9 | 8AM to 9AM | 66.9 | 56.3 | 48.9 | 53.4 | 24.39 | 0.0723 | 0.35 | 13.93 | 1
May | 9 | 9AM to 10AM | 69.1 | 52.6 | 37.9 | 34.9 | 22.03 | 0.0721 | 0.23 | 13.93 | 1
May | 9 | 10AM to 11AM | 71.1 | 53.8 | 39 | 36.4 | 22.75 | 0.0719 | 0.24 | 13.99 | 1
May | 9 | 11AM to 12PM | 72 | 54.9 | 41 | 39.4 | 23.42 | 0.0717 | 0.26 | 14.02 | 1
May | 9 | 12PM to 1PM | 73.9 | 56.4 | 43 | 42.5 | 24.4 | 0.0714 | 0.28 | 14.09 | 1
May | 9 | 1PM to 2PM | 73 | 54.9 | 39.9 | 37.8 | 23.43 | 0.0716 | 0.25 | 14.05 | 1
May | 9 | 2PM to 3PM | 73 | 54.9 | 39.9 | 37.8 | 23.43 | 0.0716 | 0.25 | 14.05 | 1
May | 9 | 3PM to 4PM | 73 | 53.9 | 37 | 33.7 | 22.8 | 0.0716 | 0.22 | 14.03 | 1
May | 9 | 4PM to 5PM | 70 | 51.9 | 35.1 | 31.1 | 21.66 | 0.072 | 0.2 | 13.94 | 1
May | 9 | 5PM to 6PM | 68 | 49.8 | 30.9 | 26.2 | 20.41 | 0.0723 | 0.17 | 13.88 | 1
May | 9 | 6PM to 7PM | 64 | 47.4 | 28.9 | 23.9 | 19.09 | 0.0729 | 0.16 | 13.77 | 1
May | 9 | 7PM to 8PM | 60.1 | 45.2 | 28 | 22.9 | 17.98 | 0.0735 | 0.15 | 13.66 | 1
May | 9 | 8PM to 9PM | 55.9 | 43.2 | 28 | 22.9 | 16.98 | 0.074 | 0.15 | 13.55 | 1
May | 9 | 9PM to 10PM | 52 | 41.6 | 28.9 | 23.9 | 16.18 | 0.0746 | 0.16 | 13.45 | 1
May | 9 | 10PM to 11PM | 54 | 42.6 | 28.9 | 23.9 | 16.66 | 0.0743 | 0.16 | 13.5 | 1
May | 9 | 11PM to 12AM | 52 | 41.6 | 28.9 | 23.9 | 16.18 | 0.0746 | 0.16 | 13.45 | 1
May | 10 | 12AM to 1AM | 51.1 | 41.1 | 28.9 | 23.9 | 15.96 | 0.0747 | 0.16 | 13.42 | 1
May | 10 | 1AM to 2AM | 51.1 | 41.1 | 28.9 | 23.9 | 15.96 | 0.0747 | 0.16 | 13.42 | 1
May | 10 | 2AM to 3AM | 50 | 40.6 | 28.9 | 23.9 | 15.7 | 0.0749 | 0.16 | 13.4 | 1
May | 10 | 3AM to 4AM | 48 | 40 | 30 | 25.1 | 15.41 | 0.0752 | 0.16 | 13.35 | 1
May | 10 | 4AM to 5AM | 48 | 40 | 30 | 25.1 | 15.41 | 0.0752 | 0.16 | 13.35 | 1
May | 10 | 5AM to 6AM | 48.9 | 40.4 | 30 | 25.1 | 15.63 | 0.0751 | 0.16 | 13.37 | 1
May | 10 | 6AM to 7AM | 48.9 | 40.4 | 30 | 25.1 | 15.63 | 0.0751 | 0.16 | 13.37 | 1
May | 10 | 7AM to 8AM | 52 | 42.7 | 32 | 27.5 | 16.74 | 0.0746 | 0.18 | 13.46 | 1
May | 10 | 8AM to 9AM | 57 | 45.2 | 32 | 27.5 | 17.96 | 0.0739 | 0.18 | 13.59 | 1
May | 10 | 9AM to 10AM | 60.1 | 46.6 | 32 | 27.5 | 18.7 | 0.0734 | 0.18 | 13.67 | 1
May | 10 | 10AM to 11AM | 63 | 48.9 | 35.1 | 31.1 | 19.96 | 0.073 | 0.2 | 13.76 | 1
May | 10 | 11AM to 12PM | 64 | 50.1 | 37 | 33.7 | 20.62 | 0.0728 | 0.22 | 13.8 | 1
May | 10 | 12PM to 1PM | 68 | 52.5 | 39 | 36.4 | 22.01 | 0.0723 | 0.24 | 13.91 | 1
May | 10 | 1PM to 2PM | 69.1 | 53.7 | 41 | 39.4 | 22.73 | 0.0721 | 0.26 | 13.95 | 1
May | 10 | 2PM to 3PM | 71.1 | 54.5 | 41 | 39.4 | 23.21 | 0.0718 | 0.26 | 14 | 1
May | 10 | 3PM to 4PM | 72 | 54.9 | 41 | 39.4 | 23.42 | 0.0717 | 0.26 | 14.02 | 1
May | 10 | 4PM to 5PM | 71.1 | 53.1 | 37 | 33.7 | 22.32 | 0.0719 | 0.22 | 13.98 | 1
May | 10 | 5PM to 6PM | 70 | 51 | 32 | 27.5 | 21.09 | 0.0721 | 0.18 | 13.93 | 1
May | 10 | 6PM to 7PM | 68 | 49.1 | 28.9 | 23.9 | 20.05 | 0.0723 | 0.16 | 13.87 | 1
May | 10 | 7PM to 8PM | 62.1 | 47.5 | 32 | 27.5 | 19.18 | 0.0731 | 0.18 | 13.72 | 1
May | 10 | 8PM to 9PM | 59 | 46.5 | 33.1 | 28.8 | 18.63 | 0.0736 | 0.19 | 13.65 | 1
May | 10 | 9PM to 10PM | 55.9 | 45 | 33.1 | 28.8 | 17.89 | 0.074 | 0.19 | 13.57 | 1
May | 10 | 10PM to 11PM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
May | 10 | 11PM to 12AM | 52 | 43.4 | 34 | 29.8 | 17.1 | 0.0746 | 0.2 | 13.47 | 1
May | 11 | 12AM to 1AM | 50 | 42.5 | 34 | 29.8 | 16.62 | 0.0749 | 0.2 | 13.41 | 1
May | 11 | 1AM to 2AM | 50 | 42.5 | 34 | 29.8 | 16.62 | 0.0749 | 0.2 | 13.41 | 1
May | 11 | 2AM to 3AM | 50 | 42.9 | 35.1 | 31.1 | 16.82 | 0.0749 | 0.2 | 13.42 | 1
May | 11 | 3AM to 4AM | 48.9 | 43.2 | 37 | 33.7 | 16.96 | 0.075 | 0.22 | 13.4 | 1
May | 11 | 4AM to 5AM | 46.9 | 41.7 | 36 | 32.3 | 16.26 | 0.0753 | 0.21 | 13.34 | 1
May | 11 | 5AM to 6AM | 46 | 41.7 | 37 | 33.7 | 16.26 | 0.0754 | 0.22 | 13.32 | 1
May | 11 | 6AM to 7AM | 50 | 43.7 | 37 | 33.7 | 17.22 | 0.0748 | 0.22 | 13.43 | 1
May | 11 | 7AM to 8AM | 53.1 | 46 | 39 | 36.4 | 18.39 | 0.0744 | 0.24 | 13.52 | 1
May | 11 | 8AM to 9AM | 57.9 | 50.4 | 44.1 | 44.4 | 20.79 | 0.0736 | 0.29 | 13.67 | 1
May | 11 | 9AM to 10AM | 63 | 55.9 | 51.1 | 58 | 24.13 | 0.0728 | 0.38 | 13.84 | 1
May | 11 | 10AM to 11AM | 68 | 58.8 | 53.1 | 62.4 | 26.05 | 0.0721 | 0.41 | 13.99 | 1
May | 11 | 11AM to 12PM | 73 | 58.6 | 48.9 | 53.4 | 25.88 | 0.0715 | 0.35 | 14.1 | 1
May | 11 | 12PM to 1PM | 72 | 57.8 | 48 | 51.6 | 25.34 | 0.0716 | 0.34 | 14.06 | 1
May | 11 | 1PM to 2PM | 73 | 57.7 | 46.9 | 49.6 | 25.27 | 0.0715 | 0.32 | 14.08 | 1
May | 11 | 2PM to 3PM | 73 | 57.3 | 46 | 47.9 | 25.01 | 0.0715 | 0.31 | 14.08 | 1
May | 11 | 3PM to 4PM | 73 | 58.6 | 48.9 | 53.4 | 25.88 | 0.0715 | 0.35 | 14.1 | 1
May | 11 | 4PM to 5PM | 73 | 58.6 | 48.9 | 53.4 | 25.88 | 0.0715 | 0.35 | 14.1 | 1
May | 11 | 5PM to 6PM | 73 | 57.7 | 46.9 | 49.6 | 25.27 | 0.0715 | 0.32 | 14.08 | 1
May | 11 | 6PM to 7PM | 69.1 | 56.2 | 46.9 | 49.6 | 24.31 | 0.072 | 0.32 | 13.98 | 1
May | 11 | 7PM to 8PM | 66 | 55.5 | 48 | 51.6 | 23.89 | 0.0724 | 0.34 | 13.9 | 1
May | 11 | 8PM to 9PM | 63 | 54.3 | 48 | 51.6 | 23.15 | 0.0729 | 0.34 | 13.82 | 1
May | 11 | 9PM to 10PM | 62.1 | 54.4 | 48.9 | 53.4 | 23.21 | 0.073 | 0.35 | 13.81 | 1
May | 11 | 10PM to 11PM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
May | 11 | 11PM to 12AM | 61 | 53 | 46.9 | 49.6 | 22.34 | 0.0732 | 0.32 | 13.76 | 1
May | 12 | 12AM to 1AM | 60.1 | 51.7 | 45 | 45.9 | 21.56 | 0.0733 | 0.3 | 13.73 | 1
May | 12 | 1AM to 2AM | 59 | 51.8 | 46 | 47.9 | 21.6 | 0.0735 | 0.31 | 13.71 | 1
May | 12 | 2AM to 3AM | 55.9 | 50.5 | 46 | 47.9 | 20.86 | 0.0739 | 0.31 | 13.63 | 1
May | 12 | 3AM to 4AM | 54 | 49.6 | 46 | 47.9 | 20.37 | 0.0742 | 0.31 | 13.57 | 1
May | 12 | 4AM to 5AM | 53.1 | 48.7 | 45 | 45.9 | 19.85 | 0.0743 | 0.3 | 13.54 | 1
May | 12 | 5AM to 6AM | 52 | 48.2 | 45 | 45.9 | 19.59 | 0.0745 | 0.3 | 13.52 | 1
May | 12 | 6AM to 7AM | 53.1 | 49.2 | 46 | 47.9 | 20.16 | 0.0743 | 0.31 | 13.55 | 1
May | 12 | 7AM to 8AM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
May | 12 | 8AM to 9AM | 62.1 | 54.4 | 48.9 | 53.4 | 23.21 | 0.073 | 0.35 | 13.81 | 1
May | 12 | 9AM to 10AM | 68 | 57.3 | 50 | 55.6 | 25 | 0.0722 | 0.36 | 13.97 | 1
May | 12 | 10AM to 11AM | 70 | 58 | 50 | 55.6 | 25.48 | 0.0719 | 0.36 | 14.02 | 1
May | 12 | 11AM to 12PM | 73 | 59.1 | 50 | 55.6 | 26.23 | 0.0715 | 0.36 | 14.1 | 1
May | 12 | 12PM to 1PM | 73 | 58.2 | 48 | 51.6 | 25.6 | 0.0715 | 0.34 | 14.09 | 1
May | 12 | 1PM to 2PM | 75 | 59.3 | 48.9 | 53.4 | 26.36 | 0.0712 | 0.35 | 14.15 | 1
May | 12 | 2PM to 3PM | 75 | 58.5 | 46.9 | 49.6 | 25.76 | 0.0712 | 0.32 | 14.14 | 1
May | 12 | 3PM to 4PM | 75.9 | 60.2 | 50 | 55.6 | 26.93 | 0.0711 | 0.36 | 14.18 | 1
May | 12 | 4PM to 5PM | 75.9 | 59.7 | 48.9 | 53.4 | 26.58 | 0.0711 | 0.35 | 14.17 | 1
May | 12 | 5PM to 6PM | 73.9 | 59.5 | 50 | 55.6 | 26.45 | 0.0713 | 0.36 | 14.13 | 1
May | 12 | 6PM to 7PM | 72 | 58.2 | 48.9 | 53.4 | 25.62 | 0.0716 | 0.35 | 14.07 | 1
May | 12 | 7PM to 8PM | 69.1 | 56.2 | 46.9 | 49.6 | 24.31 | 0.072 | 0.32 | 13.98 | 1
May | 12 | 8PM to 9PM | 66 | 55.5 | 48 | 51.6 | 23.89 | 0.0724 | 0.34 | 13.9 | 1
May | 12 | 9PM to 10PM | 64 | 54.2 | 46.9 | 49.6 | 23.09 | 0.0727 | 0.32 | 13.85 | 1
May | 12 | 10PM to 11PM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
May | 12 | 11PM to 12AM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
May | 13 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 58 | 22.42 | 0.0738 | 0.38 | 13.66 | 1
May | 13 | 1AM to 2AM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
May | 13 | 2AM to 3AM | 55 | 51.6 | 48.9 | 53.4 | 21.5 | 0.074 | 0.35 | 13.62 | 1
May | 13 | 3AM to 4AM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
May | 13 | 4AM to 5AM | 55.9 | 49 | 43 | 42.5 | 20.03 | 0.0739 | 0.28 | 13.61 | 1
May | 13 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
May | 13 | 6AM to 7AM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
May | 13 | 7AM to 8AM | 63 | 53.8 | 46.9 | 49.6 | 22.82 | 0.0729 | 0.32 | 13.82 | 1
May | 13 | 8AM to 9AM | 68 | 57.8 | 51.1 | 58 | 25.36 | 0.0721 | 0.38 | 13.98 | 1
May | 13 | 9AM to 10AM | 72 | 56.5 | 45 | 45.9 | 24.45 | 0.0717 | 0.3 | 14.04 | 1
May | 13 | 10AM to 11AM | 73.9 | 56.8 | 44.1 | 44.4 | 24.68 | 0.0714 | 0.29 | 14.09 | 1
May | 13 | 11AM to 12PM | 75 | 56.8 | 43 | 42.5 | 24.66 | 0.0713 | 0.28 | 14.11 | 1
May | 13 | 12PM to 1PM | 77 | 56.4 | 39.9 | 37.8 | 24.39 | 0.071 | 0.25 | 14.15 | 1
May | 13 | 1PM to 2PM | 79 | 57.2 | 39.9 | 37.8 | 24.87 | 0.0708 | 0.25 | 14.2 | 1
May | 13 | 2PM to 3PM | 80.1 | 57.6 | 39.9 | 37.8 | 25.13 | 0.0706 | 0.25 | 14.23 | 1
May | 13 | 3PM to 4PM | 81 | 59.8 | 45 | 45.9 | 26.63 | 0.0705 | 0.3 | 14.28 | 1
May | 13 | 4PM to 5PM | 79 | 57.2 | 39.9 | 37.8 | 24.87 | 0.0708 | 0.25 | 14.2 | 1
May | 13 | 5PM to 6PM | 78.1 | 58 | 43 | 42.5 | 25.4 | 0.0709 | 0.28 | 14.19 | 1
May | 13 | 6PM to 7PM | 75 | 56.5 | 42.1 | 41.1 | 24.43 | 0.0713 | 0.27 | 14.11 | 1
May | 13 | 7PM to 8PM | 71.1 | 55.3 | 43 | 42.5 | 23.7 | 0.0718 | 0.28 | 14.01 | 1
May | 13 | 8PM to 9PM | 63 | 52 | 43 | 42.5 | 21.73 | 0.0729 | 0.28 | 13.8 | 1
May | 13 | 9PM to 10PM | 60.1 | 51.7 | 45 | 45.9 | 21.56 | 0.0733 | 0.3 | 13.73 | 1
May | 13 | 10PM to 11PM | 57.9 | 51.3 | 46 | 47.9 | 21.34 | 0.0736 | 0.31 | 13.68 | 1
May | 13 | 11PM to 12AM | 57.9 | 51.7 | 46.9 | 49.6 | 21.6 | 0.0736 | 0.32 | 13.68 | 1
May | 14 | 12AM to 1AM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
May | 14 | 1AM to 2AM | 57.9 | 52.3 | 48 | 51.6 | 21.92 | 0.0736 | 0.34 | 13.69 | 1
May | 14 | 2AM to 3AM | 55 | 51.6 | 48.9 | 53.4 | 21.5 | 0.074 | 0.35 | 13.62 | 1
May | 14 | 3AM to 4AM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
May | 14 | 4AM to 5AM | 55 | 51.6 | 48.9 | 53.4 | 21.5 | 0.074 | 0.35 | 13.62 | 1
May | 14 | 5AM to 6AM | 53.1 | 50.7 | 48.9 | 53.4 | 21.02 | 0.0743 | 0.35 | 13.57 | 1
May | 14 | 6AM to 7AM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
May | 14 | 7AM to 8AM | 60.1 | 54.2 | 50 | 55.6 | 23.07 | 0.0733 | 0.36 | 13.76 | 1
May | 14 | 8AM to 9AM | 66 | 57.5 | 52 | 59.9 | 25.19 | 0.0724 | 0.39 | 13.93 | 1
May | 14 | 9AM to 10AM | 71.1 | 59.9 | 53.1 | 62.4 | 26.8 | 0.0717 | 0.41 | 14.07 | 1
May | 14 | 10AM to 11AM | 75 | 60.4 | 51.1 | 58 | 27.07 | 0.0712 | 0.38 | 14.16 | 1
May | 14 | 11AM to 12PM | 75.9 | 58.8 | 46.9 | 49.6 | 25.97 | 0.0711 | 0.32 | 14.16 | 1
May | 14 | 12PM to 1PM | 75 | 59.8 | 50 | 55.6 | 26.71 | 0.0712 | 0.36 | 14.16 | 1
May | 14 | 1PM to 2PM | 77 | 61.5 | 52 | 59.9 | 27.86 | 0.0709 | 0.39 | 14.22 | 1
May | 14 | 2PM to 3PM | 78.1 | 60 | 48 | 51.6 | 26.82 | 0.0708 | 0.34 | 14.22 | 1
May | 14 | 3PM to 4PM | 78.1 | 60 | 48 | 51.6 | 26.82 | 0.0708 | 0.34 | 14.22 | 1
May | 14 | 4PM to 5PM | 78.1 | 60.9 | 50 | 55.6 | 27.45 | 0.0708 | 0.36 | 14.24 | 1
May | 14 | 5PM to 6PM | 78.1 | 58.7 | 45 | 45.9 | 25.93 | 0.0709 | 0.3 | 14.21 | 1
May | 14 | 6PM to 7PM | 73 | 56.9 | 45 | 45.9 | 24.71 | 0.0715 | 0.3 | 14.07 | 1
May | 14 | 7PM to 8PM | 69.1 | 55.3 | 45 | 45.9 | 23.75 | 0.0721 | 0.3 | 13.97 | 1
May | 14 | 8PM to 9PM | 66 | 55 | 46.9 | 49.6 | 23.57 | 0.0725 | 0.32 | 13.9 | 1
May | 14 | 9PM to 10PM | 63 | 54.3 | 48 | 51.6 | 23.15 | 0.0729 | 0.34 | 13.82 | 1
May | 14 | 10PM to 11PM | 60.1 | 53.6 | 48.9 | 53.4 | 22.72 | 0.0733 | 0.35 | 13.75 | 1
May | 14 | 11PM to 12AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
May | 15 | 12AM to 1AM | 57 | 53 | 50 | 55.6 | 22.32 | 0.0737 | 0.36 | 13.68 | 1
May | 15 | 1AM to 2AM | 55.9 | 52.5 | 50 | 55.6 | 22.06 | 0.0738 | 0.36 | 13.65 | 1
May | 15 | 2AM to 3AM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
May | 15 | 3AM to 4AM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
May | 15 | 4AM to 5AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
May | 15 | 5AM to 6AM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
May | 15 | 6AM to 7AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
May | 15 | 7AM to 8AM | 61 | 55.6 | 52 | 59.9 | 23.96 | 0.0731 | 0.39 | 13.8 | 1
May | 15 | 8AM to 9AM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
May | 15 | 9AM to 10AM | 75 | 61.3 | 53.1 | 62.4 | 27.77 | 0.0712 | 0.41 | 14.18 | 1
May | 15 | 10AM to 11AM | 78.1 | 62.4 | 53.1 | 62.4 | 28.51 | 0.0708 | 0.41 | 14.26 | 1
May | 15 | 11AM to 12PM | 80.1 | 63 | 53.1 | 62.4 | 29 | 0.0705 | 0.41 | 14.31 | 1
May | 15 | 12PM to 1PM | 82 | 63.7 | 53.1 | 62.4 | 29.48 | 0.0702 | 0.41 | 14.36 | 1
May | 15 | 1PM to 2PM | 82.9 | 63.1 | 51.1 | 58 | 29 | 0.0702 | 0.38 | 14.37 | 1
May | 15 | 2PM to 3PM | 82.9 | 63.1 | 51.1 | 58 | 29 | 0.0702 | 0.38 | 14.37 | 1
May | 15 | 3PM to 4PM | 84 | 63 | 50 | 55.6 | 28.9 | 0.07 | 0.36 | 14.39 | 1
May | 15 | 4PM to 5PM | 84 | 62.1 | 48 | 51.6 | 28.27 | 0.07 | 0.34 | 14.38 | 1
May | 15 | 5PM to 6PM | 82 | 61.8 | 48.9 | 53.4 | 28.07 | 0.0703 | 0.35 | 14.33 | 1
May | 15 | 6PM to 7PM | 81 | 60.6 | 46.9 | 49.6 | 27.2 | 0.0705 | 0.32 | 14.29 | 1
May | 15 | 7PM to 8PM | 75.9 | 59.7 | 48.9 | 53.4 | 26.58 | 0.0711 | 0.35 | 14.17 | 1
May | 15 | 8PM to 9PM | 73 | 59.1 | 50 | 55.6 | 26.23 | 0.0715 | 0.36 | 14.1 | 1
May | 15 | 9PM to 10PM | 72 | 59.3 | 51.1 | 58 | 26.32 | 0.0716 | 0.38 | 14.08 | 1
May | 15 | 10PM to 11PM | 71.1 | 59.9 | 53.1 | 62.4 | 26.8 | 0.0717 | 0.41 | 14.07 | 1
May | 15 | 11PM to 12AM | 68 | 58.8 | 53.1 | 62.4 | 26.05 | 0.0721 | 0.41 | 13.99 | 1
May | 16 | 12AM to 1AM | 62.1 | 56.6 | 53.1 | 62.4 | 24.6 | 0.0729 | 0.41 | 13.83 | 1
May | 16 | 1AM to 2AM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
May | 16 | 2AM to 3AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
May | 16 | 3AM to 4AM | 63 | 57.5 | 54 | 64.5 | 25.15 | 0.0728 | 0.42 | 13.86 | 1
May | 16 | 4AM to 5AM | 61 | 56.7 | 54 | 64.5 | 24.67 | 0.0731 | 0.42 | 13.81 | 1
May | 16 | 5AM to 6AM | 60.1 | 55.3 | 52 | 59.9 | 23.74 | 0.0732 | 0.39 | 13.77 | 1
May | 16 | 6AM to 7AM | 63 | 56.4 | 52 | 59.9 | 24.44 | 0.0728 | 0.39 | 13.85 | 1
May | 16 | 7AM to 8AM | 68 | 62.2 | 59 | 77.7 | 28.43 | 0.072 | 0.5 | 14.04 | 1
May | 16 | 8AM to 9AM | 71.1 | 60.4 | 54 | 64.5 | 27.13 | 0.0717 | 0.42 | 14.08 | 1
May | 16 | 9AM to 10AM | 75 | 62.8 | 55.9 | 69.4 | 28.86 | 0.0711 | 0.45 | 14.2 | 1
May | 16 | 10AM to 11AM | 79 | 64.7 | 57 | 72.3 | 30.27 | 0.0706 | 0.47 | 14.31 | 1
May | 16 | 11AM to 12PM | 82 | 64.1 | 54 | 64.5 | 29.81 | 0.0702 | 0.42 | 14.37 | 1
May | 16 | 12PM to 1PM | 82.9 | 64.4 | 54 | 64.5 | 30.03 | 0.0701 | 0.42 | 14.39 | 1
May | 16 | 1PM to 2PM | 82.9 | 63.5 | 52 | 59.9 | 29.31 | 0.0701 | 0.39 | 14.38 | 1
May | 16 | 2PM to 3PM | 84.9 | 64.6 | 53.1 | 62.4 | 30.18 | 0.0699 | 0.41 | 14.44 | 1
May | 16 | 3PM to 4PM | 84.9 | 63.3 | 50 | 55.6 | 29.12 | 0.0699 | 0.36 | 14.42 | 1
May | 16 | 4PM to 5PM | 84 | 63.4 | 51.1 | 58 | 29.26 | 0.07 | 0.38 | 14.4 | 1
May | 16 | 5PM to 6PM | 82.9 | 62.6 | 50 | 55.6 | 28.64 | 0.0702 | 0.36 | 14.37 | 1
May | 16 | 6PM to 7PM | 82 | 62.8 | 51.1 | 58 | 28.78 | 0.0703 | 0.38 | 14.35 | 1
May | 16 | 7PM to 8PM | 75.9 | 61.6 | 53.1 | 62.4 | 27.99 | 0.071 | 0.41 | 14.2 | 1
May | 16 | 8PM to 9PM | 73.9 | 61.4 | 54 | 64.5 | 27.83 | 0.0713 | 0.42 | 14.16 | 1
May | 16 | 9PM to 10PM | 73.9 | 61.4 | 54 | 64.5 | 27.83 | 0.0713 | 0.42 | 14.16 | 1
May | 16 | 10PM to 11PM | 71.1 | 60.4 | 54 | 64.5 | 27.13 | 0.0717 | 0.42 | 14.08 | 1
May | 16 | 11PM to 12AM | 68 | 59.3 | 54 | 64.5 | 26.38 | 0.0721 | 0.42 | 14 | 1
May | 17 | 12AM to 1AM | 66 | 58.1 | 53.1 | 62.4 | 25.57 | 0.0724 | 0.41 | 13.94 | 1
May | 17 | 1AM to 2AM | 66 | 57.1 | 51.1 | 58 | 24.88 | 0.0724 | 0.38 | 13.92 | 1
May | 17 | 2AM to 3AM | 62.1 | 55.5 | 51.1 | 58 | 23.91 | 0.073 | 0.38 | 13.82 | 1
May | 17 | 3AM to 4AM | 61 | 55.1 | 51.1 | 58 | 23.65 | 0.0731 | 0.38 | 13.79 | 1
May | 17 | 4AM to 5AM | 62.1 | 55.5 | 51.1 | 58 | 23.91 | 0.073 | 0.38 | 13.82 | 1
May | 17 | 5AM to 6AM | 62.1 | 55.5 | 51.1 | 58 | 23.91 | 0.073 | 0.38 | 13.82 | 1
May | 17 | 6AM to 7AM | 63 | 56.4 | 52 | 59.9 | 24.44 | 0.0728 | 0.39 | 13.85 | 1
May | 17 | 7AM to 8AM | 66.9 | 58.4 | 53.1 | 62.4 | 25.79 | 0.0723 | 0.41 | 13.96 | 1
May | 17 | 8AM to 9AM | 72 | 61.8 | 55.9 | 69.4 | 28.12 | 0.0715 | 0.45 | 14.12 | 1
May | 17 | 9AM to 10AM | 75.9 | 63.1 | 55.9 | 69.4 | 29.08 | 0.071 | 0.45 | 14.22 | 1
May | 17 | 10AM to 11AM | 79 | 64.7 | 57 | 72.3 | 30.27 | 0.0706 | 0.47 | 14.31 | 1
May | 17 | 11AM to 12PM | 81 | 65.3 | 57 | 72.3 | 30.76 | 0.0703 | 0.47 | 14.37 | 1
May | 17 | 12PM to 1PM | 82.9 | 65 | 55 | 67.2 | 30.44 | 0.0701 | 0.44 | 14.4 | 1
May | 17 | 1PM to 2PM | 82 | 64.1 | 54 | 64.5 | 29.81 | 0.0702 | 0.42 | 14.37 | 1
May | 17 | 2PM to 3PM | 84 | 64.3 | 53.1 | 62.4 | 29.96 | 0.07 | 0.41 | 14.42 | 1
May | 17 | 3PM to 4PM | 82.9 | 64 | 53.1 | 62.4 | 29.7 | 0.0701 | 0.41 | 14.39 | 1
May | 17 | 4PM to 5PM | 84 | 64.8 | 54 | 64.5 | 30.29 | 0.07 | 0.42 | 14.42 | 1
May | 17 | 5PM to 6PM | 82.9 | 63.5 | 52 | 59.9 | 29.31 | 0.0701 | 0.39 | 14.38 | 1
May | 17 | 6PM to 7PM | 80.1 | 62.5 | 52 | 59.9 | 28.61 | 0.0705 | 0.39 | 14.3 | 1
May | 17 | 7PM to 8PM | 77 | 62.5 | 54 | 64.5 | 28.58 | 0.0709 | 0.42 | 14.24 | 1
May | 17 | 8PM to 9PM | 77 | 63 | 55 | 67.2 | 28.99 | 0.0709 | 0.44 | 14.25 | 1
May | 17 | 9PM to 10PM | 71.1 | 61 | 55 | 67.2 | 27.54 | 0.0717 | 0.44 | 14.09 | 1
May | 17 | 10PM to 11PM | 69.1 | 59.7 | 54 | 64.5 | 26.65 | 0.072 | 0.42 | 14.03 | 1
May | 17 | 11PM to 12AM | 69.1 | 59.7 | 54 | 64.5 | 26.65 | 0.072 | 0.42 | 14.03 | 1
May | 18 | 12AM to 1AM | 64.9 | 57.7 | 53.1 | 62.4 | 25.31 | 0.0725 | 0.41 | 13.91 | 1
May | 18 | 1AM to 2AM | 64.9 | 57.7 | 53.1 | 62.4 | 25.31 | 0.0725 | 0.41 | 13.91 | 1
May | 18 | 2AM to 3AM | 64 | 57.9 | 54 | 64.5 | 25.42 | 0.0726 | 0.42 | 13.89 | 1
May | 18 | 3AM to 4AM | 62.1 | 57.1 | 54 | 64.5 | 24.93 | 0.0729 | 0.42 | 13.84 | 1
May | 18 | 4AM to 5AM | 62.1 | 57.1 | 54 | 64.5 | 24.93 | 0.0729 | 0.42 | 13.84 | 1
May | 18 | 5AM to 6AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
May | 18 | 6AM to 7AM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
May | 18 | 7AM to 8AM | 72 | 61.8 | 55.9 | 69.4 | 28.12 | 0.0715 | 0.45 | 14.12 | 1
May | 18 | 8AM to 9AM | 75.9 | 64.2 | 57.9 | 74.7 | 29.9 | 0.071 | 0.48 | 14.24 | 1
May | 18 | 9AM to 10AM | 78.1 | 63.8 | 55.9 | 69.4 | 29.61 | 0.0707 | 0.45 | 14.28 | 1
May | 18 | 10AM to 11AM | 81 | 65.3 | 57 | 72.3 | 30.76 | 0.0703 | 0.47 | 14.37 | 1
May | 18 | 11AM to 12PM | 84 | 65.8 | 55.9 | 69.4 | 31.06 | 0.0699 | 0.45 | 14.44 | 1
May | 18 | 12PM to 1PM | 84 | 65.3 | 55 | 67.2 | 30.71 | 0.07 | 0.44 | 14.43 | 1
May | 18 | 1PM to 2PM | 82.9 | 64.4 | 54 | 64.5 | 30.03 | 0.0701 | 0.42 | 14.39 | 1
May | 18 | 2PM to 3PM | 84.9 | 64.1 | 52 | 59.9 | 29.79 | 0.0699 | 0.39 | 14.43 | 1
May | 18 | 3PM to 4PM | 84.9 | 65.1 | 54 | 64.5 | 30.51 | 0.0699 | 0.42 | 14.45 | 1
May | 18 | 4PM to 5PM | 84.9 | 64.6 | 53.1 | 62.4 | 30.18 | 0.0699 | 0.41 | 14.44 | 1
May | 18 | 5PM to 6PM | 84 | 64.3 | 53.1 | 62.4 | 29.96 | 0.07 | 0.41 | 14.42 | 1
May | 18 | 6PM to 7PM | 82 | 64.1 | 54 | 64.5 | 29.81 | 0.0702 | 0.42 | 14.37 | 1
May | 18 | 7PM to 8PM | 79 | 63.7 | 55 | 67.2 | 29.48 | 0.0706 | 0.44 | 14.3 | 1
May | 18 | 8PM to 9PM | 73 | 62.1 | 55.9 | 69.4 | 28.38 | 0.0714 | 0.45 | 14.15 | 1
May | 18 | 9PM to 10PM | 71.1 | 61.5 | 55.9 | 69.4 | 27.9 | 0.0717 | 0.45 | 14.09 | 1
May | 18 | 10PM to 11PM | 72 | 61.8 | 55.9 | 69.4 | 28.12 | 0.0715 | 0.45 | 14.12 | 1
May | 18 | 11PM to 12AM | 70 | 61.1 | 55.9 | 69.4 | 27.63 | 0.0718 | 0.45 | 14.07 | 1
May | 19 | 12AM to 1AM | 68 | 61.5 | 57.9 | 74.7 | 27.96 | 0.072 | 0.48 | 14.03 | 1
May | 19 | 1AM to 2AM | 66 | 60.8 | 57.9 | 74.7 | 27.48 | 0.0723 | 0.48 | 13.98 | 1
May | 19 | 2AM to 3AM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
May | 19 | 3AM to 4AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
May | 19 | 4AM to 5AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
May | 19 | 5AM to 6AM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
May | 19 | 6AM to 7AM | 66 | 60.8 | 57.9 | 74.7 | 27.48 | 0.0723 | 0.48 | 13.98 | 1
May | 19 | 7AM to 8AM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
May | 19 | 8AM to 9AM | 75.9 | 64.2 | 57.9 | 74.7 | 29.9 | 0.071 | 0.48 | 14.24 | 1
May | 19 | 9AM to 10AM | 78.1 | 64.9 | 57.9 | 74.7 | 30.43 | 0.0707 | 0.48 | 14.3 | 1
May | 19 | 10AM to 11AM | 82 | 66.7 | 59 | 77.7 | 31.87 | 0.0702 | 0.5 | 14.41 | 1
May | 19 | 11AM to 12PM | 84 | 66.3 | 57 | 72.3 | 31.51 | 0.0699 | 0.47 | 14.45 | 1
May | 19 | 12PM to 1PM | 86 | 65.4 | 54 | 64.5 | 30.78 | 0.0697 | 0.42 | 14.48 | 1
May | 19 | 1PM to 2PM | 87.1 | 65.3 | 53.1 | 62.4 | 30.71 | 0.0696 | 0.41 | 14.5 | 1
May | 19 | 2PM to 3PM | 87.1 | 65.8 | 54 | 64.5 | 31.04 | 0.0696 | 0.42 | 14.5 | 1
May | 19 | 3PM to 4PM | 87.1 | 66.7 | 55.9 | 69.4 | 31.81 | 0.0696 | 0.45 | 14.52 | 1
May | 19 | 4PM to 5PM | 87.1 | 66.3 | 55 | 67.2 | 31.46 | 0.0696 | 0.44 | 14.51 | 1
May | 19 | 5PM to 6PM | 84.9 | 66 | 55.9 | 69.4 | 31.28 | 0.0698 | 0.45 | 14.46 | 1
May | 19 | 6PM to 7PM | 82.9 | 65 | 55 | 67.2 | 30.44 | 0.0701 | 0.44 | 14.4 | 1
May | 19 | 7PM to 8PM | 78.1 | 62.8 | 54 | 64.5 | 28.84 | 0.0707 | 0.42 | 14.27 | 1
May | 19 | 8PM to 9PM | 75 | 61.3 | 53.1 | 62.4 | 27.77 | 0.0712 | 0.41 | 14.18 | 1
May | 19 | 9PM to 10PM | 72 | 60.3 | 53.1 | 62.4 | 27.02 | 0.0716 | 0.41 | 14.1 | 1
May | 19 | 10PM to 11PM | 69.1 | 60.3 | 55 | 67.2 | 27.06 | 0.0719 | 0.44 | 14.03 | 1
May | 19 | 11PM to 12AM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
May | 20 | 12AM to 1AM | 66 | 59.7 | 55.9 | 69.4 | 26.66 | 0.0723 | 0.45 | 13.96 | 1
May | 20 | 1AM to 2AM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
May | 20 | 2AM to 3AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
May | 20 | 3AM to 4AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
May | 20 | 4AM to 5AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
May | 20 | 5AM to 6AM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
May | 20 | 6AM to 7AM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
May | 20 | 7AM to 8AM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
May | 20 | 8AM to 9AM | 75 | 63.9 | 57.9 | 74.7 | 29.68 | 0.0711 | 0.48 | 14.22 | 1
May | 20 | 9AM to 10AM | 79 | 65.8 | 59 | 77.7 | 31.12 | 0.0705 | 0.5 | 14.33 | 1
May | 20 | 10AM to 11AM | 82 | 66.2 | 57.9 | 74.7 | 31.4 | 0.0702 | 0.48 | 14.4 | 1
May | 20 | 11AM to 12PM | 84 | 67.3 | 59 | 77.7 | 32.36 | 0.0699 | 0.5 | 14.47 | 1
May | 20 | 12PM to 1PM | 86 | 66.9 | 57 | 72.3 | 31.99 | 0.0697 | 0.47 | 14.5 | 1
May | 20 | 1PM to 2PM | 86 | 65.9 | 55 | 67.2 | 31.19 | 0.0697 | 0.44 | 14.48 | 1
May | 20 | 2PM to 3PM | 84.9 | 65.6 | 55 | 67.2 | 30.93 | 0.0698 | 0.44 | 14.46 | 1
May | 20 | 3PM to 4PM | 80.1 | 66.1 | 59 | 77.7 | 31.39 | 0.0704 | 0.5 | 14.36 | 1
May | 20 | 4PM to 5PM | 79 | 63.1 | 54 | 64.5 | 29.06 | 0.0706 | 0.42 | 14.29 | 1
May | 20 | 5PM to 6PM | 78.1 | 64.4 | 57 | 72.3 | 30.05 | 0.0707 | 0.47 | 14.29 | 1
May | 20 | 6PM to 7PM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
May | 20 | 7PM to 8PM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
May | 20 | 8PM to 9PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
May | 20 | 9PM to 10PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
May | 20 | 10PM to 11PM | 66 | 60.3 | 57 | 72.3 | 27.1 | 0.0723 | 0.47 | 13.97 | 1
May | 20 | 11PM to 12AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
May | 21 | 12AM to 1AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
May | 21 | 1AM to 2AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
May | 21 | 2AM to 3AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
May | 21 | 3AM to 4AM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
May | 21 | 4AM to 5AM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
May | 21 | 5AM to 6AM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
May | 21 | 6AM to 7AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
May | 21 | 7AM to 8AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
May | 21 | 8AM to 9AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
May | 21 | 9AM to 10AM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
May | 21 | 10AM to 11AM | 73.9 | 66.5 | 63 | 89.6 | 31.76 | 0.0711 | 0.58 | 14.24 | 1
May | 21 | 11AM to 12PM | 78.1 | 68.4 | 64 | 93.2 | 33.33 | 0.0706 | 0.6 | 14.36 | 1
May | 21 | 12PM to 1PM | 79 | 68.1 | 63 | 89.6 | 32.99 | 0.0705 | 0.58 | 14.37 | 1
May | 21 | 1PM to 2PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
May | 21 | 2PM to 3PM | 79 | 67.5 | 62.1 | 86.8 | 32.55 | 0.0705 | 0.56 | 14.36 | 1
May | 21 | 3PM to 4PM | 80.1 | 67.2 | 61 | 83.5 | 32.29 | 0.0704 | 0.54 | 14.38 | 1
May | 21 | 4PM to 5PM | 80.1 | 67.8 | 62.1 | 86.8 | 32.81 | 0.0704 | 0.56 | 14.39 | 1
May | 21 | 5PM to 6PM | 78.1 | 66.6 | 61 | 83.5 | 31.81 | 0.0706 | 0.54 | 14.33 | 1
May | 21 | 6PM to 7PM | 75 | 65.7 | 61 | 83.5 | 31.06 | 0.071 | 0.54 | 14.24 | 1
May | 21 | 7PM to 8PM | 72 | 65.3 | 62.1 | 86.8 | 30.82 | 0.0714 | 0.56 | 14.17 | 1
May | 21 | 8PM to 9PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
May | 21 | 9PM to 10PM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
May | 21 | 10PM to 11PM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
May | 21 | 11PM to 12AM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
May | 22 | 12AM to 1AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
May | 22 | 1AM to 2AM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 22 | 2AM to 3AM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
May | 22 | 3AM to 4AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 22 | 4AM to 5AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 22 | 5AM to 6AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 22 | 6AM to 7AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
May | 22 | 7AM to 8AM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
May | 22 | 8AM to 9AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
May | 22 | 9AM to 10AM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
May | 22 | 10AM to 11AM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
May | 22 | 11AM to 12PM | 77 | 66.9 | 62.1 | 86.8 | 32.06 | 0.0708 | 0.56 | 14.31 | 1
May | 22 | 12PM to 1PM | 79 | 66.9 | 61 | 83.5 | 32.03 | 0.0705 | 0.54 | 14.35 | 1
May | 22 | 1PM to 2PM | 80.1 | 67.2 | 61 | 83.5 | 32.29 | 0.0704 | 0.54 | 14.38 | 1
May | 22 | 2PM to 3PM | 81 | 66.4 | 59 | 77.7 | 31.61 | 0.0703 | 0.5 | 14.38 | 1
May | 22 | 3PM to 4PM | 81 | 64.8 | 55.9 | 69.4 | 30.32 | 0.0703 | 0.45 | 14.36 | 1
May | 22 | 4PM to 5PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
May | 22 | 5PM to 6PM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
May | 22 | 6PM to 7PM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
May | 22 | 7PM to 8PM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
May | 22 | 8PM to 9PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
May | 22 | 9PM to 10PM | 66 | 62.7 | 61 | 83.5 | 28.85 | 0.0723 | 0.54 | 14.01 | 1
May | 22 | 10PM to 11PM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
May | 22 | 11PM to 12AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
May | 23 | 12AM to 1AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 23 | 1AM to 2AM | 62.1 | 60.8 | 60.1 | 80.8 | 27.46 | 0.0728 | 0.52 | 13.89 | 1
May | 23 | 2AM to 3AM | 62.1 | 60.8 | 60.1 | 80.8 | 27.46 | 0.0728 | 0.52 | 13.89 | 1
May | 23 | 3AM to 4AM | 62.1 | 60.8 | 60.1 | 80.8 | 27.46 | 0.0728 | 0.52 | 13.89 | 1
May | 23 | 4AM to 5AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 23 | 5AM to 6AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 23 | 6AM to 7AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 23 | 7AM to 8AM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
May | 23 | 8AM to 9AM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 23 | 9AM to 10AM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 23 | 10AM to 11AM | 73.9 | 67.2 | 64 | 93.2 | 32.31 | 0.0711 | 0.6 | 14.25 | 1
May | 23 | 11AM to 12PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
May | 23 | 12PM to 1PM | 79 | 66.9 | 61 | 83.5 | 32.03 | 0.0705 | 0.54 | 14.35 | 1
May | 23 | 1PM to 2PM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
May | 23 | 2PM to 3PM | 81 | 68.1 | 62.1 | 86.8 | 33.03 | 0.0702 | 0.56 | 14.41 | 1
May | 23 | 3PM to 4PM | 80.1 | 67.8 | 62.1 | 86.8 | 32.81 | 0.0704 | 0.56 | 14.39 | 1
May | 23 | 4PM to 5PM | 81 | 67 | 60.1 | 80.8 | 32.09 | 0.0703 | 0.52 | 14.39 | 1
May | 23 | 5PM to 6PM | 77 | 64.1 | 57 | 72.3 | 29.79 | 0.0708 | 0.47 | 14.26 | 1
May | 23 | 6PM to 7PM | 75 | 62.8 | 55.9 | 69.4 | 28.86 | 0.0711 | 0.45 | 14.2 | 1
May | 23 | 7PM to 8PM | 71.1 | 61.5 | 55.9 | 69.4 | 27.9 | 0.0717 | 0.45 | 14.09 | 1
May | 23 | 8PM to 9PM | 71.1 | 61.5 | 55.9 | 69.4 | 27.9 | 0.0717 | 0.45 | 14.09 | 1
May | 23 | 9PM to 10PM | 69.1 | 62.5 | 59 | 77.7 | 28.7 | 0.0719 | 0.5 | 14.07 | 1
May | 23 | 10PM to 11PM | 68 | 61 | 57 | 72.3 | 27.59 | 0.0721 | 0.47 | 14.02 | 1
May | 23 | 11PM to 12AM | 68 | 61 | 57 | 72.3 | 27.59 | 0.0721 | 0.47 | 14.02 | 1
May | 24 | 12AM to 1AM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
May | 24 | 1AM to 2AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
May | 24 | 2AM to 3AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
May | 24 | 3AM to 4AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
May | 24 | 4AM to 5AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
May | 24 | 5AM to 6AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 24 | 6AM to 7AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
May | 24 | 7AM to 8AM | 66 | 61.5 | 59 | 77.7 | 27.95 | 0.0723 | 0.5 | 13.99 | 1
May | 24 | 8AM to 9AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
May | 24 | 9AM to 10AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 24 | 10AM to 11AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 24 | 11AM to 12PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 24 | 12PM to 1PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 24 | 1PM to 2PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 24 | 2PM to 3PM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
May | 24 | 3PM to 4PM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
May | 24 | 4PM to 5PM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
May | 24 | 5PM to 6PM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
May | 24 | 6PM to 7PM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
May | 24 | 7PM to 8PM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
May | 24 | 8PM to 9PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 24 | 9PM to 10PM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 24 | 10PM to 11PM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
May | 24 | 11PM to 12AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
May | 25 | 12AM to 1AM | 62.1 | 60.8 | 60.1 | 80.8 | 27.46 | 0.0728 | 0.52 | 13.89 | 1
May | 25 | 1AM to 2AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
May | 25 | 2AM to 3AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 25 | 3AM to 4AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
May | 25 | 4AM to 5AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
May | 25 | 5AM to 6AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
May | 25 | 6AM to 7AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 25 | 7AM to 8AM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
May | 25 | 8AM to 9AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 25 | 9AM to 10AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
May | 25 | 10AM to 11AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
May | 25 | 11AM to 12PM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
May | 25 | 12PM to 1PM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
May | 25 | 1PM to 2PM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
May | 25 | 2PM to 3PM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
May | 25 | 3PM to 4PM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 25 | 4PM to 5PM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 25 | 5PM to 6PM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 25 | 6PM to 7PM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
May | 25 | 7PM to 8PM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
May | 25 | 8PM to 9PM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
May | 25 | 9PM to 10PM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
May | 25 | 10PM to 11PM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
May | 25 | 11PM to 12AM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
May | 26 | 12AM to 1AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
May | 26 | 1AM to 2AM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
May | 26 | 2AM to 3AM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
May | 26 | 3AM to 4AM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
May | 26 | 4AM to 5AM | 66 | 65.3 | 64.9 | 96.2 | 30.83 | 0.0722 | 0.62 | 14.05 | 1
May | 26 | 5AM to 6AM | 66 | 65.3 | 64.9 | 96.2 | 30.83 | 0.0722 | 0.62 | 14.05 | 1
May | 26 | 6AM to 7AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
May | 26 | 7AM to 8AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
May | 26 | 8AM to 9AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
May | 26 | 9AM to 10AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
May | 26 | 10AM to 11AM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
May | 26 | 11AM to 12PM | 75 | 68.1 | 64.9 | 96.2 | 33.05 | 0.071 | 0.62 | 14.29 | 1
May | 26 | 12PM to 1PM | 77 | 68.7 | 64.9 | 96.2 | 33.54 | 0.0707 | 0.62 | 14.34 | 1
May | 26 | 1PM to 2PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
May | 26 | 2PM to 3PM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
May | 26 | 3PM to 4PM | 82.9 | 69.9 | 64 | 93.2 | 34.52 | 0.0699 | 0.6 | 14.49 | 1
May | 26 | 4PM to 5PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
May | 26 | 5PM to 6PM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
May | 26 | 6PM to 7PM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
May | 26 | 7PM to 8PM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
May | 26 | 8PM to 9PM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
May | 26 | 9PM to 10PM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
May | 26 | 10PM to 11PM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
May | 26 | 11PM to 12AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
May | 27 | 12AM to 1AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
May | 27 | 1AM to 2AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
May | 27 | 2AM to 3AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
May | 27 | 3AM to 4AM | 64 | 64 | 64 | 93.2 | 29.87 | 0.0725 | 0.6 | 13.98 | 1
May | 27 | 4AM to 5AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
May | 27 | 5AM to 6AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
May | 27 | 6AM to 7AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
May | 27 | 7AM to 8AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
May | 27 | 8AM to 9AM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
May | 27 | 9AM to 10AM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
May | 27 | 10AM to 11AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
May | 27 | 11AM to 12PM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
May | 27 | 12PM to 1PM | 73.9 | 67.2 | 64 | 93.2 | 32.31 | 0.0711 | 0.6 | 14.25 | 1
May | 27 | 1PM to 2PM | 75.9 | 67.1 | 63 | 89.6 | 32.24 | 0.0709 | 0.58 | 14.29 | 1
May | 27 | 2PM to 3PM | 77 | 66.9 | 62.1 | 86.8 | 32.06 | 0.0708 | 0.56 | 14.31 | 1
May | 27 | 3PM to 4PM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
May | 27 | 4PM to 5PM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
May | 27 | 5PM to 6PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
May | 27 | 6PM to 7PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
May | 27 | 7PM to 8PM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
May | 27 | 8PM to 9PM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 27 | 9PM to 10PM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
May | 27 | 10PM to 11PM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
May | 27 | 11PM to 12AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 28 | 12AM to 1AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
May | 28 | 1AM to 2AM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
May | 28 | 2AM to 3AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 28 | 3AM to 4AM | 63 | 61.7 | 61 | 83.5 | 28.1 | 0.0727 | 0.54 | 13.92 | 1
May | 28 | 4AM to 5AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 28 | 5AM to 6AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
May | 28 | 6AM to 7AM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
May | 28 | 7AM to 8AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
May | 28 | 8AM to 9AM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
May | 28 | 9AM to 10AM | 73.9 | 67.8 | 64.9 | 96.2 | 32.78 | 0.0711 | 0.62 | 14.26 | 1
May | 28 | 10AM to 11AM | 77 | 68.7 | 64.9 | 96.2 | 33.54 | 0.0707 | 0.62 | 14.34 | 1
May | 28 | 11AM to 12PM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
May | 28 | 12PM to 1PM | 80.1 | 67.8 | 62.1 | 86.8 | 32.81 | 0.0704 | 0.56 | 14.39 | 1
May | 28 | 1PM to 2PM | 79 | 67.5 | 62.1 | 86.8 | 32.55 | 0.0705 | 0.56 | 14.36 | 1
May | 28 | 2PM to 3PM | 80.1 | 67.8 | 62.1 | 86.8 | 32.81 | 0.0704 | 0.56 | 14.39 | 1
May | 28 | 3PM to 4PM | 81 | 67 | 60.1 | 80.8 | 32.09 | 0.0703 | 0.52 | 14.39 | 1
May | 28 | 4PM to 5PM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
May | 28 | 5PM to 6PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
May | 28 | 6PM to 7PM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
May | 28 | 7PM to 8PM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
May | 28 | 8PM to 9PM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
May | 28 | 9PM to 10PM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
May | 28 | 10PM to 11PM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
May | 28 | 11PM to 12AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
May | 29 | 12AM to 1AM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
May | 29 | 1AM to 2AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 29 | 2AM to 3AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 29 | 3AM to 4AM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
May | 29 | 4AM to 5AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
May | 29 | 5AM to 6AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
May | 29 | 6AM to 7AM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
May | 29 | 7AM to 8AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
May | 29 | 8AM to 9AM | 71.1 | 66.3 | 64 | 93.2 | 31.6 | 0.0715 | 0.6 | 14.17 | 1
May | 29 | 9AM to 10AM | 77 | 68.1 | 64 | 93.2 | 33.06 | 0.0707 | 0.6 | 14.33 | 1
May | 29 | 10AM to 11AM | 80.1 | 68.4 | 63 | 89.6 | 33.26 | 0.0703 | 0.58 | 14.4 | 1
May | 29 | 11AM to 12PM | 82 | 68.4 | 62.1 | 86.8 | 33.3 | 0.0701 | 0.56 | 14.44 | 1
May | 29 | 12PM to 1PM | 84 | 69 | 62.1 | 86.8 | 33.78 | 0.0698 | 0.56 | 14.5 | 1
May | 29 | 1PM to 2PM | 82.9 | 68.7 | 62.1 | 86.8 | 33.52 | 0.07 | 0.56 | 14.47 | 1
May | 29 | 2PM to 3PM | 84.9 | 69.3 | 62.1 | 86.8 | 34.01 | 0.0697 | 0.56 | 14.52 | 1
May | 29 | 3PM to 4PM | 86 | 69 | 61 | 83.5 | 33.75 | 0.0696 | 0.54 | 14.54 | 1
May | 29 | 4PM to 5PM | 86 | 69 | 61 | 83.5 | 33.75 | 0.0696 | 0.54 | 14.54 | 1
May | 29 | 5PM to 6PM | 84.9 | 68.2 | 60.1 | 80.8 | 33.06 | 0.0698 | 0.52 | 14.5 | 1
May | 29 | 6PM to 7PM | 82 | 67.8 | 61 | 83.5 | 32.78 | 0.0701 | 0.54 | 14.43 | 1
May | 29 | 7PM to 8PM | 81 | 67.5 | 61 | 83.5 | 32.51 | 0.0703 | 0.54 | 14.4 | 1
May | 29 | 8PM to 9PM | 73.9 | 66.5 | 63 | 89.6 | 31.76 | 0.0711 | 0.58 | 14.24 | 1
May | 29 | 9PM to 10PM | 73 | 66.2 | 63 | 89.6 | 31.53 | 0.0713 | 0.58 | 14.21 | 1
May | 29 | 10PM to 11PM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
May | 29 | 11PM to 12AM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
May | 30 | 12AM to 1AM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
May | 30 | 1AM to 2AM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
May | 30 | 2AM to 3AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
May | 30 | 3AM to 4AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
May | 30 | 4AM to 5AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
May | 30 | 5AM to 6AM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
May | 30 | 6AM to 7AM | 71.1 | 66.3 | 64 | 93.2 | 31.6 | 0.0715 | 0.6 | 14.17 | 1
May | 30 | 7AM to 8AM | 75 | 66.3 | 62.1 | 86.8 | 31.58 | 0.071 | 0.56 | 14.26 | 1
May | 30 | 8AM to 9AM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
May | 30 | 9AM to 10AM | 82 | 70.1 | 64.9 | 96.2 | 34.78 | 0.07 | 0.62 | 14.47 | 1
May | 30 | 10AM to 11AM | 84 | 70.2 | 64 | 93.2 | 34.79 | 0.0698 | 0.6 | 14.52 | 1
May | 30 | 11AM to 12PM | 84.9 | 70.4 | 64 | 93.2 | 35.01 | 0.0697 | 0.6 | 14.54 | 1
May | 30 | 12PM to 1PM | 84.9 | 69.3 | 62.1 | 86.8 | 34.01 | 0.0697 | 0.56 | 14.52 | 1
May | 30 | 1PM to 2PM | 87.1 | 69.9 | 62.1 | 86.8 | 34.54 | 0.0695 | 0.56 | 14.58 | 1
May | 30 | 2PM to 3PM | 87.1 | 70.4 | 63 | 89.6 | 34.98 | 0.0694 | 0.58 | 14.59 | 1
May | 30 | 3PM to 4PM | 82 | 70.8 | 66 | 100 | 35.37 | 0.07 | 0.64 | 14.49 | 1
May | 30 | 4PM to 5PM | 82.9 | 71.1 | 66 | 100 | 35.59 | 0.0699 | 0.64 | 14.51 | 1
May | 30 | 5PM to 6PM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
May | 30 | 6PM to 7PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
May | 30 | 7PM to 8PM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
May | 30 | 8PM to 9PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
May | 30 | 9PM to 10PM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
May | 30 | 10PM to 11PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
May | 30 | 11PM to 12AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
May | 31 | 12AM to 1AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
May | 31 | 1AM to 2AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
May | 31 | 2AM to 3AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
May | 31 | 3AM to 4AM | 68 | 66.6 | 66 | 100 | 31.91 | 0.0719 | 0.64 | 14.11 | 1
May | 31 | 4AM to 5AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
May | 31 | 5AM to 6AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
May | 31 | 6AM to 7AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
May | 31 | 7AM to 8AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
May | 31 | 8AM to 9AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
May | 31 | 9AM to 10AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
May | 31 | 10AM to 11AM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
May | 31 | 11AM to 12PM | 82 | 70.8 | 66 | 100 | 35.37 | 0.07 | 0.64 | 14.49 | 1
May | 31 | 12PM to 1PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
May | 31 | 1PM to 2PM | 84 | 71.4 | 66 | 100 | 35.86 | 0.0698 | 0.64 | 14.54 | 1
May | 31 | 2PM to 3PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
May | 31 | 3PM to 4PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
May | 31 | 4PM to 5PM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
May | 31 | 5PM to 6PM | 79 | 65.8 | 59 | 77.7 | 31.12 | 0.0705 | 0.5 | 14.33 | 1
May | 31 | 6PM to 7PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
May | 31 | 7PM to 8PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
May | 31 | 8PM to 9PM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
May | 31 | 9PM to 10PM | 71.2 | 65.5 | 62.8 | 89.1 | 31 | 0.0715 | 0.58 | 14.16 | 1
May | 31 | 10PM to 11PM | 70.5 | 65.3 | 62.8 | 89.1 | 30.83 | 0.0716 | 0.58 | 14.14 | 1
May | 31 | 11PM to 12AM | 69.8 | 65 | 62.6 | 88.5 | 30.56 | 0.0717 | 0.57 | 14.12 | 1
June | 1 | 12AM to 1AM | 69.1 | 64.6 | 62.4 | 87.9 | 30.29 | 0.0718 | 0.57 | 14.1 | 1
June | 1 | 1AM to 2AM | 68.4 | 64.3 | 62.2 | 87.3 | 30.03 | 0.0719 | 0.57 | 14.08 | 1
June | 1 | 2AM to 3AM | 67.6 | 64 | 62.2 | 87.3 | 29.85 | 0.072 | 0.57 | 14.06 | 1
June | 1 | 3AM to 4AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
June | 1 | 4AM to 5AM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
June | 1 | 5AM to 6AM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
June | 1 | 6AM to 7AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
June | 1 | 7AM to 8AM | 72 | 67.1 | 64.9 | 96.2 | 32.3 | 0.0714 | 0.62 | 14.2 | 1
June | 1 | 8AM to 9AM | 75 | 68.1 | 64.9 | 96.2 | 33.05 | 0.071 | 0.62 | 14.29 | 1
June | 1 | 9AM to 10AM | 78.1 | 69 | 64.9 | 96.2 | 33.8 | 0.0706 | 0.62 | 14.37 | 1
June | 1 | 10AM to 11AM | 80.1 | 67.2 | 61 | 83.5 | 32.29 | 0.0704 | 0.54 | 14.38 | 1
June | 1 | 11AM to 12PM | 82.9 | 67.6 | 60.1 | 80.8 | 32.58 | 0.07 | 0.52 | 14.45 | 1
June | 1 | 12PM to 1PM | 84.9 | 67.6 | 59 | 77.7 | 32.58 | 0.0698 | 0.5 | 14.49 | 1
June | 1 | 1PM to 2PM | 84.9 | 67 | 57.9 | 74.7 | 32.11 | 0.0698 | 0.48 | 14.48 | 1
June | 1 | 2PM to 3PM | 84.9 | 66 | 55.9 | 69.4 | 31.28 | 0.0698 | 0.45 | 14.46 | 1
June | 1 | 3PM to 4PM | 84.9 | 67.6 | 59 | 77.7 | 32.58 | 0.0698 | 0.5 | 14.49 | 1
June | 1 | 4PM to 5PM | 84.9 | 67.6 | 59 | 77.7 | 32.58 | 0.0698 | 0.5 | 14.49 | 1
June | 1 | 5PM to 6PM | 84 | 66.3 | 57 | 72.3 | 31.51 | 0.0699 | 0.47 | 14.45 | 1
June | 1 | 6PM to 7PM | 82 | 66.2 | 57.9 | 74.7 | 31.4 | 0.0702 | 0.48 | 14.4 | 1
June | 1 | 7PM to 8PM | 77 | 63 | 55 | 67.2 | 28.99 | 0.0709 | 0.44 | 14.25 | 1
June | 1 | 8PM to 9PM | 75 | 62.8 | 55.9 | 69.4 | 28.86 | 0.0711 | 0.45 | 14.2 | 1
June | 1 | 9PM to 10PM | 73 | 62.1 | 55.9 | 69.4 | 28.38 | 0.0714 | 0.45 | 14.15 | 1
June | 1 | 10PM to 11PM | 72 | 61.8 | 55.9 | 69.4 | 28.12 | 0.0715 | 0.45 | 14.12 | 1
June | 1 | 11PM to 12AM | 71.1 | 61.5 | 55.9 | 69.4 | 27.9 | 0.0717 | 0.45 | 14.09 | 1
June | 2 | 12AM to 1AM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
June | 2 | 1AM to 2AM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
June | 2 | 2AM to 3AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
June | 2 | 3AM to 4AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
June | 2 | 4AM to 5AM | 59 | 56.6 | 55 | 67.2 | 24.6 | 0.0733 | 0.44 | 13.77 | 1
June | 2 | 5AM to 6AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
June | 2 | 6AM to 7AM | 66 | 58.6 | 54 | 64.5 | 25.9 | 0.0724 | 0.42 | 13.95 | 1
June | 2 | 7AM to 8AM | 72 | 60.7 | 54 | 64.5 | 27.35 | 0.0716 | 0.42 | 14.1 | 1
June | 2 | 8AM to 9AM | 75 | 61.3 | 53.1 | 62.4 | 27.77 | 0.0712 | 0.41 | 14.18 | 1
June | 2 | 9AM to 10AM | 78.1 | 62.8 | 54 | 64.5 | 28.84 | 0.0707 | 0.42 | 14.27 | 1
June | 2 | 10AM to 11AM | 80.1 | 62.5 | 52 | 59.9 | 28.61 | 0.0705 | 0.39 | 14.3 | 1
June | 2 | 11AM to 12PM | 78.1 | 60.9 | 50 | 55.6 | 27.45 | 0.0708 | 0.36 | 14.24 | 1
June | 2 | 12PM to 1PM | 77 | 62 | 53.1 | 62.4 | 28.25 | 0.0709 | 0.41 | 14.23 | 1
June | 2 | 1PM to 2PM | 82 | 63.2 | 52 | 59.9 | 29.09 | 0.0703 | 0.39 | 14.36 | 1
June | 2 | 2PM to 3PM | 81 | 62.8 | 52 | 59.9 | 28.83 | 0.0704 | 0.39 | 14.33 | 1
June | 2 | 3PM to 4PM | 81 | 63.3 | 53.1 | 62.4 | 29.21 | 0.0704 | 0.41 | 14.33 | 1
June | 2 | 4PM to 5PM | 82 | 63.7 | 53.1 | 62.4 | 29.48 | 0.0702 | 0.41 | 14.36 | 1
June | 2 | 5PM to 6PM | 80.1 | 63 | 53.1 | 62.4 | 29 | 0.0705 | 0.41 | 14.31 | 1
June | 2 | 6PM to 7PM | 79 | 62.7 | 53.1 | 62.4 | 28.73 | 0.0706 | 0.41 | 14.28 | 1
June | 2 | 7PM to 8PM | 73.9 | 60.4 | 52 | 59.9 | 27.12 | 0.0713 | 0.39 | 14.14 | 1
June | 2 | 8PM to 9PM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
June | 2 | 9PM to 10PM | 68 | 59.3 | 54 | 64.5 | 26.38 | 0.0721 | 0.42 | 14 | 1
June | 2 | 10PM to 11PM | 70 | 60.6 | 55 | 67.2 | 27.28 | 0.0718 | 0.44 | 14.06 | 1
June | 2 | 11PM to 12AM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
June | 3 | 12AM to 1AM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
June | 3 | 1AM to 2AM | 66.9 | 59.5 | 55 | 67.2 | 26.53 | 0.0722 | 0.44 | 13.98 | 1
June | 3 | 2AM to 3AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
June | 3 | 3AM to 4AM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
June | 3 | 4AM to 5AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
June | 3 | 5AM to 6AM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
June | 3 | 6AM to 7AM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
June | 3 | 7AM to 8AM | 75 | 63.4 | 57 | 72.3 | 29.3 | 0.0711 | 0.47 | 14.21 | 1
June | 3 | 8AM to 9AM | 78.1 | 64.4 | 57 | 72.3 | 30.05 | 0.0707 | 0.47 | 14.29 | 1
June | 3 | 9AM to 10AM | 81 | 64.8 | 55.9 | 69.4 | 30.32 | 0.0703 | 0.45 | 14.36 | 1
June | 3 | 10AM to 11AM | 81 | 64.8 | 55.9 | 69.4 | 30.32 | 0.0703 | 0.45 | 14.36 | 1
June | 3 | 11AM to 12PM | 82.9 | 64 | 53.1 | 62.4 | 29.7 | 0.0701 | 0.41 | 14.39 | 1
June | 3 | 12PM to 1PM | 84 | 65.8 | 55.9 | 69.4 | 31.06 | 0.0699 | 0.45 | 14.44 | 1
June | 3 | 1PM to 2PM | 84.9 | 65.6 | 55 | 67.2 | 30.93 | 0.0698 | 0.44 | 14.46 | 1
June | 3 | 2PM to 3PM | 86 | 65.9 | 55 | 67.2 | 31.19 | 0.0697 | 0.44 | 14.48 | 1
June | 3 | 3PM to 4PM | 86 | 65.4 | 54 | 64.5 | 30.78 | 0.0697 | 0.42 | 14.48 | 1
June | 3 | 4PM to 5PM | 84.9 | 65.1 | 54 | 64.5 | 30.51 | 0.0699 | 0.42 | 14.45 | 1
June | 3 | 5PM to 6PM | 84.9 | 65.1 | 54 | 64.5 | 30.51 | 0.0699 | 0.42 | 14.45 | 1
June | 3 | 6PM to 7PM | 82 | 63.7 | 53.1 | 62.4 | 29.48 | 0.0702 | 0.41 | 14.36 | 1
June | 3 | 7PM to 8PM | 77 | 62 | 53.1 | 62.4 | 28.25 | 0.0709 | 0.41 | 14.23 | 1
June | 3 | 8PM to 9PM | 73.9 | 61.4 | 54 | 64.5 | 27.83 | 0.0713 | 0.42 | 14.16 | 1
June | 3 | 9PM to 10PM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
June | 3 | 10PM to 11PM | 72 | 60.3 | 53.1 | 62.4 | 27.02 | 0.0716 | 0.41 | 14.1 | 1
June | 3 | 11PM to 12AM | 72 | 60.7 | 54 | 64.5 | 27.35 | 0.0716 | 0.42 | 14.1 | 1
June | 4 | 12AM to 1AM | 70 | 59.5 | 53.1 | 62.4 | 26.54 | 0.0718 | 0.41 | 14.04 | 1
June | 4 | 1AM to 2AM | 70 | 59.5 | 53.1 | 62.4 | 26.54 | 0.0718 | 0.41 | 14.04 | 1
June | 4 | 2AM to 3AM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
June | 4 | 3AM to 4AM | 68 | 58.8 | 53.1 | 62.4 | 26.05 | 0.0721 | 0.41 | 13.99 | 1
June | 4 | 4AM to 5AM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
June | 4 | 5AM to 6AM | 69.1 | 59.7 | 54 | 64.5 | 26.65 | 0.072 | 0.42 | 14.03 | 1
June | 4 | 6AM to 7AM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
June | 4 | 7AM to 8AM | 72 | 62.4 | 57 | 72.3 | 28.56 | 0.0715 | 0.47 | 14.13 | 1
June | 4 | 8AM to 9AM | 75.9 | 64.8 | 59 | 77.7 | 30.37 | 0.071 | 0.5 | 14.25 | 1
June | 4 | 9AM to 10AM | 80.1 | 66.7 | 60.1 | 80.8 | 31.87 | 0.0704 | 0.52 | 14.37 | 1
June | 4 | 10AM to 11AM | 84.9 | 68.2 | 60.1 | 80.8 | 33.06 | 0.0698 | 0.52 | 14.5 | 1
June | 4 | 11AM to 12PM | 84.9 | 66.6 | 57 | 72.3 | 31.73 | 0.0698 | 0.47 | 14.47 | 1
June | 4 | 12PM to 1PM | 87.1 | 66.7 | 55.9 | 69.4 | 31.81 | 0.0696 | 0.45 | 14.52 | 1
June | 4 | 1PM to 2PM | 87.1 | 66.7 | 55.9 | 69.4 | 31.81 | 0.0696 | 0.45 | 14.52 | 1
June | 4 | 2PM to 3PM | 88 | 66.6 | 55 | 67.2 | 31.68 | 0.0695 | 0.44 | 14.54 | 1
June | 4 | 3PM to 4PM | 88 | 66.6 | 55 | 67.2 | 31.68 | 0.0695 | 0.44 | 14.54 | 1
June | 4 | 4PM to 5PM | 89.1 | 67.3 | 55.9 | 69.4 | 32.3 | 0.0693 | 0.45 | 14.57 | 1
June | 4 | 5PM to 6PM | 87.1 | 66.7 | 55.9 | 69.4 | 31.81 | 0.0696 | 0.45 | 14.52 | 1
June | 4 | 6PM to 7PM | 84.9 | 66 | 55.9 | 69.4 | 31.28 | 0.0698 | 0.45 | 14.46 | 1
June | 4 | 7PM to 8PM | 82 | 65.7 | 57 | 72.3 | 31.02 | 0.0702 | 0.47 | 14.4 | 1
June | 4 | 8PM to 9PM | 78.1 | 65.5 | 59 | 77.7 | 30.9 | 0.0707 | 0.5 | 14.31 | 1
June | 4 | 9PM to 10PM | 75.9 | 65.4 | 60.1 | 80.8 | 30.86 | 0.0709 | 0.52 | 14.26 | 1
June | 4 | 10PM to 11PM | 73 | 64.5 | 60.1 | 80.8 | 30.15 | 0.0713 | 0.52 | 14.18 | 1
June | 4 | 11PM to 12AM | 73.9 | 64.8 | 60.1 | 80.8 | 30.37 | 0.0712 | 0.52 | 14.21 | 1
June | 5 | 12AM to 1AM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
June | 5 | 1AM to 2AM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
June | 5 | 2AM to 3AM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
June | 5 | 3AM to 4AM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
June | 5 | 4AM to 5AM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
June | 5 | 5AM to 6AM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
June | 5 | 6AM to 7AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
June | 5 | 7AM to 8AM | 73.9 | 65.3 | 61 | 83.5 | 30.79 | 0.0712 | 0.54 | 14.22 | 1
June | 5 | 8AM to 9AM | 79 | 67.5 | 62.1 | 86.8 | 32.55 | 0.0705 | 0.56 | 14.36 | 1
June | 5 | 9AM to 10AM | 84 | 69 | 62.1 | 86.8 | 33.78 | 0.0698 | 0.56 | 14.5 | 1
June | 5 | 10AM to 11AM | 86 | 67.9 | 59 | 77.7 | 32.84 | 0.0696 | 0.5 | 14.52 | 1
June | 5 | 11AM to 12PM | 87.1 | 67.2 | 57 | 72.3 | 32.25 | 0.0695 | 0.47 | 14.53 | 1
June | 5 | 12PM to 1PM | 89.1 | 68.3 | 57.9 | 74.7 | 33.12 | 0.0693 | 0.48 | 14.59 | 1
June | 5 | 1PM to 2PM | 89.1 | 68.3 | 57.9 | 74.7 | 33.12 | 0.0693 | 0.48 | 14.59 | 1
June | 5 | 2PM to 3PM | 89.1 | 68.3 | 57.9 | 74.7 | 33.12 | 0.0693 | 0.48 | 14.59 | 1
June | 5 | 3PM to 4PM | 90 | 68.1 | 57 | 72.3 | 32.96 | 0.0692 | 0.47 | 14.61 | 1
June | 5 | 4PM to 5PM | 90 | 68.1 | 57 | 72.3 | 32.96 | 0.0692 | 0.47 | 14.61 | 1
June | 5 | 5PM to 6PM | 88 | 68 | 57.9 | 74.7 | 32.85 | 0.0694 | 0.48 | 14.56 | 1
June | 5 | 6PM to 7PM | 84.9 | 67 | 57.9 | 74.7 | 32.11 | 0.0698 | 0.48 | 14.48 | 1
June | 5 | 7PM to 8PM | 81 | 65.8 | 57.9 | 74.7 | 31.14 | 0.0703 | 0.48 | 14.37 | 1
June | 5 | 8PM to 9PM | 75 | 64.5 | 59 | 77.7 | 30.15 | 0.0711 | 0.5 | 14.23 | 1
June | 5 | 9PM to 10PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
June | 5 | 10PM to 11PM | 69.1 | 62.5 | 59 | 77.7 | 28.7 | 0.0719 | 0.5 | 14.07 | 1
June | 5 | 11PM to 12AM | 66.9 | 61.2 | 57.9 | 74.7 | 27.7 | 0.0722 | 0.48 | 14 | 1
June | 6 | 12AM to 1AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
June | 6 | 1AM to 2AM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
June | 6 | 2AM to 3AM | 66.9 | 59.5 | 55 | 67.2 | 26.53 | 0.0722 | 0.44 | 13.98 | 1
June | 6 | 3AM to 4AM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
June | 6 | 4AM to 5AM | 66 | 59.7 | 55.9 | 69.4 | 26.66 | 0.0723 | 0.45 | 13.96 | 1
June | 6 | 5AM to 6AM | 66 | 59.7 | 55.9 | 69.4 | 26.66 | 0.0723 | 0.45 | 13.96 | 1
June | 6 | 6AM to 7AM | 70 | 60 | 54 | 64.5 | 26.87 | 0.0718 | 0.42 | 14.05 | 1
June | 6 | 7AM to 8AM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
June | 6 | 8AM to 9AM | 79 | 67.5 | 62.1 | 86.8 | 32.55 | 0.0705 | 0.56 | 14.36 | 1
June | 6 | 9AM to 10AM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
June | 6 | 10AM to 11AM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
June | 6 | 11AM to 12PM | 91 | 72.2 | 64 | 93.2 | 36.51 | 0.0689 | 0.6 | 14.7 | 1
June | 6 | 12PM to 1PM | 91.9 | 71.8 | 63 | 89.6 | 36.18 | 0.0688 | 0.58 | 14.72 | 1
June | 6 | 1PM to 2PM | 93 | 71.6 | 62.1 | 86.8 | 35.99 | 0.0687 | 0.56 | 14.74 | 1
June | 6 | 2PM to 3PM | 93.9 | 72.4 | 63 | 89.6 | 36.66 | 0.0686 | 0.58 | 14.77 | 1
June | 6 | 3PM to 4PM | 93 | 71.6 | 62.1 | 86.8 | 35.99 | 0.0687 | 0.56 | 14.74 | 1
June | 6 | 4PM to 5PM | 93 | 71 | 61 | 83.5 | 35.47 | 0.0687 | 0.54 | 14.72 | 1
June | 6 | 5PM to 6PM | 91 | 70 | 60.1 | 80.8 | 34.56 | 0.069 | 0.52 | 14.66 | 1
June | 6 | 6PM to 7PM | 82 | 65.1 | 55.9 | 69.4 | 30.58 | 0.0702 | 0.45 | 14.39 | 1
June | 6 | 7PM to 8PM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
June | 6 | 8PM to 9PM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
June | 6 | 9PM to 10PM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
June | 6 | 10PM to 11PM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
June | 6 | 11PM to 12AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
June | 7 | 12AM to 1AM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
June | 7 | 1AM to 2AM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
June | 7 | 2AM to 3AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
June | 7 | 3AM to 4AM | 60.1 | 54.8 | 51.1 | 58 | 23.43 | 0.0732 | 0.38 | 13.77 | 1
June | 7 | 4AM to 5AM | 57 | 54 | 52 | 59.9 | 22.99 | 0.0737 | 0.39 | 13.69 | 1
June | 7 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 58 | 22.42 | 0.0738 | 0.38 | 13.66 | 1
June | 7 | 6AM to 7AM | 57.9 | 52.8 | 48.9 | 53.4 | 22.2 | 0.0736 | 0.35 | 13.7 | 1
June | 7 | 7AM to 8AM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
June | 7 | 8AM to 9AM | 66 | 55.5 | 48 | 51.6 | 23.89 | 0.0724 | 0.34 | 13.9 | 1
June | 7 | 9AM to 10AM | 68 | 56.3 | 48 | 51.6 | 24.37 | 0.0722 | 0.34 | 13.96 | 1
June | 7 | 10AM to 11AM | 70 | 56.6 | 46.9 | 49.6 | 24.53 | 0.0719 | 0.32 | 14 | 1
June | 7 | 11AM to 12PM | 72 | 57.8 | 48 | 51.6 | 25.34 | 0.0716 | 0.34 | 14.06 | 1
June | 7 | 12PM to 1PM | 73 | 58.6 | 48.9 | 53.4 | 25.88 | 0.0715 | 0.35 | 14.1 | 1
June | 7 | 1PM to 2PM | 73.9 | 58.9 | 48.9 | 53.4 | 26.1 | 0.0714 | 0.35 | 14.12 | 1
June | 7 | 2PM to 3PM | 75 | 59.3 | 48.9 | 53.4 | 26.36 | 0.0712 | 0.35 | 14.15 | 1
June | 7 | 3PM to 4PM | 75.9 | 58.8 | 46.9 | 49.6 | 25.97 | 0.0711 | 0.32 | 14.16 | 1
June | 7 | 4PM to 5PM | 75 | 57.6 | 45 | 45.9 | 25.19 | 0.0713 | 0.3 | 14.12 | 1
June | 7 | 5PM to 6PM | 73.9 | 56.8 | 44.1 | 44.4 | 24.68 | 0.0714 | 0.29 | 14.09 | 1
June | 7 | 6PM to 7PM | 72 | 56.1 | 44.1 | 44.4 | 24.2 | 0.0717 | 0.29 | 14.04 | 1
June | 7 | 7PM to 8PM | 69.1 | 55.3 | 45 | 45.9 | 23.75 | 0.0721 | 0.3 | 13.97 | 1
June | 7 | 8PM to 9PM | 66 | 54.6 | 46 | 47.9 | 23.31 | 0.0725 | 0.31 | 13.89 | 1
June | 7 | 9PM to 10PM | 64 | 53.8 | 46 | 47.9 | 22.82 | 0.0727 | 0.31 | 13.84 | 1
June | 7 | 10PM to 11PM | 63 | 52.9 | 45 | 45.9 | 22.26 | 0.0729 | 0.3 | 13.81 | 1
June | 7 | 11PM to 12AM | 60.1 | 51.3 | 44.1 | 44.4 | 21.32 | 0.0733 | 0.29 | 13.73 | 1
June | 8 | 12AM to 1AM | 57 | 50 | 44.1 | 44.4 | 20.57 | 0.0738 | 0.29 | 13.64 | 1
June | 8 | 1AM to 2AM | 53.1 | 49.2 | 46 | 47.9 | 20.16 | 0.0743 | 0.31 | 13.55 | 1
June | 8 | 2AM to 3AM | 55 | 49.1 | 44.1 | 44.4 | 20.09 | 0.074 | 0.29 | 13.59 | 1
June | 8 | 3AM to 4AM | 53.1 | 47.7 | 43 | 42.5 | 19.33 | 0.0743 | 0.28 | 13.53 | 1
June | 8 | 4AM to 5AM | 53.1 | 47.3 | 42.1 | 41.1 | 19.1 | 0.0743 | 0.27 | 13.53 | 1
June | 8 | 5AM to 6AM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
June | 8 | 6AM to 7AM | 57 | 48.6 | 41 | 39.4 | 19.8 | 0.0738 | 0.26 | 13.63 | 1
June | 8 | 7AM to 8AM | 63 | 51.6 | 42.1 | 41.1 | 21.51 | 0.0729 | 0.27 | 13.79 | 1
June | 8 | 8AM to 9AM | 66.9 | 53.6 | 43 | 42.5 | 22.69 | 0.0724 | 0.28 | 13.9 | 1
June | 8 | 9AM to 10AM | 68 | 54.5 | 44.1 | 44.4 | 23.24 | 0.0722 | 0.29 | 13.93 | 1
June | 8 | 10AM to 11AM | 71.1 | 55.7 | 44.1 | 44.4 | 23.98 | 0.0718 | 0.29 | 14.01 | 1
June | 8 | 11AM to 12PM | 73 | 56.1 | 43 | 42.5 | 24.18 | 0.0715 | 0.28 | 14.06 | 1
June | 8 | 12PM to 1PM | 73 | 54.9 | 39.9 | 37.8 | 23.43 | 0.0716 | 0.25 | 14.05 | 1
June | 8 | 1PM to 2PM | 75 | 56.1 | 41 | 39.4 | 24.17 | 0.0713 | 0.26 | 14.1 | 1
June | 8 | 2PM to 3PM | 78.1 | 57.6 | 42.1 | 41.1 | 25.17 | 0.0709 | 0.27 | 14.19 | 1
June | 8 | 3PM to 4PM | 79 | 56.9 | 39 | 36.4 | 24.67 | 0.0708 | 0.24 | 14.2 | 1
June | 8 | 4PM to 5PM | 80.1 | 57.3 | 39 | 36.4 | 24.93 | 0.0707 | 0.24 | 14.23 | 1
June | 8 | 5PM to 6PM | 79 | 55.6 | 35.1 | 31.1 | 23.83 | 0.0708 | 0.2 | 14.18 | 1
June | 8 | 6PM to 7PM | 77 | 55.7 | 37.9 | 34.9 | 23.95 | 0.0711 | 0.23 | 14.14 | 1
June | 8 | 7PM to 8PM | 71.1 | 54.1 | 39.9 | 37.8 | 22.95 | 0.0718 | 0.25 | 13.99 | 1
June | 8 | 8PM to 9PM | 69.1 | 54.1 | 42.1 | 41.1 | 22.99 | 0.0721 | 0.27 | 13.95 | 1
June | 8 | 9PM to 10PM | 66 | 54.1 | 45 | 45.9 | 23 | 0.0725 | 0.3 | 13.89 | 1
June | 8 | 10PM to 11PM | 63 | 53.4 | 46 | 47.9 | 22.56 | 0.0729 | 0.31 | 13.81 | 1
June | 8 | 11PM to 12AM | 62.1 | 52.1 | 44.1 | 44.4 | 21.8 | 0.073 | 0.29 | 13.78 | 1
June | 9 | 12AM to 1AM | 60.1 | 49.9 | 41 | 39.4 | 20.54 | 0.0734 | 0.26 | 13.71 | 1
June | 9 | 1AM to 2AM | 60.1 | 50.4 | 42.1 | 41.1 | 20.81 | 0.0733 | 0.27 | 13.71 | 1
June | 9 | 2AM to 3AM | 60.1 | 50.4 | 42.1 | 41.1 | 20.81 | 0.0733 | 0.27 | 13.71 | 1
June | 9 | 3AM to 4AM | 57.9 | 48.5 | 39.9 | 37.8 | 19.77 | 0.0737 | 0.25 | 13.65 | 1
June | 9 | 4AM to 5AM | 57 | 48.6 | 41 | 39.4 | 19.8 | 0.0738 | 0.26 | 13.63 | 1
June | 9 | 5AM to 6AM | 55.9 | 48.6 | 42.1 | 41.1 | 19.8 | 0.0739 | 0.27 | 13.61 | 1
June | 9 | 6AM to 7AM | 63 | 52.5 | 44.1 | 44.4 | 22.02 | 0.0729 | 0.29 | 13.8 | 1
June | 9 | 7AM to 8AM | 70 | 55.3 | 44.1 | 44.4 | 23.72 | 0.072 | 0.29 | 13.99 | 1
June | 9 | 8AM to 9AM | 73 | 57.3 | 46 | 47.9 | 25.01 | 0.0715 | 0.31 | 14.08 | 1
June | 9 | 9AM to 10AM | 75.9 | 59.7 | 48.9 | 53.4 | 26.58 | 0.0711 | 0.35 | 14.17 | 1
June | 9 | 10AM to 11AM | 80.1 | 62.1 | 51.1 | 58 | 28.3 | 0.0705 | 0.38 | 14.3 | 1
June | 9 | 11AM to 12PM | 82.9 | 63.5 | 52 | 59.9 | 29.31 | 0.0701 | 0.39 | 14.38 | 1
June | 9 | 12PM to 1PM | 84.9 | 65.1 | 54 | 64.5 | 30.51 | 0.0699 | 0.42 | 14.45 | 1
June | 9 | 1PM to 2PM | 86 | 65.9 | 55 | 67.2 | 31.19 | 0.0697 | 0.44 | 14.48 | 1
June | 9 | 2PM to 3PM | 84.9 | 66 | 55.9 | 69.4 | 31.28 | 0.0698 | 0.45 | 14.46 | 1
June | 9 | 3PM to 4PM | 84.9 | 66.6 | 57 | 72.3 | 31.73 | 0.0698 | 0.47 | 14.47 | 1
June | 9 | 4PM to 5PM | 84.9 | 66.6 | 57 | 72.3 | 31.73 | 0.0698 | 0.47 | 14.47 | 1
June | 9 | 5PM to 6PM | 82.9 | 65 | 55 | 67.2 | 30.44 | 0.0701 | 0.44 | 14.4 | 1
June | 9 | 6PM to 7PM | 81 | 64.3 | 55 | 67.2 | 29.96 | 0.0704 | 0.44 | 14.35 | 1
June | 9 | 7PM to 8PM | 77 | 62.5 | 54 | 64.5 | 28.58 | 0.0709 | 0.42 | 14.24 | 1
June | 9 | 8PM to 9PM | 73 | 56.5 | 44.1 | 44.4 | 24.46 | 0.0715 | 0.29 | 14.07 | 1
June | 9 | 9PM to 10PM | 71.1 | 54.5 | 41 | 39.4 | 23.21 | 0.0718 | 0.26 | 14 | 1
June | 9 | 10PM to 11PM | 69.1 | 53.3 | 39.9 | 37.8 | 22.47 | 0.0721 | 0.25 | 13.94 | 1
June | 9 | 11PM to 12AM | 64.9 | 51.6 | 39.9 | 37.8 | 21.47 | 0.0727 | 0.25 | 13.83 | 1
June | 10 | 12AM to 1AM | 60.1 | 49.5 | 39.9 | 37.8 | 20.29 | 0.0734 | 0.25 | 13.7 | 1
June | 10 | 1AM to 2AM | 60.1 | 49.5 | 39.9 | 37.8 | 20.29 | 0.0734 | 0.25 | 13.7 | 1
June | 10 | 2AM to 3AM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
June | 10 | 3AM to 4AM | 54 | 47.2 | 41 | 39.4 | 19.06 | 0.0742 | 0.26 | 13.55 | 1
June | 10 | 4AM to 5AM | 52 | 47.8 | 44.1 | 44.4 | 19.35 | 0.0745 | 0.29 | 13.51 | 1
June | 10 | 5AM to 6AM | 54 | 48.1 | 43 | 42.5 | 19.55 | 0.0742 | 0.28 | 13.56 | 1
June | 10 | 6AM to 7AM | 57 | 50 | 44.1 | 44.4 | 20.57 | 0.0738 | 0.29 | 13.64 | 1
June | 10 | 7AM to 8AM | 61 | 53 | 46.9 | 49.6 | 22.34 | 0.0732 | 0.32 | 13.76 | 1
June | 10 | 8AM to 9AM | 69.1 | 55.8 | 46 | 47.9 | 24.05 | 0.0721 | 0.31 | 13.97 | 1
June | 10 | 9AM to 10AM | 71.1 | 55.3 | 43 | 42.5 | 23.7 | 0.0718 | 0.28 | 14.01 | 1
June | 10 | 10AM to 11AM | 75 | 56.8 | 43 | 42.5 | 24.66 | 0.0713 | 0.28 | 14.11 | 1
June | 10 | 11AM to 12PM | 78.1 | 56.5 | 39 | 36.4 | 24.45 | 0.0709 | 0.24 | 14.17 | 1
June | 10 | 12PM to 1PM | 80.1 | 56.9 | 37.9 | 34.9 | 24.69 | 0.0707 | 0.23 | 14.22 | 1
June | 10 | 1PM to 2PM | 84 | 58.4 | 37.9 | 34.9 | 25.65 | 0.0701 | 0.23 | 14.33 | 1
June | 10 | 2PM to 3PM | 84.9 | 58.1 | 36 | 32.3 | 25.45 | 0.07 | 0.21 | 14.34 | 1
June | 10 | 3PM to 4PM | 86 | 58.2 | 35.1 | 31.1 | 25.53 | 0.0699 | 0.2 | 14.37 | 1
June | 10 | 4PM to 5PM | 84.9 | 57.3 | 33.1 | 28.8 | 24.9 | 0.0701 | 0.19 | 14.33 | 1
June | 10 | 5PM to 6PM | 84 | 56.9 | 33.1 | 28.8 | 24.68 | 0.0702 | 0.19 | 14.31 | 1
June | 10 | 6PM to 7PM | 81 | 56.6 | 36 | 32.3 | 24.49 | 0.0706 | 0.21 | 14.24 | 1
June | 10 | 7PM to 8PM | 75.9 | 55.3 | 37.9 | 34.9 | 23.69 | 0.0712 | 0.23 | 14.11 | 1
June | 10 | 8PM to 9PM | 72 | 54.1 | 39 | 36.4 | 22.96 | 0.0717 | 0.24 | 14.01 | 1
June | 10 | 9PM to 10PM | 70 | 53.3 | 39 | 36.4 | 22.49 | 0.072 | 0.24 | 13.96 | 1
June | 10 | 10PM to 11PM | 70 | 53.3 | 39 | 36.4 | 22.49 | 0.072 | 0.24 | 13.96 | 1
June | 10 | 11PM to 12AM | 69.1 | 53 | 39 | 36.4 | 22.27 | 0.0721 | 0.24 | 13.94 | 1
June | 11 | 12AM to 1AM | 66.9 | 52.4 | 39.9 | 37.8 | 21.95 | 0.0724 | 0.25 | 13.88 | 1
June | 11 | 1AM to 2AM | 64.9 | 51.6 | 39.9 | 37.8 | 21.47 | 0.0727 | 0.25 | 13.83 | 1
June | 11 | 2AM to 3AM | 61 | 51.7 | 44.1 | 44.4 | 21.54 | 0.0732 | 0.29 | 13.75 | 1
June | 11 | 3AM to 4AM | 61 | 51.7 | 44.1 | 44.4 | 21.54 | 0.0732 | 0.29 | 13.75 | 1
June | 11 | 4AM to 5AM | 55.9 | 49.9 | 45 | 45.9 | 20.55 | 0.0739 | 0.3 | 13.62 | 1
June | 11 | 5AM to 6AM | 64 | 51.6 | 41 | 39.4 | 21.5 | 0.0728 | 0.26 | 13.81 | 1
June | 11 | 6AM to 7AM | 68 | 52.9 | 39.9 | 37.8 | 22.21 | 0.0723 | 0.25 | 13.91 | 1
June | 11 | 7AM to 8AM | 71.1 | 54.9 | 42.1 | 41.1 | 23.47 | 0.0718 | 0.27 | 14 | 1
June | 11 | 8AM to 9AM | 73.9 | 57.2 | 45 | 45.9 | 24.93 | 0.0714 | 0.3 | 14.1 | 1
June | 11 | 9AM to 10AM | 77 | 58.3 | 45 | 45.9 | 25.67 | 0.071 | 0.3 | 14.18 | 1
June | 11 | 10AM to 11AM | 80.1 | 59.9 | 46 | 47.9 | 26.72 | 0.0706 | 0.31 | 14.26 | 1
June | 11 | 11AM to 12PM | 82.9 | 62.6 | 50 | 55.6 | 28.64 | 0.0702 | 0.36 | 14.37 | 1
June | 11 | 12PM to 1PM | 86 | 65.9 | 55 | 67.2 | 31.19 | 0.0697 | 0.44 | 14.48 | 1
June | 11 | 1PM to 2PM | 88 | 67.5 | 57 | 72.3 | 32.47 | 0.0694 | 0.47 | 14.55 | 1
June | 11 | 2PM to 3PM | 90 | 70.2 | 61 | 83.5 | 34.72 | 0.0691 | 0.54 | 14.64 | 1
June | 11 | 3PM to 4PM | 91 | 70.5 | 61 | 83.5 | 34.99 | 0.069 | 0.54 | 14.67 | 1
June | 11 | 4PM to 5PM | 90 | 69.7 | 60.1 | 80.8 | 34.3 | 0.0691 | 0.52 | 14.63 | 1
June | 11 | 5PM to 6PM | 90 | 69.7 | 60.1 | 80.8 | 34.3 | 0.0691 | 0.52 | 14.63 | 1
June | 11 | 6PM to 7PM | 88 | 69.1 | 60.1 | 80.8 | 33.81 | 0.0694 | 0.52 | 14.58 | 1
June | 11 | 7PM to 8PM | 82.9 | 68.1 | 61 | 83.5 | 33 | 0.07 | 0.54 | 14.46 | 1
June | 11 | 8PM to 9PM | 81 | 68.1 | 62.1 | 86.8 | 33.03 | 0.0702 | 0.56 | 14.41 | 1
June | 11 | 9PM to 10PM | 79 | 67.5 | 62.1 | 86.8 | 32.55 | 0.0705 | 0.56 | 14.36 | 1
June | 11 | 10PM to 11PM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
June | 11 | 11PM to 12AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
June | 12 | 12AM to 1AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 12 | 1AM to 2AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 12 | 2AM to 3AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
June | 12 | 3AM to 4AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
June | 12 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 12 | 5AM to 6AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
June | 12 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 12 | 7AM to 8AM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
June | 12 | 8AM to 9AM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
June | 12 | 9AM to 10AM | 84 | 73.3 | 69.1 | 111.4 | 37.65 | 0.0697 | 0.72 | 14.58 | 1
June | 12 | 10AM to 11AM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
June | 12 | 11AM to 12PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
June | 12 | 12PM to 1PM | 90 | 72.4 | 64.9 | 96.2 | 36.73 | 0.069 | 0.62 | 14.68 | 1
June | 12 | 1PM to 2PM | 90 | 72.4 | 64.9 | 96.2 | 36.73 | 0.069 | 0.62 | 14.68 | 1
June | 12 | 2PM to 3PM | 91.9 | 72.9 | 64.9 | 96.2 | 37.21 | 0.0688 | 0.62 | 14.74 | 1
June | 12 | 3PM to 4PM | 91.9 | 71.3 | 62.1 | 86.8 | 35.73 | 0.0688 | 0.56 | 14.71 | 1
June | 12 | 4PM to 5PM | 90 | 71.3 | 63 | 89.6 | 35.69 | 0.0691 | 0.58 | 14.66 | 1
June | 12 | 5PM to 6PM | 89.1 | 71 | 63 | 89.6 | 35.47 | 0.0692 | 0.58 | 14.64 | 1
June | 12 | 6PM to 7PM | 88 | 71.3 | 64 | 93.2 | 35.76 | 0.0693 | 0.6 | 14.62 | 1
June | 12 | 7PM to 8PM | 82.9 | 71.1 | 66 | 100 | 35.59 | 0.0699 | 0.64 | 14.51 | 1
June | 12 | 8PM to 9PM | 80.1 | 70.2 | 66 | 100 | 34.88 | 0.0703 | 0.64 | 14.43 | 1
June | 12 | 9PM to 10PM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
June | 12 | 10PM to 11PM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
June | 12 | 11PM to 12AM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
June | 13 | 12AM to 1AM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
June | 13 | 1AM to 2AM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
June | 13 | 2AM to 3AM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
June | 13 | 3AM to 4AM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
June | 13 | 4AM to 5AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
June | 13 | 5AM to 6AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
June | 13 | 6AM to 7AM | 72 | 67.1 | 64.9 | 96.2 | 32.3 | 0.0714 | 0.62 | 14.2 | 1
June | 13 | 7AM to 8AM | 77 | 68.7 | 64.9 | 96.2 | 33.54 | 0.0707 | 0.62 | 14.34 | 1
June | 13 | 8AM to 9AM | 81 | 70.5 | 66 | 100 | 35.1 | 0.0702 | 0.64 | 14.46 | 1
June | 13 | 9AM to 10AM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
June | 13 | 10AM to 11AM | 89.1 | 73.3 | 66.9 | 103.2 | 37.61 | 0.0691 | 0.67 | 14.68 | 1
June | 13 | 11AM to 12PM | 90 | 73 | 66 | 100 | 37.32 | 0.069 | 0.64 | 14.7 | 1
June | 13 | 12PM to 1PM | 91.9 | 72.4 | 64 | 93.2 | 36.73 | 0.0688 | 0.6 | 14.73 | 1
June | 13 | 1PM to 2PM | 93 | 72.1 | 63 | 89.6 | 36.44 | 0.0687 | 0.58 | 14.74 | 1
June | 13 | 2PM to 3PM | 91 | 71.1 | 62.1 | 86.8 | 35.51 | 0.069 | 0.56 | 14.68 | 1
June | 13 | 3PM to 4PM | 90 | 72.4 | 64.9 | 96.2 | 36.73 | 0.069 | 0.62 | 14.68 | 1
June | 13 | 4PM to 5PM | 91 | 72.2 | 64 | 93.2 | 36.51 | 0.0689 | 0.6 | 14.7 | 1
June | 13 | 5PM to 6PM | 90 | 71.3 | 63 | 89.6 | 35.69 | 0.0691 | 0.58 | 14.66 | 1
June | 13 | 6PM to 7PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
June | 13 | 7PM to 8PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
June | 13 | 8PM to 9PM | 82.9 | 71.1 | 66 | 100 | 35.59 | 0.0699 | 0.64 | 14.51 | 1
June | 13 | 9PM to 10PM | 81 | 69.8 | 64.9 | 96.2 | 34.51 | 0.0702 | 0.62 | 14.44 | 1
June | 13 | 10PM to 11PM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
June | 13 | 11PM to 12AM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
June | 14 | 12AM to 1AM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
June | 14 | 1AM to 2AM | 75 | 66.8 | 63 | 89.6 | 32.02 | 0.071 | 0.58 | 14.26 | 1
June | 14 | 2AM to 3AM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
June | 14 | 3AM to 4AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
June | 14 | 4AM to 5AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
June | 14 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
June | 14 | 6AM to 7AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
June | 14 | 7AM to 8AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
June | 14 | 8AM to 9AM | 77 | 69.9 | 66.9 | 103.2 | 34.63 | 0.0707 | 0.67 | 14.36 | 1
June | 14 | 9AM to 10AM | 78.1 | 70.2 | 66.9 | 103.2 | 34.9 | 0.0705 | 0.67 | 14.39 | 1
June | 14 | 10AM to 11AM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
June | 14 | 11AM to 12PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
June | 14 | 12PM to 1PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
June | 14 | 1PM to 2PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
June | 14 | 2PM to 3PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
June | 14 | 3PM to 4PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
June | 14 | 4PM to 5PM | 87.1 | 70.4 | 63 | 89.6 | 34.98 | 0.0694 | 0.58 | 14.59 | 1
June | 14 | 5PM to 6PM | 86 | 69 | 61 | 83.5 | 33.75 | 0.0696 | 0.54 | 14.54 | 1
June | 14 | 6PM to 7PM | 82.9 | 68.1 | 61 | 83.5 | 33 | 0.07 | 0.54 | 14.46 | 1
June | 14 | 7PM to 8PM | 82 | 68.4 | 62.1 | 86.8 | 33.3 | 0.0701 | 0.56 | 14.44 | 1
June | 14 | 8PM to 9PM | 80.1 | 70.2 | 66 | 100 | 34.88 | 0.0703 | 0.64 | 14.43 | 1
June | 14 | 9PM to 10PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
June | 14 | 10PM to 11PM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
June | 14 | 11PM to 12AM | 75 | 65.7 | 61 | 83.5 | 31.06 | 0.071 | 0.54 | 14.24 | 1
June | 15 | 12AM to 1AM | 73.9 | 66 | 62.1 | 86.8 | 31.31 | 0.0712 | 0.56 | 14.23 | 1
June | 15 | 1AM to 2AM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
June | 15 | 2AM to 3AM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
June | 15 | 3AM to 4AM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
June | 15 | 4AM to 5AM | 72 | 65.3 | 62.1 | 86.8 | 30.82 | 0.0714 | 0.56 | 14.17 | 1
June | 15 | 5AM to 6AM | 72 | 65.3 | 62.1 | 86.8 | 30.82 | 0.0714 | 0.56 | 14.17 | 1
June | 15 | 6AM to 7AM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
June | 15 | 7AM to 8AM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
June | 15 | 8AM to 9AM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
June | 15 | 9AM to 10AM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
June | 15 | 10AM to 11AM | 79 | 68.7 | 64 | 93.2 | 33.55 | 0.0705 | 0.6 | 14.38 | 1
June | 15 | 11AM to 12PM | 80.1 | 69.6 | 64.9 | 96.2 | 34.29 | 0.0703 | 0.62 | 14.42 | 1
June | 15 | 12PM to 1PM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
June | 15 | 1PM to 2PM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
June | 15 | 2PM to 3PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
June | 15 | 3PM to 4PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
June | 15 | 4PM to 5PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
June | 15 | 5PM to 6PM | 78.1 | 69 | 64.9 | 96.2 | 33.8 | 0.0706 | 0.62 | 14.37 | 1
June | 15 | 6PM to 7PM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
June | 15 | 7PM to 8PM | 73.9 | 67.2 | 64 | 93.2 | 32.31 | 0.0711 | 0.6 | 14.25 | 1
June | 15 | 8PM to 9PM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
June | 15 | 9PM to 10PM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
June | 15 | 10PM to 11PM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
June | 15 | 11PM to 12AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
June | 16 | 12AM to 1AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 16 | 1AM to 2AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 16 | 2AM to 3AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 16 | 3AM to 4AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 16 | 4AM to 5AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 16 | 5AM to 6AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 16 | 6AM to 7AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
June | 16 | 7AM to 8AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
June | 16 | 8AM to 9AM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
June | 16 | 9AM to 10AM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
June | 16 | 10AM to 11AM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
June | 16 | 11AM to 12PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
June | 16 | 12PM to 1PM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
June | 16 | 1PM to 2PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
June | 16 | 2PM to 3PM | 82.9 | 69.2 | 63 | 89.6 | 33.97 | 0.07 | 0.58 | 14.48 | 1
June | 16 | 3PM to 4PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
June | 16 | 4PM to 5PM | 86 | 70.7 | 64 | 93.2 | 35.27 | 0.0696 | 0.6 | 14.57 | 1
June | 16 | 5PM to 6PM | 82.9 | 69.2 | 63 | 89.6 | 33.97 | 0.07 | 0.58 | 14.48 | 1
June | 16 | 6PM to 7PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
June | 16 | 7PM to 8PM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
June | 16 | 8PM to 9PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
June | 16 | 9PM to 10PM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
June | 16 | 10PM to 11PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
June | 16 | 11PM to 12AM | 72 | 67.1 | 64.9 | 96.2 | 32.3 | 0.0714 | 0.62 | 14.2 | 1
June | 17 | 12AM to 1AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
June | 17 | 1AM to 2AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
June | 17 | 2AM to 3AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 17 | 3AM to 4AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
June | 17 | 4AM to 5AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
June | 17 | 5AM to 6AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
June | 17 | 6AM to 7AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
June | 17 | 7AM to 8AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
June | 17 | 8AM to 9AM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
June | 17 | 9AM to 10AM | 81 | 71.8 | 68 | 107.2 | 36.24 | 0.0701 | 0.69 | 14.48 | 1
June | 17 | 10AM to 11AM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
June | 17 | 11AM to 12PM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
June | 17 | 12PM to 1PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
June | 17 | 1PM to 2PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
June | 17 | 2PM to 3PM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
June | 17 | 3PM to 4PM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
June | 17 | 4PM to 5PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
June | 17 | 5PM to 6PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
June | 17 | 6PM to 7PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
June | 17 | 7PM to 8PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
June | 17 | 8PM to 9PM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
June | 17 | 9PM to 10PM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
June | 17 | 10PM to 11PM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
June | 17 | 11PM to 12AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
June | 18 | 12AM to 1AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
June | 18 | 1AM to 2AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
June | 18 | 2AM to 3AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
June | 18 | 3AM to 4AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 18 | 4AM to 5AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 18 | 5AM to 6AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
June | 18 | 6AM to 7AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 18 | 7AM to 8AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 18 | 8AM to 9AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
June | 18 | 9AM to 10AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
June | 18 | 10AM to 11AM | 80.1 | 74.2 | 72 | 123.2 | 38.52 | 0.0701 | 0.79 | 14.51 | 1
June | 18 | 11AM to 12PM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
June | 18 | 12PM to 1PM | 82.9 | 74.3 | 71.1 | 119.4 | 38.63 | 0.0698 | 0.77 | 14.57 | 1
June | 18 | 1PM to 2PM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
June | 18 | 2PM to 3PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
June | 18 | 3PM to 4PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
June | 18 | 4PM to 5PM | 82.9 | 75.6 | 73 | 127.9 | 39.97 | 0.0697 | 0.82 | 14.6 | 1
June | 18 | 5PM to 6PM | 81 | 71.8 | 68 | 107.2 | 36.24 | 0.0701 | 0.69 | 14.48 | 1
June | 18 | 6PM to 7PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
June | 18 | 7PM to 8PM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
June | 18 | 8PM to 9PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
June | 18 | 9PM to 10PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
June | 18 | 10PM to 11PM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
June | 18 | 11PM to 12AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
June | 19 | 12AM to 1AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
June | 19 | 1AM to 2AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 19 | 2AM to 3AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 19 | 3AM to 4AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 19 | 4AM to 5AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
June | 19 | 5AM to 6AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 19 | 6AM to 7AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 19 | 7AM to 8AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
June | 19 | 8AM to 9AM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
June | 19 | 9AM to 10AM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
June | 19 | 10AM to 11AM | 84.9 | 71 | 64.9 | 96.2 | 35.49 | 0.0697 | 0.62 | 14.55 | 1
June | 19 | 11AM to 12PM | 84 | 69 | 62.1 | 86.8 | 33.78 | 0.0698 | 0.56 | 14.5 | 1
June | 19 | 12PM to 1PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
June | 19 | 1PM to 2PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
June | 19 | 2PM to 3PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
June | 19 | 3PM to 4PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
June | 19 | 4PM to 5PM | 89.1 | 71.6 | 64 | 93.2 | 36.03 | 0.0692 | 0.6 | 14.65 | 1
June | 19 | 5PM to 6PM | 87.1 | 71.1 | 64 | 93.2 | 35.54 | 0.0694 | 0.6 | 14.6 | 1
June | 19 | 6PM to 7PM | 84.9 | 71 | 64.9 | 96.2 | 35.49 | 0.0697 | 0.62 | 14.55 | 1
June | 19 | 7PM to 8PM | 80.1 | 69.6 | 64.9 | 96.2 | 34.29 | 0.0703 | 0.62 | 14.42 | 1
June | 19 | 8PM to 9PM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
June | 19 | 9PM to 10PM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
June | 19 | 10PM to 11PM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 19 | 11PM to 12AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 20 | 12AM to 1AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 20 | 1AM to 2AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 20 | 2AM to 3AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
June | 20 | 3AM to 4AM | 66.9 | 66.3 | 66 | 100 | 31.64 | 0.072 | 0.64 | 14.08 | 1
June | 20 | 4AM to 5AM | 66.9 | 66.3 | 66 | 100 | 31.64 | 0.072 | 0.64 | 14.08 | 1
June | 20 | 5AM to 6AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
June | 20 | 6AM to 7AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 20 | 7AM to 8AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 20 | 8AM to 9AM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
June | 20 | 9AM to 10AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
June | 20 | 10AM to 11AM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
June | 20 | 11AM to 12PM | 84 | 72.6 | 68 | 107.2 | 37 | 0.0697 | 0.69 | 14.56 | 1
June | 20 | 12PM to 1PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
June | 20 | 1PM to 2PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
June | 20 | 2PM to 3PM | 89.1 | 72.8 | 66 | 100 | 37.1 | 0.0691 | 0.64 | 14.67 | 1
June | 20 | 3PM to 4PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
June | 20 | 4PM to 5PM | 88 | 72.5 | 66 | 100 | 36.83 | 0.0693 | 0.64 | 14.64 | 1
June | 20 | 5PM to 6PM | 87.1 | 72.2 | 66 | 100 | 36.61 | 0.0694 | 0.64 | 14.62 | 1
June | 20 | 6PM to 7PM | 84 | 71.4 | 66 | 100 | 35.86 | 0.0698 | 0.64 | 14.54 | 1
June | 20 | 7PM to 8PM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 20 | 8PM to 9PM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
June | 20 | 9PM to 10PM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
June | 20 | 10PM to 11PM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
June | 20 | 11PM to 12AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
June | 21 | 12AM to 1AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
June | 21 | 1AM to 2AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
June | 21 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
June | 21 | 3AM to 4AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
June | 21 | 4AM to 5AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
June | 21 | 5AM to 6AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
June | 21 | 6AM to 7AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
June | 21 | 7AM to 8AM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
June | 21 | 8AM to 9AM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
June | 21 | 9AM to 10AM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
June | 21 | 10AM to 11AM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
June | 21 | 11AM to 12PM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
June | 21 | 12PM to 1PM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
June | 21 | 1PM to 2PM | 89.1 | 73.3 | 66.9 | 103.2 | 37.61 | 0.0691 | 0.67 | 14.68 | 1
June | 21 | 2PM to 3PM | 90 | 73 | 66 | 100 | 37.32 | 0.069 | 0.64 | 14.7 | 1
June | 21 | 3PM to 4PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
June | 21 | 4PM to 5PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
June | 21 | 5PM to 6PM | 87.1 | 71.1 | 64 | 93.2 | 35.54 | 0.0694 | 0.6 | 14.6 | 1
June | 21 | 6PM to 7PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
June | 21 | 7PM to 8PM | 84 | 70.2 | 64 | 93.2 | 34.79 | 0.0698 | 0.6 | 14.52 | 1
June | 21 | 8PM to 9PM | 80.1 | 69.6 | 64.9 | 96.2 | 34.29 | 0.0703 | 0.62 | 14.42 | 1
June | 21 | 9PM to 10PM | 78.1 | 69 | 64.9 | 96.2 | 33.8 | 0.0706 | 0.62 | 14.37 | 1
June | 21 | 10PM to 11PM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
June | 21 | 11PM to 12AM | 77 | 69.4 | 66 | 100 | 34.13 | 0.0707 | 0.64 | 14.35 | 1
June | 22 | 12AM to 1AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
June | 22 | 1AM to 2AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
June | 22 | 2AM to 3AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
June | 22 | 3AM to 4AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
June | 22 | 4AM to 5AM | 68 | 66.6 | 66 | 100 | 31.91 | 0.0719 | 0.64 | 14.11 | 1
June | 22 | 5AM to 6AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
June | 22 | 6AM to 7AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
June | 22 | 7AM to 8AM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
June | 22 | 8AM to 9AM | 82.9 | 71.1 | 66 | 100 | 35.59 | 0.0699 | 0.64 | 14.51 | 1
June | 22 | 9AM to 10AM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
June | 22 | 10AM to 11AM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
June | 22 | 11AM to 12PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
June | 22 | 12PM to 1PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
June | 22 | 1PM to 2PM | 89.1 | 73.3 | 66.9 | 103.2 | 37.61 | 0.0691 | 0.67 | 14.68 | 1
June | 22 | 2PM to 3PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
June | 22 | 3PM to 4PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
June | 22 | 4PM to 5PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
June | 22 | 5PM to 6PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
June | 22 | 6PM to 7PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
June | 22 | 7PM to 8PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
June | 22 | 8PM to 9PM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
June | 22 | 9PM to 10PM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
June | 22 | 10PM to 11PM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 22 | 11PM to 12AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
June | 23 | 12AM to 1AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
June | 23 | 1AM to 2AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
June | 23 | 2AM to 3AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
June | 23 | 3AM to 4AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
June | 23 | 4AM to 5AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
June | 23 | 5AM to 6AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
June | 23 | 6AM to 7AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
June | 23 | 7AM to 8AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
June | 23 | 8AM to 9AM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
June | 23 | 9AM to 10AM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
June | 23 | 10AM to 11AM | 86 | 75.7 | 72 | 123.2 | 39.99 | 0.0694 | 0.79 | 14.67 | 1
June | 23 | 11AM to 12PM | 89.1 | 75.9 | 71.1 | 119.4 | 40.15 | 0.069 | 0.77 | 14.74 | 1
June | 23 | 12PM to 1PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
June | 23 | 1PM to 2PM | 91 | 74.5 | 68 | 107.2 | 38.73 | 0.0688 | 0.69 | 14.75 | 1
June | 23 | 2PM to 3PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
June | 23 | 3PM to 4PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
June | 23 | 4PM to 5PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
June | 23 | 5PM to 6PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
June | 23 | 6PM to 7PM | 82.9 | 69.9 | 64 | 93.2 | 34.52 | 0.0699 | 0.6 | 14.49 | 1
June | 23 | 7PM to 8PM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
June | 23 | 8PM to 9PM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
June | 23 | 9PM to 10PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
June | 23 | 10PM to 11PM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
June | 23 | 11PM to 12AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
June | 24 | 12AM to 1AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
June | 24 | 1AM to 2AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
June | 24 | 2AM to 3AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
June | 24 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 24 | 4AM to 5AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
June | 24 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 24 | 6AM to 7AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
June | 24 | 7AM to 8AM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
June | 24 | 8AM to 9AM | 80.1 | 72.2 | 69.1 | 111.4 | 36.67 | 0.0702 | 0.72 | 14.47 | 1
June | 24 | 9AM to 10AM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
June | 24 | 10AM to 11AM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
June | 24 | 11AM to 12PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
June | 24 | 12PM to 1PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
June | 24 | 1PM to 2PM | 90 | 71.9 | 64 | 93.2 | 36.25 | 0.0691 | 0.6 | 14.67 | 1
June | 24 | 2PM to 3PM | 91 | 71.6 | 63 | 89.6 | 35.96 | 0.0689 | 0.58 | 14.69 | 1
June | 24 | 3PM to 4PM | 91.9 | 71.8 | 63 | 89.6 | 36.18 | 0.0688 | 0.58 | 14.72 | 1
June | 24 | 4PM to 5PM | 91 | 72.2 | 64 | 93.2 | 36.51 | 0.0689 | 0.6 | 14.7 | 1
June | 24 | 5PM to 6PM | 90 | 71.9 | 64 | 93.2 | 36.25 | 0.0691 | 0.6 | 14.67 | 1
June | 24 | 6PM to 7PM | 87.1 | 71.1 | 64 | 93.2 | 35.54 | 0.0694 | 0.6 | 14.6 | 1
June | 24 | 7PM to 8PM | 82.9 | 68.7 | 62.1 | 86.8 | 33.52 | 0.07 | 0.56 | 14.47 | 1
June | 24 | 8PM to 9PM | 82 | 70.8 | 66 | 100 | 35.37 | 0.07 | 0.64 | 14.49 | 1
June | 24 | 9PM to 10PM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
June | 24 | 10PM to 11PM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
June | 24 | 11PM to 12AM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
June | 25 | 12AM to 1AM | 75 | 68.1 | 64.9 | 96.2 | 33.05 | 0.071 | 0.62 | 14.29 | 1
June | 25 | 1AM to 2AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
June | 25 | 2AM to 3AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
June | 25 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 25 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 25 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 25 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
June | 25 | 7AM to 8AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
June | 25 | 8AM to 9AM | 80.1 | 71.5 | 68 | 107.2 | 36.02 | 0.0702 | 0.69 | 14.46 | 1
June | 25 | 9AM to 10AM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
June | 25 | 10AM to 11AM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
June | 25 | 11AM to 12PM | 88 | 74.3 | 69.1 | 111.4 | 38.63 | 0.0692 | 0.72 | 14.68 | 1
June | 25 | 12PM to 1PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
June | 25 | 1PM to 2PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
June | 25 | 2PM to 3PM | 88 | 74.3 | 69.1 | 111.4 | 38.63 | 0.0692 | 0.72 | 14.68 | 1
June | 25 | 3PM to 4PM | 91.9 | 71.8 | 63 | 89.6 | 36.18 | 0.0688 | 0.58 | 14.72 | 1
June | 25 | 4PM to 5PM | 91 | 72.2 | 64 | 93.2 | 36.51 | 0.0689 | 0.6 | 14.7 | 1
June | 25 | 5PM to 6PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
June | 25 | 6PM to 7PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
June | 25 | 7PM to 8PM | 80.1 | 71.5 | 68 | 107.2 | 36.02 | 0.0702 | 0.69 | 14.46 | 1
June | 25 | 8PM to 9PM | 80.1 | 71.5 | 68 | 107.2 | 36.02 | 0.0702 | 0.69 | 14.46 | 1
June | 25 | 9PM to 10PM | 80.1 | 71.5 | 68 | 107.2 | 36.02 | 0.0702 | 0.69 | 14.46 | 1
June | 25 | 10PM to 11PM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
June | 25 | 11PM to 12AM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
June | 26 | 12AM to 1AM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
June | 26 | 1AM to 2AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 2AM to 3AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 3AM to 4AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 4AM to 5AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 5AM to 6AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 6AM to 7AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 7AM to 8AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
June | 26 | 8AM to 9AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
June | 26 | 9AM to 10AM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
June | 26 | 10AM to 11AM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
June | 26 | 11AM to 12PM | 82.9 | 74.3 | 71.1 | 119.4 | 38.63 | 0.0698 | 0.77 | 14.57 | 1
June | 26 | 12PM to 1PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
June | 26 | 1PM to 2PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
June | 26 | 2PM to 3PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
June | 26 | 3PM to 4PM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
June | 26 | 4PM to 5PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
June | 26 | 5PM to 6PM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 6PM to 7PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
June | 26 | 7PM to 8PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
June | 26 | 8PM to 9PM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 26 | 9PM to 10PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
June | 26 | 10PM to 11PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
June | 26 | 11PM to 12AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
June | 27 | 12AM to 1AM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
June | 27 | 1AM to 2AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
June | 27 | 2AM to 3AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
June | 27 | 3AM to 4AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 27 | 4AM to 5AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 27 | 5AM to 6AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
June | 27 | 6AM to 7AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
June | 27 | 7AM to 8AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
June | 27 | 8AM to 9AM | 78.1 | 73 | 71.1 | 119.4 | 37.43 | 0.0704 | 0.77 | 14.44 | 1
June | 27 | 9AM to 10AM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
June | 27 | 10AM to 11AM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
June | 27 | 11AM to 12PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
June | 27 | 12PM to 1PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
June | 27 | 1PM to 2PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
June | 27 | 2PM to 3PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
June | 27 | 3PM to 4PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
June | 27 | 4PM to 5PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
June | 27 | 5PM to 6PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
June | 27 | 6PM to 7PM | 87.1 | 72.2 | 66 | 100 | 36.61 | 0.0694 | 0.64 | 14.62 | 1
June | 27 | 7PM to 8PM | 82.9 | 69.9 | 64 | 93.2 | 34.52 | 0.0699 | 0.6 | 14.49 | 1
June | 27 | 8PM to 9PM | 81 | 69.8 | 64.9 | 96.2 | 34.51 | 0.0702 | 0.62 | 14.44 | 1
June | 27 | 9PM to 10PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
June | 27 | 10PM to 11PM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
June | 27 | 11PM to 12AM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
June | 28 | 12AM to 1AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
June | 28 | 1AM to 2AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
June | 28 | 2AM to 3AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
June | 28 | 3AM to 4AM | 73.9 | 67.8 | 64.9 | 96.2 | 32.78 | 0.0711 | 0.62 | 14.26 | 1
June | 28 | 4AM to 5AM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
June | 28 | 5AM to 6AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
June | 28 | 6AM to 7AM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
June | 28 | 7AM to 8AM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
June | 28 | 8AM to 9AM | 80.1 | 72.2 | 69.1 | 111.4 | 36.67 | 0.0702 | 0.72 | 14.47 | 1
June | 28 | 9AM to 10AM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
June | 28 | 10AM to 11AM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
June | 28 | 11AM to 12PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
June | 28 | 12PM to 1PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
June | 28 | 1PM to 2PM | 88 | 74.3 | 69.1 | 111.4 | 38.63 | 0.0692 | 0.72 | 14.68 | 1
June | 28 | 2PM to 3PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
June | 28 | 3PM to 4PM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
June | 28 | 4PM to 5PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
June | 28 | 5PM to 6PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
June | 28 | 6PM to 7PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
June | 28 | 7PM to 8PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
June | 28 | 8PM to 9PM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
June | 28 | 9PM to 10PM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
June | 28 | 10PM to 11PM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
June | 28 | 11PM to 12AM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
June | 29 | 12AM to 1AM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
June | 29 | 1AM to 2AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
June | 29 | 2AM to 3AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
June | 29 | 3AM to 4AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
June | 29 | 4AM to 5AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
June | 29 | 5AM to 6AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
June | 29 | 6AM to 7AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
June | 29 | 7AM to 8AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
June | 29 | 8AM to 9AM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
June | 29 | 9AM to 10AM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
June | 29 | 10AM to 11AM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
June | 29 | 11AM to 12PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
June | 29 | 12PM to 1PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
June | 29 | 1PM to 2PM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
June | 29 | 2PM to 3PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
June | 29 | 3PM to 4PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
June | 29 | 4PM to 5PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
June | 29 | 5PM to 6PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
June | 29 | 6PM to 7PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
June | 29 | 7PM to 8PM | 82 | 70.1 | 64.9 | 96.2 | 34.78 | 0.07 | 0.62 | 14.47 | 1
June | 29 | 8PM to 9PM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
June | 29 | 9PM to 10PM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
June | 29 | 10PM to 11PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
June | 29 | 11PM to 12AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
June | 30 | 12AM to 1AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
June | 30 | 1AM to 2AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
June | 30 | 2AM to 3AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
June | 30 | 3AM to 4AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
June | 30 | 4AM to 5AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
June | 30 | 5AM to 6AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
June | 30 | 6AM to 7AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
June | 30 | 7AM to 8AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
June | 30 | 8AM to 9AM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
June | 30 | 9AM to 10AM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
June | 30 | 10AM to 11AM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
June | 30 | 11AM to 12PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
June | 30 | 12PM to 1PM | 88 | 74.3 | 69.1 | 111.4 | 38.63 | 0.0692 | 0.72 | 14.68 | 1
June | 30 | 1PM to 2PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
June | 30 | 2PM to 3PM | 91.9 | 72.9 | 64.9 | 96.2 | 37.21 | 0.0688 | 0.62 | 14.74 | 1
June | 30 | 3PM to 4PM | 75.9 | 67.1 | 63 | 89.6 | 32.24 | 0.0709 | 0.58 | 14.29 | 1
June | 30 | 4PM to 5PM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
June | 30 | 5PM to 6PM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
June | 30 | 6PM to 7PM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
June | 30 | 7PM to 8PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
June | 30 | 8PM to 9PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
June | 30 | 9PM to 10PM | 72.7 | 70 | 68.9 | 110.7 | 34.74 | 0.0712 | 0.71 | 14.27 | 1
June | 30 | 10PM to 11PM | 72.5 | 69.8 | 68.7 | 110 | 34.58 | 0.0712 | 0.71 | 14.26 | 1
June | 30 | 11PM to 12AM | 72.1 | 69.6 | 68.5 | 109.3 | 34.38 | 0.0713 | 0.7 | 14.25 | 1
July | 1 | 12AM to 1AM | 72 | 69.6 | 68.5 | 109.3 | 34.34 | 0.0713 | 0.7 | 14.25 | 1
July | 1 | 1AM to 2AM | 71.6 | 69.3 | 68.4 | 108.6 | 34.14 | 0.0713 | 0.7 | 14.23 | 1
July | 1 | 2AM to 3AM | 71.4 | 69.1 | 68.2 | 107.9 | 33.99 | 0.0714 | 0.69 | 14.23 | 1
July | 1 | 3AM to 4AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 1 | 4AM to 5AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 1 | 5AM to 6AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
July | 1 | 6AM to 7AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
July | 1 | 7AM to 8AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
July | 1 | 8AM to 9AM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
July | 1 | 9AM to 10AM | 82.9 | 74.9 | 72 | 123.2 | 39.23 | 0.0698 | 0.79 | 14.59 | 1
July | 1 | 10AM to 11AM | 86 | 75.7 | 72 | 123.2 | 39.99 | 0.0694 | 0.79 | 14.67 | 1
July | 1 | 11AM to 12PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
July | 1 | 12PM to 1PM | 89.1 | 75.9 | 71.1 | 119.4 | 40.15 | 0.069 | 0.77 | 14.74 | 1
July | 1 | 1PM to 2PM | 82 | 73.7 | 70.5 | 117.2 | 38.06 | 0.0699 | 0.75 | 14.54 | 1
July | 1 | 2PM to 3PM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
July | 1 | 3PM to 4PM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
July | 1 | 4PM to 5PM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
July | 1 | 5PM to 6PM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
July | 1 | 6PM to 7PM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
July | 1 | 7PM to 8PM | 68 | 66.6 | 66 | 100 | 31.91 | 0.0719 | 0.64 | 14.11 | 1
July | 1 | 8PM to 9PM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
July | 1 | 9PM to 10PM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
July | 1 | 10PM to 11PM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
July | 1 | 11PM to 12AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
July | 2 | 12AM to 1AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
July | 2 | 1AM to 2AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
July | 2 | 2AM to 3AM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
July | 2 | 3AM to 4AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
July | 2 | 4AM to 5AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
July | 2 | 5AM to 6AM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
July | 2 | 6AM to 7AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
July | 2 | 7AM to 8AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
July | 2 | 8AM to 9AM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
July | 2 | 9AM to 10AM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
July | 2 | 10AM to 11AM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
July | 2 | 11AM to 12PM | 84 | 73.3 | 69.1 | 111.4 | 37.65 | 0.0697 | 0.72 | 14.58 | 1
July | 2 | 12PM to 1PM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 2 | 1PM to 2PM | 84 | 72.6 | 68 | 107.2 | 37 | 0.0697 | 0.69 | 14.56 | 1
July | 2 | 2PM to 3PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
July | 2 | 3PM to 4PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
July | 2 | 4PM to 5PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
July | 2 | 5PM to 6PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
July | 2 | 6PM to 7PM | 82.9 | 68.7 | 62.1 | 86.8 | 33.52 | 0.07 | 0.56 | 14.47 | 1
July | 2 | 7PM to 8PM | 78.1 | 66.6 | 61 | 83.5 | 31.81 | 0.0706 | 0.54 | 14.33 | 1
July | 2 | 8PM to 9PM | 73.9 | 65.3 | 61 | 83.5 | 30.79 | 0.0712 | 0.54 | 14.22 | 1
July | 2 | 9PM to 10PM | 73 | 64.5 | 60.1 | 80.8 | 30.15 | 0.0713 | 0.52 | 14.18 | 1
July | 2 | 10PM to 11PM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
July | 2 | 11PM to 12AM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
July | 3 | 12AM to 1AM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
July | 3 | 1AM to 2AM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
July | 3 | 2AM to 3AM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
July | 3 | 3AM to 4AM | 64 | 62 | 61 | 83.5 | 28.36 | 0.0725 | 0.54 | 13.95 | 1
July | 3 | 4AM to 5AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
July | 3 | 5AM to 6AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
July | 3 | 6AM to 7AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
July | 3 | 7AM to 8AM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
July | 3 | 8AM to 9AM | 78.1 | 69 | 64.9 | 96.2 | 33.8 | 0.0706 | 0.62 | 14.37 | 1
July | 3 | 9AM to 10AM | 78.1 | 70.2 | 66.9 | 103.2 | 34.9 | 0.0705 | 0.67 | 14.39 | 1
July | 3 | 10AM to 11AM | 80.1 | 70.2 | 66 | 100 | 34.88 | 0.0703 | 0.64 | 14.43 | 1
July | 3 | 11AM to 12PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
July | 3 | 12PM to 1PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
July | 3 | 1PM to 2PM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
July | 3 | 2PM to 3PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
July | 3 | 3PM to 4PM | 84.9 | 71 | 64.9 | 96.2 | 35.49 | 0.0697 | 0.62 | 14.55 | 1
July | 3 | 4PM to 5PM | 86 | 70.1 | 63 | 89.6 | 34.72 | 0.0696 | 0.58 | 14.56 | 1
July | 3 | 5PM to 6PM | 84.9 | 69.8 | 63 | 89.6 | 34.45 | 0.0697 | 0.58 | 14.53 | 1
July | 3 | 6PM to 7PM | 82.9 | 68.1 | 61 | 83.5 | 33 | 0.07 | 0.54 | 14.46 | 1
July | 3 | 7PM to 8PM | 80.1 | 67.2 | 61 | 83.5 | 32.29 | 0.0704 | 0.54 | 14.38 | 1
July | 3 | 8PM to 9PM | 79 | 66.9 | 61 | 83.5 | 32.03 | 0.0705 | 0.54 | 14.35 | 1
July | 3 | 9PM to 10PM | 78.1 | 66.6 | 61 | 83.5 | 31.81 | 0.0706 | 0.54 | 14.33 | 1
July | 3 | 10PM to 11PM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
July | 3 | 11PM to 12AM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
July | 4 | 12AM to 1AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
July | 4 | 1AM to 2AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
July | 4 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
July | 4 | 3AM to 4AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
July | 4 | 4AM to 5AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
July | 4 | 5AM to 6AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
July | 4 | 6AM to 7AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 4 | 7AM to 8AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 4 | 8AM to 9AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
July | 4 | 9AM to 10AM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
July | 4 | 10AM to 11AM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
July | 4 | 11AM to 12PM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 4 | 12PM to 1PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
July | 4 | 1PM to 2PM | 89.1 | 72.8 | 66 | 100 | 37.1 | 0.0691 | 0.64 | 14.67 | 1
July | 4 | 2PM to 3PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
July | 4 | 3PM to 4PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
July | 4 | 4PM to 5PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
July | 4 | 5PM to 6PM | 87.1 | 72.2 | 66 | 100 | 36.61 | 0.0694 | 0.64 | 14.62 | 1
July | 4 | 6PM to 7PM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
July | 4 | 7PM to 8PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
July | 4 | 8PM to 9PM | 81 | 71.8 | 68 | 107.2 | 36.24 | 0.0701 | 0.69 | 14.48 | 1
July | 4 | 9PM to 10PM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
July | 4 | 10PM to 11PM | 79 | 72.5 | 70 | 115 | 36.96 | 0.0703 | 0.74 | 14.45 | 1
July | 4 | 11PM to 12AM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
July | 5 | 12AM to 1AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
July | 5 | 1AM to 2AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 5 | 2AM to 3AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 5 | 3AM to 4AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
July | 5 | 4AM to 5AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 5 | 5AM to 6AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 5 | 6AM to 7AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
July | 5 | 7AM to 8AM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
July | 5 | 8AM to 9AM | 82.9 | 74.3 | 71.1 | 119.4 | 38.63 | 0.0698 | 0.77 | 14.57 | 1
July | 5 | 9AM to 10AM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
July | 5 | 10AM to 11AM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
July | 5 | 11AM to 12PM | 89.1 | 72.8 | 66 | 100 | 37.1 | 0.0691 | 0.64 | 14.67 | 1
July | 5 | 12PM to 1PM | 90 | 73 | 66 | 100 | 37.32 | 0.069 | 0.64 | 14.7 | 1
July | 5 | 1PM to 2PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
July | 5 | 2PM to 3PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
July | 5 | 3PM to 4PM | 91 | 73.3 | 66 | 100 | 37.59 | 0.0689 | 0.64 | 14.73 | 1
July | 5 | 4PM to 5PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
July | 5 | 5PM to 6PM | 89.1 | 73.3 | 66.9 | 103.2 | 37.61 | 0.0691 | 0.67 | 14.68 | 1
July | 5 | 6PM to 7PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
July | 5 | 7PM to 8PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
July | 5 | 8PM to 9PM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
July | 5 | 9PM to 10PM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
July | 5 | 10PM to 11PM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 5 | 11PM to 12AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 6 | 12AM to 1AM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
July | 6 | 1AM to 2AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
July | 6 | 2AM to 3AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 6 | 3AM to 4AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 6 | 4AM to 5AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 6 | 5AM to 6AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 6 | 6AM to 7AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
July | 6 | 7AM to 8AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 6 | 8AM to 9AM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
July | 6 | 9AM to 10AM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 6 | 10AM to 11AM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
July | 6 | 11AM to 12PM | 89.1 | 75.9 | 71.1 | 119.4 | 40.15 | 0.069 | 0.77 | 14.74 | 1
July | 6 | 12PM to 1PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
July | 6 | 1PM to 2PM | 91.9 | 75.9 | 70 | 115 | 40.17 | 0.0687 | 0.74 | 14.8 | 1
July | 6 | 2PM to 3PM | 91.9 | 74.1 | 66.9 | 103.2 | 38.32 | 0.0687 | 0.67 | 14.76 | 1
July | 6 | 3PM to 4PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
July | 6 | 4PM to 5PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
July | 6 | 5PM to 6PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
July | 6 | 6PM to 7PM | 89.1 | 75.2 | 70 | 115 | 39.45 | 0.069 | 0.74 | 14.72 | 1
July | 6 | 7PM to 8PM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
July | 6 | 8PM to 9PM | 82.9 | 74.3 | 71.1 | 119.4 | 38.63 | 0.0698 | 0.77 | 14.57 | 1
July | 6 | 9PM to 10PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
July | 6 | 10PM to 11PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
July | 6 | 11PM to 12AM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
July | 7 | 12AM to 1AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 7 | 1AM to 2AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 7 | 2AM to 3AM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
July | 7 | 3AM to 4AM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
July | 7 | 4AM to 5AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
July | 7 | 5AM to 6AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
July | 7 | 6AM to 7AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
July | 7 | 7AM to 8AM | 80.1 | 74.2 | 72 | 123.2 | 38.52 | 0.0701 | 0.79 | 14.51 | 1
July | 7 | 8AM to 9AM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
July | 7 | 9AM to 10AM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
July | 7 | 10AM to 11AM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
July | 7 | 11AM to 12PM | 91.9 | 77.2 | 72 | 123.2 | 41.46 | 0.0686 | 0.79 | 14.83 | 1
July | 7 | 12PM to 1PM | 93 | 75.7 | 69.1 | 111.4 | 39.87 | 0.0686 | 0.72 | 14.82 | 1
July | 7 | 1PM to 2PM | 93.9 | 74.6 | 66.9 | 103.2 | 38.81 | 0.0685 | 0.67 | 14.81 | 1
July | 7 | 2PM to 3PM | 95 | 74.9 | 66.9 | 103.2 | 39.07 | 0.0684 | 0.67 | 14.84 | 1
July | 7 | 3PM to 4PM | 96.1 | 75.2 | 66.9 | 103.2 | 39.34 | 0.0682 | 0.67 | 14.87 | 1
July | 7 | 4PM to 5PM | 95 | 74.4 | 66 | 100 | 38.56 | 0.0684 | 0.64 | 14.83 | 1
July | 7 | 5PM to 6PM | 93 | 73.8 | 66 | 100 | 38.07 | 0.0686 | 0.64 | 14.78 | 1
July | 7 | 6PM to 7PM | 91.9 | 73.5 | 66 | 100 | 37.81 | 0.0688 | 0.64 | 14.75 | 1
July | 7 | 7PM to 8PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
July | 7 | 8PM to 9PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
July | 7 | 9PM to 10PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
July | 7 | 10PM to 11PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
July | 7 | 11PM to 12AM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
July | 8 | 12AM to 1AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 8 | 1AM to 2AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
July | 8 | 2AM to 3AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
July | 8 | 3AM to 4AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
July | 8 | 4AM to 5AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 8 | 5AM to 6AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 8 | 6AM to 7AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
July | 8 | 7AM to 8AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 8 | 8AM to 9AM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
July | 8 | 9AM to 10AM | 89.1 | 76.5 | 72 | 123.2 | 40.75 | 0.069 | 0.79 | 14.75 | 1
July | 8 | 10AM to 11AM | 93 | 76.2 | 70 | 115 | 40.43 | 0.0685 | 0.74 | 14.83 | 1
July | 8 | 11AM to 12PM | 93.9 | 75.2 | 68 | 107.2 | 39.44 | 0.0685 | 0.69 | 14.83 | 1
July | 8 | 12PM to 1PM | 96.1 | 75.8 | 68 | 107.2 | 39.97 | 0.0682 | 0.69 | 14.89 | 1
July | 8 | 1PM to 2PM | 97 | 76 | 68 | 107.2 | 40.19 | 0.0681 | 0.69 | 14.91 | 1
July | 8 | 2PM to 3PM | 98.1 | 75.2 | 66 | 100 | 39.31 | 0.068 | 0.64 | 14.91 | 1
July | 8 | 3PM to 4PM | 98.1 | 75.2 | 66 | 100 | 39.31 | 0.068 | 0.64 | 14.91 | 1
July | 8 | 4PM to 5PM | 93.9 | 74.1 | 66 | 100 | 38.3 | 0.0685 | 0.64 | 14.8 | 1
July | 8 | 5PM to 6PM | 93.9 | 74.1 | 66 | 100 | 38.3 | 0.0685 | 0.64 | 14.8 | 1
July | 8 | 6PM to 7PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
July | 8 | 7PM to 8PM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
July | 8 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
July | 8 | 9PM to 10PM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
July | 8 | 10PM to 11PM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
July | 8 | 11PM to 12AM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
July | 9 | 12AM to 1AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 9 | 1AM to 2AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 9 | 2AM to 3AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 9 | 3AM to 4AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
July | 9 | 4AM to 5AM | 69.1 | 69.1 | 69.1 | 111.4 | 33.96 | 0.0717 | 0.72 | 14.18 | 1
July | 9 | 5AM to 6AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 9 | 6AM to 7AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
July | 9 | 7AM to 8AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 9 | 8AM to 9AM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
July | 9 | 9AM to 10AM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
July | 9 | 10AM to 11AM | 84.9 | 73.5 | 69.1 | 111.4 | 37.87 | 0.0696 | 0.72 | 14.6 | 1
July | 9 | 11AM to 12PM | 88 | 74.3 | 69.1 | 111.4 | 38.63 | 0.0692 | 0.72 | 14.68 | 1
July | 9 | 12PM to 1PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
July | 9 | 1PM to 2PM | 91 | 74.5 | 68 | 107.2 | 38.73 | 0.0688 | 0.69 | 14.75 | 1
July | 9 | 2PM to 3PM | 93 | 73.8 | 66 | 100 | 38.07 | 0.0686 | 0.64 | 14.78 | 1
July | 9 | 3PM to 4PM | 93 | 73.8 | 66 | 100 | 38.07 | 0.0686 | 0.64 | 14.78 | 1
July | 9 | 4PM to 5PM | 91.9 | 72.9 | 64.9 | 96.2 | 37.21 | 0.0688 | 0.62 | 14.74 | 1
July | 9 | 5PM to 6PM | 91 | 72.7 | 64.9 | 96.2 | 36.99 | 0.0689 | 0.62 | 14.71 | 1
July | 9 | 6PM to 7PM | 90 | 72.4 | 64.9 | 96.2 | 36.73 | 0.069 | 0.62 | 14.68 | 1
July | 9 | 7PM to 8PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
July | 9 | 8PM to 9PM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
July | 9 | 9PM to 10PM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
July | 9 | 10PM to 11PM | 77 | 69.9 | 66.9 | 103.2 | 34.63 | 0.0707 | 0.67 | 14.36 | 1
July | 9 | 11PM to 12AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
July | 10 | 12AM to 1AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
July | 10 | 1AM to 2AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
July | 10 | 2AM to 3AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
July | 10 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
July | 10 | 4AM to 5AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
July | 10 | 5AM to 6AM | 68 | 66.6 | 66 | 100 | 31.91 | 0.0719 | 0.64 | 14.11 | 1
July | 10 | 6AM to 7AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
July | 10 | 7AM to 8AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
July | 10 | 8AM to 9AM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
July | 10 | 9AM to 10AM | 81 | 69.3 | 64 | 93.2 | 34.03 | 0.0702 | 0.6 | 14.43 | 1
July | 10 | 10AM to 11AM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
July | 10 | 11AM to 12PM | 87.1 | 71.1 | 64 | 93.2 | 35.54 | 0.0694 | 0.6 | 14.6 | 1
July | 10 | 12PM to 1PM | 88 | 71.3 | 64 | 93.2 | 35.76 | 0.0693 | 0.6 | 14.62 | 1
July | 10 | 1PM to 2PM | 90 | 71.9 | 64 | 93.2 | 36.25 | 0.0691 | 0.6 | 14.67 | 1
July | 10 | 2PM to 3PM | 90 | 71.9 | 64 | 93.2 | 36.25 | 0.0691 | 0.6 | 14.67 | 1
July | 10 | 3PM to 4PM | 91 | 72.2 | 64 | 93.2 | 36.51 | 0.0689 | 0.6 | 14.7 | 1
July | 10 | 4PM to 5PM | 90 | 71.3 | 63 | 89.6 | 35.69 | 0.0691 | 0.58 | 14.66 | 1
July | 10 | 5PM to 6PM | 87.1 | 71.1 | 64 | 93.2 | 35.54 | 0.0694 | 0.6 | 14.6 | 1
July | 10 | 6PM to 7PM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
July | 10 | 7PM to 8PM | 82.9 | 71.1 | 66 | 100 | 35.59 | 0.0699 | 0.64 | 14.51 | 1
July | 10 | 8PM to 9PM | 80.1 | 70.2 | 66 | 100 | 34.88 | 0.0703 | 0.64 | 14.43 | 1
July | 10 | 9PM to 10PM | 78.1 | 70.2 | 66.9 | 103.2 | 34.9 | 0.0705 | 0.67 | 14.39 | 1
July | 10 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 96.2 | 33.27 | 0.0708 | 0.62 | 14.31 | 1
July | 10 | 11PM to 12AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
July | 11 | 12AM to 1AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
July | 11 | 1AM to 2AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
July | 11 | 2AM to 3AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
July | 11 | 3AM to 4AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
July | 11 | 4AM to 5AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
July | 11 | 5AM to 6AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
July | 11 | 6AM to 7AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 11 | 7AM to 8AM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
July | 11 | 8AM to 9AM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
July | 11 | 9AM to 10AM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
July | 11 | 10AM to 11AM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
July | 11 | 11AM to 12PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
July | 11 | 12PM to 1PM | 87.1 | 71.1 | 64 | 93.2 | 35.54 | 0.0694 | 0.6 | 14.6 | 1
July | 11 | 1PM to 2PM | 90 | 72.4 | 64.9 | 96.2 | 36.73 | 0.069 | 0.62 | 14.68 | 1
July | 11 | 2PM to 3PM | 88 | 71.3 | 64 | 93.2 | 35.76 | 0.0693 | 0.6 | 14.62 | 1
July | 11 | 3PM to 4PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
July | 11 | 4PM to 5PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
July | 11 | 5PM to 6PM | 82.9 | 71.1 | 66 | 100 | 35.59 | 0.0699 | 0.64 | 14.51 | 1
July | 11 | 6PM to 7PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
July | 11 | 7PM to 8PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
July | 11 | 8PM to 9PM | 80.1 | 69.6 | 64.9 | 96.2 | 34.29 | 0.0703 | 0.62 | 14.42 | 1
July | 11 | 9PM to 10PM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
July | 11 | 10PM to 11PM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
July | 11 | 11PM to 12AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
July | 12 | 12AM to 1AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
July | 12 | 1AM to 2AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
July | 12 | 2AM to 3AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
July | 12 | 3AM to 4AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
July | 12 | 4AM to 5AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
July | 12 | 5AM to 6AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
July | 12 | 6AM to 7AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
July | 12 | 7AM to 8AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 12 | 8AM to 9AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
July | 12 | 9AM to 10AM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
July | 12 | 10AM to 11AM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
July | 12 | 11AM to 12PM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
July | 12 | 12PM to 1PM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 12 | 1PM to 2PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
July | 12 | 2PM to 3PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
July | 12 | 3PM to 4PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
July | 12 | 4PM to 5PM | 89.1 | 72.8 | 66 | 100 | 37.1 | 0.0691 | 0.64 | 14.67 | 1
July | 12 | 5PM to 6PM | 90 | 72.4 | 64.9 | 96.2 | 36.73 | 0.069 | 0.62 | 14.68 | 1
July | 12 | 6PM to 7PM | 88 | 72.5 | 66 | 100 | 36.83 | 0.0693 | 0.64 | 14.64 | 1
July | 12 | 7PM to 8PM | 84 | 73.3 | 69.1 | 111.4 | 37.65 | 0.0697 | 0.72 | 14.58 | 1
July | 12 | 8PM to 9PM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
July | 12 | 9PM to 10PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
July | 12 | 10PM to 11PM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
July | 12 | 11PM to 12AM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
July | 13 | 12AM to 1AM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
July | 13 | 1AM to 2AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 13 | 2AM to 3AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 13 | 3AM to 4AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
July | 13 | 4AM to 5AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 13 | 5AM to 6AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 13 | 6AM to 7AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 13 | 7AM to 8AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 13 | 8AM to 9AM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
July | 13 | 9AM to 10AM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 13 | 10AM to 11AM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
July | 13 | 11AM to 12PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
July | 13 | 12PM to 1PM | 91.9 | 74.7 | 68 | 107.2 | 38.95 | 0.0687 | 0.69 | 14.77 | 1
July | 13 | 1PM to 2PM | 91.9 | 74.1 | 66.9 | 103.2 | 38.32 | 0.0687 | 0.67 | 14.76 | 1
July | 13 | 2PM to 3PM | 93.9 | 73.5 | 64.9 | 96.2 | 37.7 | 0.0685 | 0.62 | 14.79 | 1
July | 13 | 3PM to 4PM | 93.9 | 74.1 | 66 | 100 | 38.3 | 0.0685 | 0.64 | 14.8 | 1
July | 13 | 4PM to 5PM | 93.9 | 72.4 | 63 | 89.6 | 36.66 | 0.0686 | 0.58 | 14.77 | 1
July | 13 | 5PM to 6PM | 93 | 72.7 | 64 | 93.2 | 37 | 0.0687 | 0.6 | 14.76 | 1
July | 13 | 6PM to 7PM | 80.1 | 71.5 | 68 | 107.2 | 36.02 | 0.0702 | 0.69 | 14.46 | 1
July | 13 | 7PM to 8PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
July | 13 | 8PM to 9PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 13 | 9PM to 10PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 13 | 10PM to 11PM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
July | 13 | 11PM to 12AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
July | 14 | 12AM to 1AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
July | 14 | 1AM to 2AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
July | 14 | 2AM to 3AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
July | 14 | 3AM to 4AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
July | 14 | 4AM to 5AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
July | 14 | 5AM to 6AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
July | 14 | 6AM to 7AM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
July | 14 | 7AM to 8AM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
July | 14 | 8AM to 9AM | 84 | 72.6 | 68 | 107.2 | 37 | 0.0697 | 0.69 | 14.56 | 1
July | 14 | 9AM to 10AM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
July | 14 | 10AM to 11AM | 89.1 | 75.2 | 70 | 115 | 39.45 | 0.069 | 0.74 | 14.72 | 1
July | 14 | 11AM to 12PM | 91.9 | 75.9 | 70 | 115 | 40.17 | 0.0687 | 0.74 | 14.8 | 1
July | 14 | 12PM to 1PM | 93 | 75.7 | 69.1 | 111.4 | 39.87 | 0.0686 | 0.72 | 14.82 | 1
July | 14 | 1PM to 2PM | 93.9 | 75.2 | 68 | 107.2 | 39.44 | 0.0685 | 0.69 | 14.83 | 1
July | 14 | 2PM to 3PM | 95 | 74.9 | 66.9 | 103.2 | 39.07 | 0.0684 | 0.67 | 14.84 | 1
July | 14 | 3PM to 4PM | 93 | 74.4 | 66.9 | 103.2 | 38.58 | 0.0686 | 0.67 | 14.79 | 1
July | 14 | 4PM to 5PM | 93.9 | 74.6 | 66.9 | 103.2 | 38.81 | 0.0685 | 0.67 | 14.81 | 1
July | 14 | 5PM to 6PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
July | 14 | 6PM to 7PM | 84 | 71.4 | 66 | 100 | 35.86 | 0.0698 | 0.64 | 14.54 | 1
July | 14 | 7PM to 8PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
July | 14 | 8PM to 9PM | 82.9 | 70.4 | 64.9 | 96.2 | 35 | 0.0699 | 0.62 | 14.5 | 1
July | 14 | 9PM to 10PM | 82 | 70.8 | 66 | 100 | 35.37 | 0.07 | 0.64 | 14.49 | 1
July | 14 | 10PM to 11PM | 82 | 69.6 | 64 | 93.2 | 34.3 | 0.0701 | 0.6 | 14.46 | 1
July | 14 | 11PM to 12AM | 82 | 69.6 | 64 | 93.2 | 34.3 | 0.0701 | 0.6 | 14.46 | 1
July | 15 | 12AM to 1AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
July | 15 | 1AM to 2AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
July | 15 | 2AM to 3AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
July | 15 | 3AM to 4AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
July | 15 | 4AM to 5AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
July | 15 | 5AM to 6AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
July | 15 | 6AM to 7AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
July | 15 | 7AM to 8AM | 80.1 | 71.5 | 68 | 107.2 | 36.02 | 0.0702 | 0.69 | 14.46 | 1
July | 15 | 8AM to 9AM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
July | 15 | 9AM to 10AM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
July | 15 | 10AM to 11AM | 88 | 76.2 | 72 | 123.2 | 40.48 | 0.0691 | 0.79 | 14.72 | 1
July | 15 | 11AM to 12PM | 91 | 76.4 | 71.1 | 119.4 | 40.64 | 0.0688 | 0.77 | 14.79 | 1
July | 15 | 12PM to 1PM | 91.9 | 76.6 | 71.1 | 119.4 | 40.86 | 0.0687 | 0.77 | 14.81 | 1
July | 15 | 1PM to 2PM | 93 | 76.2 | 70 | 115 | 40.43 | 0.0685 | 0.74 | 14.83 | 1
July | 15 | 2PM to 3PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
July | 15 | 3PM to 4PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
July | 15 | 4PM to 5PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
July | 15 | 5PM to 6PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
July | 15 | 6PM to 7PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
July | 15 | 7PM to 8PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
July | 15 | 8PM to 9PM | 84.9 | 73.5 | 69.1 | 111.4 | 37.87 | 0.0696 | 0.72 | 14.6 | 1
July | 15 | 9PM to 10PM | 84 | 73.3 | 69.1 | 111.4 | 37.65 | 0.0697 | 0.72 | 14.58 | 1
July | 15 | 10PM to 11PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
July | 15 | 11PM to 12AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 16 | 12AM to 1AM | 80.1 | 72.2 | 69.1 | 111.4 | 36.67 | 0.0702 | 0.72 | 14.47 | 1
July | 16 | 1AM to 2AM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
July | 16 | 2AM to 3AM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
July | 16 | 3AM to 4AM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
July | 16 | 4AM to 5AM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
July | 16 | 5AM to 6AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
July | 16 | 6AM to 7AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
July | 16 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
July | 16 | 8AM to 9AM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
July | 16 | 9AM to 10AM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
July | 16 | 10AM to 11AM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
July | 16 | 11AM to 12PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
July | 16 | 12PM to 1PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
July | 16 | 1PM to 2PM | 93 | 73.8 | 66 | 100 | 38.07 | 0.0686 | 0.64 | 14.78 | 1
July | 16 | 2PM to 3PM | 91.9 | 72.4 | 64 | 93.2 | 36.73 | 0.0688 | 0.6 | 14.73 | 1
July | 16 | 3PM to 4PM | 91.9 | 72.4 | 64 | 93.2 | 36.73 | 0.0688 | 0.6 | 14.73 | 1
July | 16 | 4PM to 5PM | 91 | 72.7 | 64.9 | 96.2 | 36.99 | 0.0689 | 0.62 | 14.71 | 1
July | 16 | 5PM to 6PM | 91 | 72.7 | 64.9 | 96.2 | 36.99 | 0.0689 | 0.62 | 14.71 | 1
July | 16 | 6PM to 7PM | 88 | 71.3 | 64 | 93.2 | 35.76 | 0.0693 | 0.6 | 14.62 | 1
July | 16 | 7PM to 8PM | 86 | 70.7 | 64 | 93.2 | 35.27 | 0.0696 | 0.6 | 14.57 | 1
July | 16 | 8PM to 9PM | 84.9 | 70.4 | 64 | 93.2 | 35.01 | 0.0697 | 0.6 | 14.54 | 1
July | 16 | 9PM to 10PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
July | 16 | 10PM to 11PM | 82.9 | 69.9 | 64 | 93.2 | 34.52 | 0.0699 | 0.6 | 14.49 | 1
July | 16 | 11PM to 12AM | 81 | 69.3 | 64 | 93.2 | 34.03 | 0.0702 | 0.6 | 14.43 | 1
July | 17 | 12AM to 1AM | 77 | 69.9 | 66.9 | 103.2 | 34.63 | 0.0707 | 0.67 | 14.36 | 1
July | 17 | 1AM to 2AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
July | 17 | 2AM to 3AM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
July | 17 | 3AM to 4AM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
July | 17 | 4AM to 5AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
July | 17 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
July | 17 | 6AM to 7AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
July | 17 | 7AM to 8AM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
July | 17 | 8AM to 9AM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
July | 17 | 9AM to 10AM | 82 | 71.4 | 66.9 | 103.2 | 35.88 | 0.07 | 0.67 | 14.5 | 1
July | 17 | 10AM to 11AM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
July | 17 | 11AM to 12PM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
July | 17 | 12PM to 1PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
July | 17 | 1PM to 2PM | 84.9 | 71 | 64.9 | 96.2 | 35.49 | 0.0697 | 0.62 | 14.55 | 1
July | 17 | 2PM to 3PM | 87.1 | 72.2 | 66 | 100 | 36.61 | 0.0694 | 0.64 | 14.62 | 1
July | 17 | 3PM to 4PM | 90 | 71.3 | 63 | 89.6 | 35.69 | 0.0691 | 0.58 | 14.66 | 1
July | 17 | 4PM to 5PM | 91 | 71.6 | 63 | 89.6 | 35.96 | 0.0689 | 0.58 | 14.69 | 1
July | 17 | 5PM to 6PM | 89.1 | 71 | 63 | 89.6 | 35.47 | 0.0692 | 0.58 | 14.64 | 1
July | 17 | 6PM to 7PM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
July | 17 | 7PM to 8PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
July | 17 | 8PM to 9PM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
July | 17 | 9PM to 10PM | 78.1 | 68.4 | 64 | 93.2 | 33.33 | 0.0706 | 0.6 | 14.36 | 1
July | 17 | 10PM to 11PM | 77 | 68.7 | 64.9 | 96.2 | 33.54 | 0.0707 | 0.62 | 14.34 | 1
July | 17 | 11PM to 12AM | 73.9 | 67.8 | 64.9 | 96.2 | 32.78 | 0.0711 | 0.62 | 14.26 | 1
July | 18 | 12AM to 1AM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
July | 18 | 1AM to 2AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
July | 18 | 2AM to 3AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
July | 18 | 3AM to 4AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
July | 18 | 4AM to 5AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
July | 18 | 5AM to 6AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
July | 18 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
July | 18 | 7AM to 8AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
July | 18 | 8AM to 9AM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
July | 18 | 9AM to 10AM | 80.1 | 69.6 | 64.9 | 96.2 | 34.29 | 0.0703 | 0.62 | 14.42 | 1
July | 18 | 10AM to 11AM | 82 | 70.8 | 66 | 100 | 35.37 | 0.07 | 0.64 | 14.49 | 1
July | 18 | 11AM to 12PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
July | 18 | 12PM to 1PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
July | 18 | 1PM to 2PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
July | 18 | 2PM to 3PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
July | 18 | 3PM to 4PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
July | 18 | 4PM to 5PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
July | 18 | 5PM to 6PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
July | 18 | 6PM to 7PM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
July | 18 | 7PM to 8PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
July | 18 | 8PM to 9PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 18 | 9PM to 10PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 18 | 10PM to 11PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 18 | 11PM to 12AM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
July | 19 | 12AM to 1AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
July | 19 | 1AM to 2AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
July | 19 | 2AM to 3AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 19 | 3AM to 4AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 19 | 4AM to 5AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
July | 19 | 5AM to 6AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
July | 19 | 6AM to 7AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
July | 19 | 7AM to 8AM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
July | 19 | 8AM to 9AM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
July | 19 | 9AM to 10AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
July | 19 | 10AM to 11AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
July | 19 | 11AM to 12PM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
July | 19 | 12PM to 1PM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
July | 19 | 1PM to 2PM | 84.9 | 73.5 | 69.1 | 111.4 | 37.87 | 0.0696 | 0.72 | 14.6 | 1
July | 19 | 2PM to 3PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
July | 19 | 3PM to 4PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
July | 19 | 4PM to 5PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
July | 19 | 5PM to 6PM | 89.1 | 73.3 | 66.9 | 103.2 | 37.61 | 0.0691 | 0.67 | 14.68 | 1
July | 19 | 6PM to 7PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
July | 19 | 7PM to 8PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
July | 19 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
July | 19 | 9PM to 10PM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
July | 19 | 10PM to 11PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 19 | 11PM to 12AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 20 | 12AM to 1AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 20 | 1AM to 2AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
July | 20 | 2AM to 3AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 20 | 3AM to 4AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
July | 20 | 4AM to 5AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
July | 20 | 5AM to 6AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
July | 20 | 6AM to 7AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 20 | 7AM to 8AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
July | 20 | 8AM to 9AM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
July | 20 | 9AM to 10AM | 82 | 71.4 | 66.9 | 103.2 | 35.88 | 0.07 | 0.67 | 14.5 | 1
July | 20 | 10AM to 11AM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
July | 20 | 11AM to 12PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
July | 20 | 12PM to 1PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
July | 20 | 1PM to 2PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
July | 20 | 2PM to 3PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
July | 20 | 3PM to 4PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
July | 20 | 4PM to 5PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
July | 20 | 5PM to 6PM | 90 | 73 | 66 | 100 | 37.32 | 0.069 | 0.64 | 14.7 | 1
July | 20 | 6PM to 7PM | 89.1 | 72.8 | 66 | 100 | 37.1 | 0.0691 | 0.64 | 14.67 | 1
July | 20 | 7PM to 8PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
July | 20 | 8PM to 9PM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
July | 20 | 9PM to 10PM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
July | 20 | 10PM to 11PM | 79 | 70.5 | 66.9 | 103.2 | 35.12 | 0.0704 | 0.67 | 14.41 | 1
July | 20 | 11PM to 12AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
July | 21 | 12AM to 1AM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
July | 21 | 1AM to 2AM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
July | 21 | 2AM to 3AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
July | 21 | 3AM to 4AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
July | 21 | 4AM to 5AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
July | 21 | 5AM to 6AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
July | 21 | 6AM to 7AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
July | 21 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
July | 21 | 8AM to 9AM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
July | 21 | 9AM to 10AM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
July | 21 | 10AM to 11AM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
July | 21 | 11AM to 12PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
July | 21 | 12PM to 1PM | 91 | 74.5 | 68 | 107.2 | 38.73 | 0.0688 | 0.69 | 14.75 | 1
July | 21 | 1PM to 2PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
July | 21 | 2PM to 3PM | 91.9 | 74.1 | 66.9 | 103.2 | 38.32 | 0.0687 | 0.67 | 14.76 | 1
July | 21 | 3PM to 4PM | 91.9 | 73.5 | 66 | 100 | 37.81 | 0.0688 | 0.64 | 14.75 | 1
July | 21 | 4PM to 5PM | 93 | 73.8 | 66 | 100 | 38.07 | 0.0686 | 0.64 | 14.78 | 1
July | 21 | 5PM to 6PM | 91.9 | 73.5 | 66 | 100 | 37.81 | 0.0688 | 0.64 | 14.75 | 1
July | 21 | 6PM to 7PM | 89.1 | 72.8 | 66 | 100 | 37.1 | 0.0691 | 0.64 | 14.67 | 1
July | 21 | 7PM to 8PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
July | 21 | 8PM to 9PM | 84 | 71.4 | 66 | 100 | 35.86 | 0.0698 | 0.64 | 14.54 | 1
July | 21 | 9PM to 10PM | 82 | 70.1 | 64.9 | 96.2 | 34.78 | 0.07 | 0.62 | 14.47 | 1
July | 21 | 10PM to 11PM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
July | 21 | 11PM to 12AM | 79 | 68.7 | 64 | 93.2 | 33.55 | 0.0705 | 0.6 | 14.38 | 1
July | 22 | 12AM to 1AM | 77 | 68.7 | 64.9 | 96.2 | 33.54 | 0.0707 | 0.62 | 14.34 | 1
July | 22 | 1AM to 2AM | 77 | 68.7 | 64.9 | 96.2 | 33.54 | 0.0707 | 0.62 | 14.34 | 1
July | 22 | 2AM to 3AM | 73.9 | 67.8 | 64.9 | 96.2 | 32.78 | 0.0711 | 0.62 | 14.26 | 1
July | 22 | 3AM to 4AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
July | 22 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
July | 22 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
July | 22 | 6AM to 7AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
July | 22 | 7AM to 8AM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
July | 22 | 8AM to 9AM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
July | 22 | 9AM to 10AM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
July | 22 | 10AM to 11AM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
July | 22 | 11AM to 12PM | 91 | 75.1 | 69.1 | 111.4 | 39.38 | 0.0688 | 0.72 | 14.76 | 1
July | 22 | 12PM to 1PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
July | 22 | 1PM to 2PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
July | 22 | 2PM to 3PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
July | 22 | 3PM to 4PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
July | 22 | 4PM to 5PM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
July | 22 | 5PM to 6PM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
July | 22 | 6PM to 7PM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
July | 22 | 7PM to 8PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
July | 22 | 8PM to 9PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
July | 22 | 9PM to 10PM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
July | 22 | 10PM to 11PM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 22 | 11PM to 12AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 23 | 12AM to 1AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 23 | 1AM to 2AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
July | 23 | 2AM to 3AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 23 | 3AM to 4AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 23 | 4AM to 5AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
July | 23 | 5AM to 6AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 23 | 6AM to 7AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
July | 23 | 7AM to 8AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
July | 23 | 8AM to 9AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
July | 23 | 9AM to 10AM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
July | 23 | 10AM to 11AM | 82 | 74.1 | 71.1 | 119.4 | 38.41 | 0.0699 | 0.77 | 14.55 | 1
July | 23 | 11AM to 12PM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
July | 23 | 12PM to 1PM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
July | 23 | 1PM to 2PM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
July | 23 | 2PM to 3PM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
July | 23 | 3PM to 4PM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
July | 23 | 4PM to 5PM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 23 | 5PM to 6PM | 84 | 72.6 | 68 | 107.2 | 37 | 0.0697 | 0.69 | 14.56 | 1
July | 23 | 6PM to 7PM | 82.9 | 70.4 | 64.9 | 96.2 | 35 | 0.0699 | 0.62 | 14.5 | 1
July | 23 | 7PM to 8PM | 81 | 69.8 | 64.9 | 96.2 | 34.51 | 0.0702 | 0.62 | 14.44 | 1
July | 23 | 8PM to 9PM | 78.1 | 68.4 | 64 | 93.2 | 33.33 | 0.0706 | 0.6 | 14.36 | 1
July | 23 | 9PM to 10PM | 77 | 68.1 | 64 | 93.2 | 33.06 | 0.0707 | 0.6 | 14.33 | 1
July | 23 | 10PM to 11PM | 75.9 | 67.1 | 63 | 89.6 | 32.24 | 0.0709 | 0.58 | 14.29 | 1
July | 23 | 11PM to 12AM | 75 | 66.8 | 63 | 89.6 | 32.02 | 0.071 | 0.58 | 14.26 | 1
July | 24 | 12AM to 1AM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
July | 24 | 1AM to 2AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
July | 24 | 2AM to 3AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
July | 24 | 3AM to 4AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
July | 24 | 4AM to 5AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
July | 24 | 5AM to 6AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
July | 24 | 6AM to 7AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
July | 24 | 7AM to 8AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
July | 24 | 8AM to 9AM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
July | 24 | 9AM to 10AM | 81 | 68.1 | 62.1 | 86.8 | 33.03 | 0.0702 | 0.56 | 14.41 | 1
July | 24 | 10AM to 11AM | 82 | 69 | 63 | 89.6 | 33.75 | 0.0701 | 0.58 | 14.45 | 1
July | 24 | 11AM to 12PM | 84 | 69 | 62.1 | 86.8 | 33.78 | 0.0698 | 0.56 | 14.5 | 1
July | 24 | 12PM to 1PM | 86 | 69 | 61 | 83.5 | 33.75 | 0.0696 | 0.54 | 14.54 | 1
July | 24 | 1PM to 2PM | 86 | 69 | 61 | 83.5 | 33.75 | 0.0696 | 0.54 | 14.54 | 1
July | 24 | 2PM to 3PM | 87.1 | 69.3 | 61 | 83.5 | 34.01 | 0.0695 | 0.54 | 14.57 | 1
July | 24 | 3PM to 4PM | 88 | 69.6 | 61 | 83.5 | 34.24 | 0.0694 | 0.54 | 14.59 | 1
July | 24 | 4PM to 5PM | 88 | 70.2 | 62.1 | 86.8 | 34.76 | 0.0693 | 0.56 | 14.6 | 1
July | 24 | 5PM to 6PM | 87.1 | 69.3 | 61 | 83.5 | 34.01 | 0.0695 | 0.54 | 14.57 | 1
July | 24 | 6PM to 7PM | 86 | 69 | 61 | 83.5 | 33.75 | 0.0696 | 0.54 | 14.54 | 1
July | 24 | 7PM to 8PM | 84 | 68.4 | 61 | 83.5 | 33.26 | 0.0699 | 0.54 | 14.48 | 1
July | 24 | 8PM to 9PM | 80.1 | 68.4 | 63 | 89.6 | 33.26 | 0.0703 | 0.58 | 14.4 | 1
July | 24 | 9PM to 10PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
July | 24 | 10PM to 11PM | 77 | 65.8 | 60.1 | 80.8 | 31.12 | 0.0708 | 0.52 | 14.29 | 1
July | 24 | 11PM to 12AM | 75 | 63.9 | 57.9 | 74.7 | 29.68 | 0.0711 | 0.48 | 14.22 | 1
July | 25 | 12AM to 1AM | 75 | 64.5 | 59 | 77.7 | 30.15 | 0.0711 | 0.5 | 14.23 | 1
July | 25 | 1AM to 2AM | 72 | 65.3 | 62.1 | 86.8 | 30.82 | 0.0714 | 0.56 | 14.17 | 1
July | 25 | 2AM to 3AM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
July | 25 | 3AM to 4AM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
July | 25 | 4AM to 5AM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
July | 25 | 5AM to 6AM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
July | 25 | 6AM to 7AM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
July | 25 | 7AM to 8AM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
July | 25 | 8AM to 9AM | 75.9 | 68.4 | 64.9 | 96.2 | 33.27 | 0.0708 | 0.62 | 14.31 | 1
July | 25 | 9AM to 10AM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
July | 25 | 10AM to 11AM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
July | 25 | 11AM to 12PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
July | 25 | 12PM to 1PM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 25 | 1PM to 2PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
July | 25 | 2PM to 3PM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
July | 25 | 3PM to 4PM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
July | 25 | 4PM to 5PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
July | 25 | 5PM to 6PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
July | 25 | 6PM to 7PM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
July | 25 | 7PM to 8PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
July | 25 | 8PM to 9PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
July | 25 | 9PM to 10PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
July | 25 | 10PM to 11PM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
July | 25 | 11PM to 12AM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
July | 26 | 12AM to 1AM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
July | 26 | 1AM to 2AM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
July | 26 | 2AM to 3AM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
July | 26 | 3AM to 4AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
July | 26 | 4AM to 5AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
July | 26 | 5AM to 6AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
July | 26 | 6AM to 7AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
July | 26 | 7AM to 8AM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
July | 26 | 8AM to 9AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
July | 26 | 9AM to 10AM | 79 | 75.3 | 73.9 | 132 | 39.62 | 0.0702 | 0.85 | 14.51 | 1
July | 26 | 10AM to 11AM | 82 | 76 | 73.9 | 132 | 40.38 | 0.0698 | 0.85 | 14.59 | 1
July | 26 | 11AM to 12PM | 84 | 76.5 | 73.9 | 132 | 40.87 | 0.0696 | 0.85 | 14.64 | 1
July | 26 | 12PM to 1PM | 84.9 | 76.2 | 73 | 127.9 | 40.46 | 0.0695 | 0.82 | 14.65 | 1
July | 26 | 1PM to 2PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
July | 26 | 2PM to 3PM | 88 | 76.2 | 72 | 123.2 | 40.48 | 0.0691 | 0.79 | 14.72 | 1
July | 26 | 3PM to 4PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
July | 26 | 4PM to 5PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
July | 26 | 5PM to 6PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
July | 26 | 6PM to 7PM | 82 | 75.4 | 73 | 127.9 | 39.75 | 0.0699 | 0.82 | 14.58 | 1
July | 26 | 7PM to 8PM | 78.1 | 74.4 | 73 | 127.9 | 38.76 | 0.0704 | 0.82 | 14.47 | 1
July | 26 | 8PM to 9PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
July | 26 | 9PM to 10PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
July | 26 | 10PM to 11PM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
July | 26 | 11PM to 12AM | 73 | 73 | 73 | 127.9 | 37.51 | 0.071 | 0.82 | 14.33 | 1
July | 27 | 12AM to 1AM | 73 | 73 | 73 | 127.9 | 37.51 | 0.071 | 0.82 | 14.33 | 1
July | 27 | 1AM to 2AM | 73 | 73 | 73 | 127.9 | 37.51 | 0.071 | 0.82 | 14.33 | 1
July | 27 | 2AM to 3AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
July | 27 | 3AM to 4AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
July | 27 | 4AM to 5AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
July | 27 | 5AM to 6AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
July | 27 | 6AM to 7AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
July | 27 | 7AM to 8AM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
July | 27 | 8AM to 9AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
July | 27 | 9AM to 10AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
July | 27 | 10AM to 11AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
July | 27 | 11AM to 12PM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
July | 27 | 12PM to 1PM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
July | 27 | 1PM to 2PM | 77 | 69.4 | 66 | 100 | 34.13 | 0.0707 | 0.64 | 14.35 | 1
July | 27 | 2PM to 3PM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
July | 27 | 3PM to 4PM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
July | 27 | 4PM to 5PM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 27 | 5PM to 6PM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 27 | 6PM to 7PM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 27 | 7PM to 8PM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 27 | 8PM to 9PM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
July | 27 | 9PM to 10PM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
July | 27 | 10PM to 11PM | 69.1 | 69.1 | 69.1 | 111.4 | 33.96 | 0.0717 | 0.72 | 14.18 | 1
July | 27 | 11PM to 12AM | 69.1 | 69.1 | 69.1 | 111.4 | 33.96 | 0.0717 | 0.72 | 14.18 | 1
July | 28 | 12AM to 1AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 28 | 1AM to 2AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 28 | 2AM to 3AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 28 | 3AM to 4AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 4AM to 5AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 5AM to 6AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 6AM to 7AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 7AM to 8AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 8AM to 9AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 9AM to 10AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 10AM to 11AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 11AM to 12PM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 12PM to 1PM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 1PM to 2PM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 2PM to 3PM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 28 | 3PM to 4PM | 66.9 | 66.3 | 66 | 100 | 31.64 | 0.072 | 0.64 | 14.08 | 1
July | 28 | 4PM to 5PM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
July | 28 | 5PM to 6PM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
July | 28 | 6PM to 7PM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
July | 28 | 7PM to 8PM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
July | 28 | 8PM to 9PM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
July | 28 | 9PM to 10PM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
July | 28 | 10PM to 11PM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
July | 28 | 11PM to 12AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
July | 29 | 12AM to 1AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
July | 29 | 1AM to 2AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
July | 29 | 2AM to 3AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
July | 29 | 3AM to 4AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
July | 29 | 4AM to 5AM | 64 | 64 | 64 | 93.2 | 29.87 | 0.0725 | 0.6 | 13.98 | 1
July | 29 | 5AM to 6AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
July | 29 | 6AM to 7AM | 64 | 64 | 64 | 93.2 | 29.87 | 0.0725 | 0.6 | 13.98 | 1
July | 29 | 7AM to 8AM | 64 | 64 | 64 | 93.2 | 29.87 | 0.0725 | 0.6 | 13.98 | 1
July | 29 | 8AM to 9AM | 64 | 64 | 64 | 93.2 | 29.87 | 0.0725 | 0.6 | 13.98 | 1
July | 29 | 9AM to 10AM | 64.9 | 64.9 | 64.9 | 96.2 | 30.57 | 0.0723 | 0.62 | 14.02 | 1
July | 29 | 10AM to 11AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
July | 29 | 11AM to 12PM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 29 | 12PM to 1PM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 29 | 1PM to 2PM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
July | 29 | 2PM to 3PM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
July | 29 | 3PM to 4PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
July | 29 | 4PM to 5PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
July | 29 | 5PM to 6PM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
July | 29 | 6PM to 7PM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
July | 29 | 7PM to 8PM | 70 | 70 | 70 | 115 | 34.74 | 0.0715 | 0.74 | 14.21 | 1
July | 29 | 8PM to 9PM | 69.1 | 69.1 | 69.1 | 111.4 | 33.96 | 0.0717 | 0.72 | 14.18 | 1
July | 29 | 9PM to 10PM | 69.1 | 69.1 | 69.1 | 111.4 | 33.96 | 0.0717 | 0.72 | 14.18 | 1
July | 29 | 10PM to 11PM | 69.1 | 69.1 | 69.1 | 111.4 | 33.96 | 0.0717 | 0.72 | 14.18 | 1
July | 29 | 11PM to 12AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 30 | 12AM to 1AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 30 | 1AM to 2AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
July | 30 | 2AM to 3AM | 70 | 70 | 70 | 115 | 34.74 | 0.0715 | 0.74 | 14.21 | 1
July | 30 | 3AM to 4AM | 70 | 70 | 70 | 115 | 34.74 | 0.0715 | 0.74 | 14.21 | 1
July | 30 | 4AM to 5AM | 70 | 70 | 70 | 115 | 34.74 | 0.0715 | 0.74 | 14.21 | 1
July | 30 | 5AM to 6AM | 70 | 70 | 70 | 115 | 34.74 | 0.0715 | 0.74 | 14.21 | 1
July | 30 | 6AM to 7AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
July | 30 | 7AM to 8AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
July | 30 | 8AM to 9AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
July | 30 | 9AM to 10AM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
July | 30 | 10AM to 11AM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
July | 30 | 11AM to 12PM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
July | 30 | 12PM to 1PM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
July | 30 | 1PM to 2PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
July | 30 | 2PM to 3PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
July | 30 | 3PM to 4PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
July | 30 | 4PM to 5PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
July | 30 | 5PM to 6PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
July | 30 | 6PM to 7PM | 82.9 | 74.9 | 72 | 123.2 | 39.23 | 0.0698 | 0.79 | 14.59 | 1
July | 30 | 7PM to 8PM | 81 | 75.1 | 73 | 127.9 | 39.48 | 0.07 | 0.82 | 14.55 | 1
July | 30 | 8PM to 9PM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
July | 30 | 9PM to 10PM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
July | 30 | 10PM to 11PM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
July | 30 | 11PM to 12AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
July | 31 | 12AM to 1AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
July | 31 | 1AM to 2AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
July | 31 | 2AM to 3AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
July | 31 | 3AM to 4AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
July | 31 | 4AM to 5AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
July | 31 | 5AM to 6AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
July | 31 | 6AM to 7AM | 70 | 70 | 70 | 115 | 34.74 | 0.0715 | 0.74 | 14.21 | 1
July | 31 | 7AM to 8AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
July | 31 | 8AM to 9AM | 78.1 | 74.4 | 73 | 127.9 | 38.76 | 0.0704 | 0.82 | 14.47 | 1
July | 31 | 9AM to 10AM | 81 | 75.8 | 73.9 | 132 | 40.11 | 0.07 | 0.85 | 14.56 | 1
July | 31 | 10AM to 11AM | 82.9 | 75.6 | 73 | 127.9 | 39.97 | 0.0697 | 0.82 | 14.6 | 1
July | 31 | 11AM to 12PM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
July | 31 | 12PM to 1PM | 87.1 | 76 | 72 | 123.2 | 40.26 | 0.0692 | 0.79 | 14.7 | 1
July | 31 | 1PM to 2PM | 87.1 | 76.7 | 73 | 127.9 | 41 | 0.0692 | 0.82 | 14.71 | 1
July | 31 | 2PM to 3PM | 87.1 | 76 | 72 | 123.2 | 40.26 | 0.0692 | 0.79 | 14.7 | 1
July | 31 | 3PM to 4PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
July | 31 | 4PM to 5PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
July | 31 | 5PM to 6PM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
July | 31 | 6PM to 7PM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
July | 31 | 7PM to 8PM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
July | 31 | 8PM to 9PM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
July | 31 | 9PM to 10PM | 78.4 | 73 | 70.9 | 118.6 | 37.4 | 0.0704 | 0.76 | 14.45 | 1
July | 31 | 10PM to 11PM | 77.9 | 72.7 | 70.7 | 117.9 | 37.15 | 0.0705 | 0.76 | 14.43 | 1
July | 31 | 11PM to 12AM | 77.4 | 72.4 | 70.5 | 117.2 | 36.9 | 0.0705 | 0.75 | 14.42 | 1
August | 1 | 12AM to 1AM | 76.6 | 72.2 | 70.5 | 117.2 | 36.73 | 0.0706 | 0.75 | 14.4 | 1
August | 1 | 1AM to 2AM | 76.1 | 72 | 70.3 | 116.4 | 36.48 | 0.0707 | 0.75 | 14.38 | 1
August | 1 | 2AM to 3AM | 75.6 | 71.7 | 70.2 | 115.7 | 36.23 | 0.0708 | 0.74 | 14.36 | 1
August | 1 | 3AM to 4AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 1 | 4AM to 5AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
August | 1 | 5AM to 6AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
August | 1 | 6AM to 7AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 1 | 7AM to 8AM | 79 | 72.5 | 70 | 115 | 36.96 | 0.0703 | 0.74 | 14.45 | 1
August | 1 | 8AM to 9AM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
August | 1 | 9AM to 10AM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 1 | 10AM to 11AM | 90 | 74.9 | 69.1 | 111.4 | 39.11 | 0.0689 | 0.72 | 14.73 | 1
August | 1 | 11AM to 12PM | 91.9 | 74.1 | 66.9 | 103.2 | 38.32 | 0.0687 | 0.67 | 14.76 | 1
August | 1 | 12PM to 1PM | 93 | 74.4 | 66.9 | 103.2 | 38.58 | 0.0686 | 0.67 | 14.79 | 1
August | 1 | 1PM to 2PM | 93 | 74.4 | 66.9 | 103.2 | 38.58 | 0.0686 | 0.67 | 14.79 | 1
August | 1 | 2PM to 3PM | 95 | 74.9 | 66.9 | 103.2 | 39.07 | 0.0684 | 0.67 | 14.84 | 1
August | 1 | 3PM to 4PM | 95 | 74.4 | 66 | 100 | 38.56 | 0.0684 | 0.64 | 14.83 | 1
August | 1 | 4PM to 5PM | 95 | 74.4 | 66 | 100 | 38.56 | 0.0684 | 0.64 | 14.83 | 1
August | 1 | 5PM to 6PM | 91.9 | 74.1 | 66.9 | 103.2 | 38.32 | 0.0687 | 0.67 | 14.76 | 1
August | 1 | 6PM to 7PM | 87.1 | 72.2 | 66 | 100 | 36.61 | 0.0694 | 0.64 | 14.62 | 1
August | 1 | 7PM to 8PM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
August | 1 | 8PM to 9PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
August | 1 | 9PM to 10PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
August | 1 | 10PM to 11PM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
August | 1 | 11PM to 12AM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
August | 2 | 12AM to 1AM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
August | 2 | 1AM to 2AM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
August | 2 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
August | 2 | 3AM to 4AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
August | 2 | 4AM to 5AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
August | 2 | 5AM to 6AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 2 | 6AM to 7AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 2 | 7AM to 8AM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
August | 2 | 8AM to 9AM | 82.9 | 74.3 | 71.1 | 119.4 | 38.63 | 0.0698 | 0.77 | 14.57 | 1
August | 2 | 9AM to 10AM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
August | 2 | 10AM to 11AM | 89.1 | 75.2 | 70 | 115 | 39.45 | 0.069 | 0.74 | 14.72 | 1
August | 2 | 11AM to 12PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
August | 2 | 12PM to 1PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
August | 2 | 1PM to 2PM | 93 | 73.8 | 66 | 100 | 38.07 | 0.0686 | 0.64 | 14.78 | 1
August | 2 | 2PM to 3PM | 93.9 | 73.5 | 64.9 | 96.2 | 37.7 | 0.0685 | 0.62 | 14.79 | 1
August | 2 | 3PM to 4PM | 95 | 73.7 | 64.9 | 96.2 | 37.97 | 0.0684 | 0.62 | 14.82 | 1
August | 2 | 4PM to 5PM | 93.9 | 73.5 | 64.9 | 96.2 | 37.7 | 0.0685 | 0.62 | 14.79 | 1
August | 2 | 5PM to 6PM | 91 | 73.3 | 66 | 100 | 37.59 | 0.0689 | 0.64 | 14.73 | 1
August | 2 | 6PM to 7PM | 91 | 74.5 | 68 | 107.2 | 38.73 | 0.0688 | 0.69 | 14.75 | 1
August | 2 | 7PM to 8PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
August | 2 | 8PM to 9PM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
August | 2 | 9PM to 10PM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
August | 2 | 10PM to 11PM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
August | 2 | 11PM to 12AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 3 | 12AM to 1AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 3 | 1AM to 2AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 3 | 2AM to 3AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 3 | 3AM to 4AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 3 | 4AM to 5AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 3 | 5AM to 6AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 3 | 6AM to 7AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 3 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
August | 3 | 8AM to 9AM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
August | 3 | 9AM to 10AM | 84 | 72.6 | 68 | 107.2 | 37 | 0.0697 | 0.69 | 14.56 | 1
August | 3 | 10AM to 11AM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
August | 3 | 11AM to 12PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
August | 3 | 12PM to 1PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
August | 3 | 1PM to 2PM | 91.9 | 74.7 | 68 | 107.2 | 38.95 | 0.0687 | 0.69 | 14.77 | 1
August | 3 | 2PM to 3PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
August | 3 | 3PM to 4PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
August | 3 | 4PM to 5PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
August | 3 | 5PM to 6PM | 91 | 73.3 | 66 | 100 | 37.59 | 0.0689 | 0.64 | 14.73 | 1
August | 3 | 6PM to 7PM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
August | 3 | 7PM to 8PM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 3 | 8PM to 9PM | 75.9 | 74.5 | 73.9 | 132 | 38.86 | 0.0706 | 0.85 | 14.42 | 1
August | 3 | 9PM to 10PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 3 | 10PM to 11PM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 3 | 11PM to 12AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 4 | 12AM to 1AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 4 | 1AM to 2AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 4 | 2AM to 3AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 4 | 3AM to 4AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
August | 4 | 4AM to 5AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 4 | 5AM to 6AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 4 | 6AM to 7AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 4 | 7AM to 8AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 4 | 8AM to 9AM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 4 | 9AM to 10AM | 82 | 75.4 | 73 | 127.9 | 39.75 | 0.0699 | 0.82 | 14.58 | 1
August | 4 | 10AM to 11AM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
August | 4 | 11AM to 12PM | 87.1 | 76 | 72 | 123.2 | 40.26 | 0.0692 | 0.79 | 14.7 | 1
August | 4 | 12PM to 1PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 4 | 1PM to 2PM | 89.1 | 75.2 | 70 | 115 | 39.45 | 0.069 | 0.74 | 14.72 | 1
August | 4 | 2PM to 3PM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
August | 4 | 3PM to 4PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
August | 4 | 4PM to 5PM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
August | 4 | 5PM to 6PM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
August | 4 | 6PM to 7PM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
August | 4 | 7PM to 8PM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
August | 4 | 8PM to 9PM | 78.1 | 73 | 71.1 | 119.4 | 37.43 | 0.0704 | 0.77 | 14.44 | 1
August | 4 | 9PM to 10PM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 4 | 10PM to 11PM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 4 | 11PM to 12AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 5 | 12AM to 1AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 5 | 1AM to 2AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
August | 5 | 2AM to 3AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 5 | 3AM to 4AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 5 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 5 | 5AM to 6AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 5 | 6AM to 7AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 5 | 7AM to 8AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 5 | 8AM to 9AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 5 | 9AM to 10AM | 78.1 | 73 | 71.1 | 119.4 | 37.43 | 0.0704 | 0.77 | 14.44 | 1
August | 5 | 10AM to 11AM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
August | 5 | 11AM to 12PM | 82 | 74.1 | 71.1 | 119.4 | 38.41 | 0.0699 | 0.77 | 14.55 | 1
August | 5 | 12PM to 1PM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
August | 5 | 1PM to 2PM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
August | 5 | 2PM to 3PM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
August | 5 | 3PM to 4PM | 82 | 75.4 | 73 | 127.9 | 39.75 | 0.0699 | 0.82 | 14.58 | 1
August | 5 | 4PM to 5PM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
August | 5 | 5PM to 6PM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
August | 5 | 6PM to 7PM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
August | 5 | 7PM to 8PM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
August | 5 | 8PM to 9PM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 5 | 9PM to 10PM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 5 | 10PM to 11PM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 5 | 11PM to 12AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 6 | 12AM to 1AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 6 | 1AM to 2AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 6 | 2AM to 3AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 6 | 3AM to 4AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 6 | 4AM to 5AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 6 | 5AM to 6AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 6 | 6AM to 7AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 6 | 7AM to 8AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 6 | 8AM to 9AM | 80.1 | 74.2 | 72 | 123.2 | 38.52 | 0.0701 | 0.79 | 14.51 | 1
August | 6 | 9AM to 10AM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
August | 6 | 10AM to 11AM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
August | 6 | 11AM to 12PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
August | 6 | 12PM to 1PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
August | 6 | 1PM to 2PM | 91 | 75.1 | 69.1 | 111.4 | 39.38 | 0.0688 | 0.72 | 14.76 | 1
August | 6 | 2PM to 3PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
August | 6 | 3PM to 4PM | 91 | 75.1 | 69.1 | 111.4 | 39.38 | 0.0688 | 0.72 | 14.76 | 1
August | 6 | 4PM to 5PM | 90 | 73.5 | 66.9 | 103.2 | 37.83 | 0.069 | 0.67 | 14.71 | 1
August | 6 | 5PM to 6PM | 90 | 73 | 66 | 100 | 37.32 | 0.069 | 0.64 | 14.7 | 1
August | 6 | 6PM to 7PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
August | 6 | 7PM to 8PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
August | 6 | 8PM to 9PM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
August | 6 | 9PM to 10PM | 82 | 74.1 | 71.1 | 119.4 | 38.41 | 0.0699 | 0.77 | 14.55 | 1
August | 6 | 10PM to 11PM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
August | 6 | 11PM to 12AM | 79 | 73.9 | 72 | 123.2 | 38.25 | 0.0703 | 0.79 | 14.48 | 1
August | 7 | 12AM to 1AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 7 | 1AM to 2AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 7 | 2AM to 3AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 7 | 3AM to 4AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
August | 7 | 4AM to 5AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 7 | 5AM to 6AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 7 | 6AM to 7AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 7 | 7AM to 8AM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 7 | 8AM to 9AM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
August | 7 | 9AM to 10AM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
August | 7 | 10AM to 11AM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
August | 7 | 11AM to 12PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
August | 7 | 12PM to 1PM | 90 | 74.9 | 69.1 | 111.4 | 39.11 | 0.0689 | 0.72 | 14.73 | 1
August | 7 | 1PM to 2PM | 89.1 | 75.9 | 71.1 | 119.4 | 40.15 | 0.069 | 0.77 | 14.74 | 1
August | 7 | 2PM to 3PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
August | 7 | 3PM to 4PM | 89.1 | 77.2 | 73 | 127.9 | 41.49 | 0.069 | 0.82 | 14.77 | 1
August | 7 | 4PM to 5PM | 87.1 | 76 | 72 | 123.2 | 40.26 | 0.0692 | 0.79 | 14.7 | 1
August | 7 | 5PM to 6PM | 77 | 69.4 | 66 | 100 | 34.13 | 0.0707 | 0.64 | 14.35 | 1
August | 7 | 6PM to 7PM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 7 | 7PM to 8PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
August | 7 | 8PM to 9PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 7 | 9PM to 10PM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
August | 7 | 10PM to 11PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
August | 7 | 11PM to 12AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 8 | 12AM to 1AM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
August | 8 | 1AM to 2AM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
August | 8 | 2AM to 3AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
August | 8 | 3AM to 4AM | 69.1 | 69.1 | 69.1 | 111.4 | 33.96 | 0.0717 | 0.72 | 14.18 | 1
August | 8 | 4AM to 5AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
August | 8 | 5AM to 6AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
August | 8 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
August | 8 | 7AM to 8AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
August | 8 | 8AM to 9AM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
August | 8 | 9AM to 10AM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 8 | 10AM to 11AM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
August | 8 | 11AM to 12PM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
August | 8 | 12PM to 1PM | 89.1 | 75.9 | 71.1 | 119.4 | 40.15 | 0.069 | 0.77 | 14.74 | 1
August | 8 | 1PM to 2PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
August | 8 | 2PM to 3PM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
August | 8 | 3PM to 4PM | 87.1 | 76 | 72 | 123.2 | 40.26 | 0.0692 | 0.79 | 14.7 | 1
August | 8 | 4PM to 5PM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 8 | 5PM to 6PM | 80.1 | 74.2 | 72 | 123.2 | 38.52 | 0.0701 | 0.79 | 14.51 | 1
August | 8 | 6PM to 7PM | 82 | 76 | 73.9 | 132 | 40.38 | 0.0698 | 0.85 | 14.59 | 1
August | 8 | 7PM to 8PM | 79 | 76 | 75 | 137 | 40.41 | 0.0702 | 0.88 | 14.52 | 1
August | 8 | 8PM to 9PM | 78.1 | 74.4 | 73 | 127.9 | 38.76 | 0.0704 | 0.82 | 14.47 | 1
August | 8 | 9PM to 10PM | 78.1 | 75 | 73.9 | 132 | 39.4 | 0.0703 | 0.85 | 14.48 | 1
August | 8 | 10PM to 11PM | 78.1 | 75 | 73.9 | 132 | 39.4 | 0.0703 | 0.85 | 14.48 | 1
August | 8 | 11PM to 12AM | 78.1 | 75 | 73.9 | 132 | 39.4 | 0.0703 | 0.85 | 14.48 | 1
August | 9 | 12AM to 1AM | 77 | 74.1 | 73 | 127.9 | 38.5 | 0.0705 | 0.82 | 14.44 | 1
August | 9 | 1AM to 2AM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 9 | 2AM to 3AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 9 | 3AM to 4AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 9 | 4AM to 5AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 9 | 5AM to 6AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 9 | 6AM to 7AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 9 | 7AM to 8AM | 79 | 74.6 | 73 | 127.9 | 38.99 | 0.0703 | 0.82 | 14.49 | 1
August | 9 | 8AM to 9AM | 82 | 75.4 | 73 | 127.9 | 39.75 | 0.0699 | 0.82 | 14.58 | 1
August | 9 | 9AM to 10AM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 9 | 10AM to 11AM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
August | 9 | 11AM to 12PM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
August | 9 | 12PM to 1PM | 90 | 74.9 | 69.1 | 111.4 | 39.11 | 0.0689 | 0.72 | 14.73 | 1
August | 9 | 1PM to 2PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
August | 9 | 2PM to 3PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
August | 9 | 3PM to 4PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
August | 9 | 4PM to 5PM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
August | 9 | 5PM to 6PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 9 | 6PM to 7PM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
August | 9 | 7PM to 8PM | 82 | 74.1 | 71.1 | 119.4 | 38.41 | 0.0699 | 0.77 | 14.55 | 1
August | 9 | 8PM to 9PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
August | 9 | 9PM to 10PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
August | 9 | 10PM to 11PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
August | 9 | 11PM to 12AM | 79 | 73.9 | 72 | 123.2 | 38.25 | 0.0703 | 0.79 | 14.48 | 1
August | 10 | 12AM to 1AM | 78.1 | 73 | 71.1 | 119.4 | 37.43 | 0.0704 | 0.77 | 14.44 | 1
August | 10 | 1AM to 2AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 10 | 2AM to 3AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 10 | 3AM to 4AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
August | 10 | 4AM to 5AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 10 | 5AM to 6AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 10 | 6AM to 7AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 10 | 7AM to 8AM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
August | 10 | 8AM to 9AM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
August | 10 | 9AM to 10AM | 87.1 | 76 | 72 | 123.2 | 40.26 | 0.0692 | 0.79 | 14.7 | 1
August | 10 | 10AM to 11AM | 90 | 76.1 | 71.1 | 119.4 | 40.37 | 0.0689 | 0.77 | 14.76 | 1
August | 10 | 11AM to 12PM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
August | 10 | 12PM to 1PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
August | 10 | 1PM to 2PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
August | 10 | 2PM to 3PM | 88 | 75.6 | 71.1 | 119.4 | 39.88 | 0.0691 | 0.77 | 14.71 | 1
August | 10 | 3PM to 4PM | 89.1 | 77.2 | 73 | 127.9 | 41.49 | 0.069 | 0.82 | 14.77 | 1
August | 10 | 4PM to 5PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
August | 10 | 5PM to 6PM | 89.1 | 75.2 | 70 | 115 | 39.45 | 0.069 | 0.74 | 14.72 | 1
August | 10 | 6PM to 7PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
August | 10 | 7PM to 8PM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
August | 10 | 8PM to 9PM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
August | 10 | 9PM to 10PM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 10 | 10PM to 11PM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 10 | 11PM to 12AM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
August | 11 | 12AM to 1AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 11 | 1AM to 2AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 11 | 2AM to 3AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 11 | 3AM to 4AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 11 | 4AM to 5AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 11 | 5AM to 6AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 11 | 6AM to 7AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 11 | 7AM to 8AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 11 | 8AM to 9AM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 11 | 9AM to 10AM | 79 | 74.6 | 73 | 127.9 | 38.99 | 0.0703 | 0.82 | 14.49 | 1
August | 11 | 10AM to 11AM | 82 | 75.4 | 73 | 127.9 | 39.75 | 0.0699 | 0.82 | 14.58 | 1
August | 11 | 11AM to 12PM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
August | 11 | 12PM to 1PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 11 | 1PM to 2PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
August | 11 | 2PM to 3PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
August | 11 | 3PM to 4PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
August | 11 | 4PM to 5PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 11 | 5PM to 6PM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 11 | 6PM to 7PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 11 | 7PM to 8PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 11 | 8PM to 9PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 11 | 9PM to 10PM | 75.9 | 74.5 | 73.9 | 132 | 38.86 | 0.0706 | 0.85 | 14.42 | 1
August | 11 | 10PM to 11PM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 11 | 11PM to 12AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 12 | 12AM to 1AM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
August | 12 | 1AM to 2AM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
August | 12 | 2AM to 3AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 12 | 3AM to 4AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 12 | 4AM to 5AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 12 | 5AM to 6AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 12 | 6AM to 7AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 12 | 7AM to 8AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 12 | 8AM to 9AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 12 | 9AM to 10AM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
August | 12 | 10AM to 11AM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
August | 12 | 11AM to 12PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
August | 12 | 12PM to 1PM | 84 | 73.3 | 69.1 | 111.4 | 37.65 | 0.0697 | 0.72 | 14.58 | 1
August | 12 | 1PM to 2PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
August | 12 | 2PM to 3PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
August | 12 | 3PM to 4PM | 89.1 | 74 | 68 | 107.2 | 38.24 | 0.0691 | 0.69 | 14.7 | 1
August | 12 | 4PM to 5PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
August | 12 | 5PM to 6PM | 88 | 72.5 | 66 | 100 | 36.83 | 0.0693 | 0.64 | 14.64 | 1
August | 12 | 6PM to 7PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
August | 12 | 7PM to 8PM | 84 | 72.6 | 68 | 107.2 | 37 | 0.0697 | 0.69 | 14.56 | 1
August | 12 | 8PM to 9PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
August | 12 | 9PM to 10PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
August | 12 | 10PM to 11PM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
August | 12 | 11PM to 12AM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
August | 13 | 12AM to 1AM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
August | 13 | 1AM to 2AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 13 | 2AM to 3AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
August | 13 | 3AM to 4AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
August | 13 | 4AM to 5AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
August | 13 | 5AM to 6AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
August | 13 | 6AM to 7AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 13 | 7AM to 8AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 13 | 8AM to 9AM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
August | 13 | 9AM to 10AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
August | 13 | 10AM to 11AM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
August | 13 | 11AM to 12PM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
August | 13 | 12PM to 1PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
August | 13 | 1PM to 2PM | 87.1 | 72.2 | 66 | 100 | 36.61 | 0.0694 | 0.64 | 14.62 | 1
August | 13 | 2PM to 3PM | 87.1 | 72.2 | 66 | 100 | 36.61 | 0.0694 | 0.64 | 14.62 | 1
August | 13 | 3PM to 4PM | 86 | 71.9 | 66 | 100 | 36.34 | 0.0695 | 0.64 | 14.59 | 1
August | 13 | 4PM to 5PM | 88 | 72.5 | 66 | 100 | 36.83 | 0.0693 | 0.64 | 14.64 | 1
August | 13 | 5PM to 6PM | 88 | 71.3 | 64 | 93.2 | 35.76 | 0.0693 | 0.6 | 14.62 | 1
August | 13 | 6PM to 7PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
August | 13 | 7PM to 8PM | 84.9 | 71 | 64.9 | 96.2 | 35.49 | 0.0697 | 0.62 | 14.55 | 1
August | 13 | 8PM to 9PM | 82.9 | 71.1 | 66 | 100 | 35.59 | 0.0699 | 0.64 | 14.51 | 1
August | 13 | 9PM to 10PM | 82 | 67.3 | 60.1 | 80.8 | 32.36 | 0.0701 | 0.52 | 14.42 | 1
August | 13 | 10PM to 11PM | 80.1 | 70.8 | 66.9 | 103.2 | 35.39 | 0.0703 | 0.67 | 14.44 | 1
August | 13 | 11PM to 12AM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
August | 14 | 12AM to 1AM | 77 | 69.9 | 66.9 | 103.2 | 34.63 | 0.0707 | 0.67 | 14.36 | 1
August | 14 | 1AM to 2AM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
August | 14 | 2AM to 3AM | 78.1 | 69 | 64.9 | 96.2 | 33.8 | 0.0706 | 0.62 | 14.37 | 1
August | 14 | 3AM to 4AM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
August | 14 | 4AM to 5AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
August | 14 | 5AM to 6AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
August | 14 | 6AM to 7AM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
August | 14 | 7AM to 8AM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
August | 14 | 8AM to 9AM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
August | 14 | 9AM to 10AM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
August | 14 | 10AM to 11AM | 84 | 72.6 | 68 | 107.2 | 37 | 0.0697 | 0.69 | 14.56 | 1
August | 14 | 11AM to 12PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
August | 14 | 12PM to 1PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
August | 14 | 1PM to 2PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
August | 14 | 2PM to 3PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
August | 14 | 3PM to 4PM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
August | 14 | 4PM to 5PM | 88 | 74.3 | 69.1 | 111.4 | 38.63 | 0.0692 | 0.72 | 14.68 | 1
August | 14 | 5PM to 6PM | 86 | 73.8 | 69.1 | 111.4 | 38.14 | 0.0694 | 0.72 | 14.63 | 1
August | 14 | 6PM to 7PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
August | 14 | 7PM to 8PM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 14 | 8PM to 9PM | 78.1 | 73 | 71.1 | 119.4 | 37.43 | 0.0704 | 0.77 | 14.44 | 1
August | 14 | 9PM to 10PM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 14 | 10PM to 11PM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 14 | 11PM to 12AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
August | 15 | 12AM to 1AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 15 | 1AM to 2AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 15 | 2AM to 3AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 15 | 3AM to 4AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 15 | 4AM to 5AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 15 | 5AM to 6AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
August | 15 | 6AM to 7AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 15 | 7AM to 8AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 15 | 8AM to 9AM | 78.1 | 73 | 71.1 | 119.4 | 37.43 | 0.0704 | 0.77 | 14.44 | 1
August | 15 | 9AM to 10AM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
August | 15 | 10AM to 11AM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
August | 15 | 11AM to 12PM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
August | 15 | 12PM to 1PM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
August | 15 | 1PM to 2PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
August | 15 | 2PM to 3PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
August | 15 | 3PM to 4PM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
August | 15 | 4PM to 5PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
August | 15 | 5PM to 6PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
August | 15 | 6PM to 7PM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
August | 15 | 7PM to 8PM | 81 | 73.8 | 71.1 | 119.4 | 38.14 | 0.07 | 0.77 | 14.52 | 1
August | 15 | 8PM to 9PM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 15 | 9PM to 10PM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 15 | 10PM to 11PM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 15 | 11PM to 12AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 16 | 12AM to 1AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 16 | 1AM to 2AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 16 | 2AM to 3AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 16 | 3AM to 4AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 16 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 16 | 5AM to 6AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 16 | 6AM to 7AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 16 | 7AM to 8AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 16 | 8AM to 9AM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
August | 16 | 9AM to 10AM | 84.9 | 73.5 | 69.1 | 111.4 | 37.87 | 0.0696 | 0.72 | 14.6 | 1
August | 16 | 10AM to 11AM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
August | 16 | 11AM to 12PM | 88 | 74.3 | 69.1 | 111.4 | 38.63 | 0.0692 | 0.72 | 14.68 | 1
August | 16 | 12PM to 1PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
August | 16 | 1PM to 2PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
August | 16 | 2PM to 3PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
August | 16 | 3PM to 4PM | 91 | 75.7 | 70 | 115 | 39.94 | 0.0688 | 0.74 | 14.78 | 1
August | 16 | 4PM to 5PM | 91.9 | 74.1 | 66.9 | 103.2 | 38.32 | 0.0687 | 0.67 | 14.76 | 1
August | 16 | 5PM to 6PM | 90 | 74.2 | 68 | 107.2 | 38.46 | 0.069 | 0.69 | 14.72 | 1
August | 16 | 6PM to 7PM | 89.1 | 73.3 | 66.9 | 103.2 | 37.61 | 0.0691 | 0.67 | 14.68 | 1
August | 16 | 7PM to 8PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
August | 16 | 8PM to 9PM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
August | 16 | 9PM to 10PM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
August | 16 | 10PM to 11PM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
August | 16 | 11PM to 12AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 17 | 12AM to 1AM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
August | 17 | 1AM to 2AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 17 | 2AM to 3AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 17 | 3AM to 4AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 17 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 17 | 5AM to 6AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 17 | 6AM to 7AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 17 | 7AM to 8AM | 79 | 73.9 | 72 | 123.2 | 38.25 | 0.0703 | 0.79 | 14.48 | 1
August | 17 | 8AM to 9AM | 82.9 | 74.9 | 72 | 123.2 | 39.23 | 0.0698 | 0.79 | 14.59 | 1
August | 17 | 9AM to 10AM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
August | 17 | 10AM to 11AM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
August | 17 | 11AM to 12PM | 89.1 | 75.9 | 71.1 | 119.4 | 40.15 | 0.069 | 0.77 | 14.74 | 1
August | 17 | 12PM to 1PM | 91 | 76.4 | 71.1 | 119.4 | 40.64 | 0.0688 | 0.77 | 14.79 | 1
August | 17 | 1PM to 2PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
August | 17 | 2PM to 3PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
August | 17 | 3PM to 4PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
August | 17 | 4PM to 5PM | 91.9 | 74.7 | 68 | 107.2 | 38.95 | 0.0687 | 0.69 | 14.77 | 1
August | 17 | 5PM to 6PM | 90 | 74.9 | 69.1 | 111.4 | 39.11 | 0.0689 | 0.72 | 14.73 | 1
August | 17 | 6PM to 7PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
August | 17 | 7PM to 8PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 17 | 8PM to 9PM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
August | 17 | 9PM to 10PM | 82 | 74.1 | 71.1 | 119.4 | 38.41 | 0.0699 | 0.77 | 14.55 | 1
August | 17 | 10PM to 11PM | 82 | 74.1 | 71.1 | 119.4 | 38.41 | 0.0699 | 0.77 | 14.55 | 1
August | 17 | 11PM to 12AM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 18 | 12AM to 1AM | 79 | 72.5 | 70 | 115 | 36.96 | 0.0703 | 0.74 | 14.45 | 1
August | 18 | 1AM to 2AM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
August | 18 | 2AM to 3AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 18 | 3AM to 4AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
August | 18 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 18 | 5AM to 6AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 18 | 6AM to 7AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 18 | 7AM to 8AM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
August | 18 | 8AM to 9AM | 82.9 | 74.9 | 72 | 123.2 | 39.23 | 0.0698 | 0.79 | 14.59 | 1
August | 18 | 9AM to 10AM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 18 | 10AM to 11AM | 90 | 74.9 | 69.1 | 111.4 | 39.11 | 0.0689 | 0.72 | 14.73 | 1
August | 18 | 11AM to 12PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
August | 18 | 12PM to 1PM | 93.9 | 72.9 | 64 | 93.2 | 37.22 | 0.0686 | 0.6 | 14.78 | 1
August | 18 | 1PM to 2PM | 91.9 | 73.5 | 66 | 100 | 37.81 | 0.0688 | 0.64 | 14.75 | 1
August | 18 | 2PM to 3PM | 93.9 | 73.5 | 64.9 | 96.2 | 37.7 | 0.0685 | 0.62 | 14.79 | 1
August | 18 | 3PM to 4PM | 95 | 73.7 | 64.9 | 96.2 | 37.97 | 0.0684 | 0.62 | 14.82 | 1
August | 18 | 4PM to 5PM | 93.9 | 72.4 | 63 | 89.6 | 36.66 | 0.0686 | 0.58 | 14.77 | 1
August | 18 | 5PM to 6PM | 93 | 74.4 | 66.9 | 103.2 | 38.58 | 0.0686 | 0.67 | 14.79 | 1
August | 18 | 6PM to 7PM | 91 | 73.8 | 66.9 | 103.2 | 38.1 | 0.0689 | 0.67 | 14.74 | 1
August | 18 | 7PM to 8PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
August | 18 | 8PM to 9PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
August | 18 | 9PM to 10PM | 84.9 | 73.5 | 69.1 | 111.4 | 37.87 | 0.0696 | 0.72 | 14.6 | 1
August | 18 | 10PM to 11PM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
August | 18 | 11PM to 12AM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
August | 19 | 12AM to 1AM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 19 | 1AM to 2AM | 79 | 73.2 | 71.1 | 119.4 | 37.65 | 0.0703 | 0.77 | 14.47 | 1
August | 19 | 2AM to 3AM | 78.1 | 73 | 71.1 | 119.4 | 37.43 | 0.0704 | 0.77 | 14.44 | 1
August | 19 | 3AM to 4AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 19 | 4AM to 5AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 19 | 5AM to 6AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 19 | 6AM to 7AM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 19 | 7AM to 8AM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
August | 19 | 8AM to 9AM | 84.9 | 74.8 | 71.1 | 119.4 | 39.13 | 0.0695 | 0.77 | 14.63 | 1
August | 19 | 9AM to 10AM | 89.1 | 75.9 | 71.1 | 119.4 | 40.15 | 0.069 | 0.77 | 14.74 | 1
August | 19 | 10AM to 11AM | 90 | 75.4 | 70 | 115 | 39.68 | 0.0689 | 0.74 | 14.75 | 1
August | 19 | 11AM to 12PM | 91 | 74.5 | 68 | 107.2 | 38.73 | 0.0688 | 0.69 | 14.75 | 1
August | 19 | 12PM to 1PM | 91.9 | 74.1 | 66.9 | 103.2 | 38.32 | 0.0687 | 0.67 | 14.76 | 1
August | 19 | 1PM to 2PM | 93 | 75 | 68 | 107.2 | 39.22 | 0.0686 | 0.69 | 14.8 | 1
August | 19 | 2PM to 3PM | 91.9 | 75.4 | 69.1 | 111.4 | 39.6 | 0.0687 | 0.72 | 14.79 | 1
August | 19 | 3PM to 4PM | 91 | 75.1 | 69.1 | 111.4 | 39.38 | 0.0688 | 0.72 | 14.76 | 1
August | 19 | 4PM to 5PM | 86 | 77 | 73.9 | 132 | 41.37 | 0.0693 | 0.85 | 14.7 | 1
August | 19 | 5PM to 6PM | 82.9 | 74.9 | 72 | 123.2 | 39.23 | 0.0698 | 0.79 | 14.59 | 1
August | 19 | 6PM to 7PM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
August | 19 | 7PM to 8PM | 80.1 | 74.2 | 72 | 123.2 | 38.52 | 0.0701 | 0.79 | 14.51 | 1
August | 19 | 8PM to 9PM | 79 | 74.6 | 73 | 127.9 | 38.99 | 0.0703 | 0.82 | 14.49 | 1
August | 19 | 9PM to 10PM | 79 | 73.9 | 72 | 123.2 | 38.25 | 0.0703 | 0.79 | 14.48 | 1
August | 19 | 10PM to 11PM | 78.1 | 74.4 | 73 | 127.9 | 38.76 | 0.0704 | 0.82 | 14.47 | 1
August | 19 | 11PM to 12AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 20 | 12AM to 1AM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
August | 20 | 1AM to 2AM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 20 | 2AM to 3AM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 20 | 3AM to 4AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 20 | 4AM to 5AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 20 | 5AM to 6AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 20 | 6AM to 7AM | 75 | 74.2 | 73.9 | 132 | 38.64 | 0.0708 | 0.85 | 14.4 | 1
August | 20 | 7AM to 8AM | 75.9 | 74.5 | 73.9 | 132 | 38.86 | 0.0706 | 0.85 | 14.42 | 1
August | 20 | 8AM to 9AM | 77 | 74.7 | 73.9 | 132 | 39.13 | 0.0705 | 0.85 | 14.45 | 1
August | 20 | 9AM to 10AM | 79 | 75.3 | 73.9 | 132 | 39.62 | 0.0702 | 0.85 | 14.51 | 1
August | 20 | 10AM to 11AM | 80.1 | 75.5 | 73.9 | 132 | 39.89 | 0.0701 | 0.85 | 14.54 | 1
August | 20 | 11AM to 12PM | 86 | 76.4 | 73 | 127.9 | 40.73 | 0.0694 | 0.82 | 14.68 | 1
August | 20 | 12PM to 1PM | 80.1 | 76.3 | 75 | 137 | 40.68 | 0.0701 | 0.88 | 14.55 | 1
August | 20 | 1PM to 2PM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
August | 20 | 2PM to 3PM | 78.1 | 75 | 73.9 | 132 | 39.4 | 0.0703 | 0.85 | 14.48 | 1
August | 20 | 3PM to 4PM | 82.9 | 76.3 | 73.9 | 132 | 40.61 | 0.0697 | 0.85 | 14.61 | 1
August | 20 | 4PM to 5PM | 82 | 76 | 73.9 | 132 | 40.38 | 0.0698 | 0.85 | 14.59 | 1
August | 20 | 5PM to 6PM | 79 | 72.5 | 70 | 115 | 36.96 | 0.0703 | 0.74 | 14.45 | 1
August | 20 | 6PM to 7PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 20 | 7PM to 8PM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 20 | 8PM to 9PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 20 | 9PM to 10PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 20 | 10PM to 11PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 20 | 11PM to 12AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 21 | 12AM to 1AM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
August | 21 | 1AM to 2AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 21 | 2AM to 3AM | 72 | 71.3 | 71.1 | 119.4 | 35.92 | 0.0712 | 0.77 | 14.28 | 1
August | 21 | 3AM to 4AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
August | 21 | 4AM to 5AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
August | 21 | 5AM to 6AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
August | 21 | 6AM to 7AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
August | 21 | 7AM to 8AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 21 | 8AM to 9AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 21 | 9AM to 10AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
August | 21 | 10AM to 11AM | 77 | 74.1 | 73 | 127.9 | 38.5 | 0.0705 | 0.82 | 14.44 | 1
August | 21 | 11AM to 12PM | 79 | 74.6 | 73 | 127.9 | 38.99 | 0.0703 | 0.82 | 14.49 | 1
August | 21 | 12PM to 1PM | 81 | 75.1 | 73 | 127.9 | 39.48 | 0.07 | 0.82 | 14.55 | 1
August | 21 | 1PM to 2PM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
August | 21 | 2PM to 3PM | 86 | 75.7 | 72 | 123.2 | 39.99 | 0.0694 | 0.79 | 14.67 | 1
August | 21 | 3PM to 4PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 21 | 4PM to 5PM | 87.1 | 76 | 72 | 123.2 | 40.26 | 0.0692 | 0.79 | 14.7 | 1
August | 21 | 5PM to 6PM | 86 | 75.7 | 72 | 123.2 | 39.99 | 0.0694 | 0.79 | 14.67 | 1
August | 21 | 6PM to 7PM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
August | 21 | 7PM to 8PM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
August | 21 | 8PM to 9PM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 21 | 9PM to 10PM | 78.1 | 74.4 | 73 | 127.9 | 38.76 | 0.0704 | 0.82 | 14.47 | 1
August | 21 | 10PM to 11PM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 21 | 11PM to 12AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 22 | 12AM to 1AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 22 | 1AM to 2AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 22 | 2AM to 3AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 22 | 3AM to 4AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
August | 22 | 4AM to 5AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 22 | 5AM to 6AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 22 | 6AM to 7AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 22 | 7AM to 8AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 22 | 8AM to 9AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
August | 22 | 9AM to 10AM | 81 | 75.1 | 73 | 127.9 | 39.48 | 0.07 | 0.82 | 14.55 | 1
August | 22 | 10AM to 11AM | 82.9 | 75.6 | 73 | 127.9 | 39.97 | 0.0697 | 0.82 | 14.6 | 1
August | 22 | 11AM to 12PM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
August | 22 | 12PM to 1PM | 84 | 75.2 | 72 | 123.2 | 39.5 | 0.0696 | 0.79 | 14.61 | 1
August | 22 | 1PM to 2PM | 86 | 75.7 | 72 | 123.2 | 39.99 | 0.0694 | 0.79 | 14.67 | 1
August | 22 | 2PM to 3PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 22 | 3PM to 4PM | 86 | 75.1 | 71.1 | 119.4 | 39.39 | 0.0694 | 0.77 | 14.65 | 1
August | 22 | 4PM to 5PM | 82.9 | 75.6 | 73 | 127.9 | 39.97 | 0.0697 | 0.82 | 14.6 | 1
August | 22 | 5PM to 6PM | 84 | 75.9 | 73 | 127.9 | 40.24 | 0.0696 | 0.82 | 14.63 | 1
August | 22 | 6PM to 7PM | 82 | 75.4 | 73 | 127.9 | 39.75 | 0.0699 | 0.82 | 14.58 | 1
August | 22 | 7PM to 8PM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 22 | 8PM to 9PM | 78.1 | 74.4 | 73 | 127.9 | 38.76 | 0.0704 | 0.82 | 14.47 | 1
August | 22 | 9PM to 10PM | 77 | 74.1 | 73 | 127.9 | 38.5 | 0.0705 | 0.82 | 14.44 | 1
August | 22 | 10PM to 11PM | 77 | 74.1 | 73 | 127.9 | 38.5 | 0.0705 | 0.82 | 14.44 | 1
August | 22 | 11PM to 12AM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
August | 23 | 12AM to 1AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 23 | 1AM to 2AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 23 | 2AM to 3AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 23 | 3AM to 4AM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
August | 23 | 4AM to 5AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
August | 23 | 5AM to 6AM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
August | 23 | 6AM to 7AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
August | 23 | 7AM to 8AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
August | 23 | 8AM to 9AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
August | 23 | 9AM to 10AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 23 | 10AM to 11AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 23 | 11AM to 12PM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 23 | 12PM to 1PM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
August | 23 | 1PM to 2PM | 81 | 75.1 | 73 | 127.9 | 39.48 | 0.07 | 0.82 | 14.55 | 1
August | 23 | 2PM to 3PM | 82 | 74.7 | 72 | 123.2 | 39.01 | 0.0699 | 0.79 | 14.56 | 1
August | 23 | 3PM to 4PM | 80.1 | 74.9 | 73 | 127.9 | 39.26 | 0.0701 | 0.82 | 14.52 | 1
August | 23 | 4PM to 5PM | 81 | 75.1 | 73 | 127.9 | 39.48 | 0.07 | 0.82 | 14.55 | 1
August | 23 | 5PM to 6PM | 79 | 74.6 | 73 | 127.9 | 38.99 | 0.0703 | 0.82 | 14.49 | 1
August | 23 | 6PM to 7PM | 78.1 | 75 | 73.9 | 132 | 39.4 | 0.0703 | 0.85 | 14.48 | 1
August | 23 | 7PM to 8PM | 75 | 74.2 | 73.9 | 132 | 38.64 | 0.0708 | 0.85 | 14.4 | 1
August | 23 | 8PM to 9PM | 75 | 74.2 | 73.9 | 132 | 38.64 | 0.0708 | 0.85 | 14.4 | 1
August | 23 | 9PM to 10PM | 75 | 74.2 | 73.9 | 132 | 38.64 | 0.0708 | 0.85 | 14.4 | 1
August | 23 | 10PM to 11PM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
August | 23 | 11PM to 12AM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
August | 24 | 12AM to 1AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 24 | 1AM to 2AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 24 | 2AM to 3AM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
August | 24 | 3AM to 4AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
August | 24 | 4AM to 5AM | 73 | 73 | 73 | 127.9 | 37.51 | 0.071 | 0.82 | 14.33 | 1
August | 24 | 5AM to 6AM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
August | 24 | 6AM to 7AM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
August | 24 | 7AM to 8AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
August | 24 | 8AM to 9AM | 73.9 | 73.3 | 73 | 127.9 | 37.74 | 0.0709 | 0.82 | 14.36 | 1
August | 24 | 9AM to 10AM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
August | 24 | 10AM to 11AM | 77 | 74.1 | 73 | 127.9 | 38.5 | 0.0705 | 0.82 | 14.44 | 1
August | 24 | 11AM to 12PM | 81 | 74.4 | 72 | 123.2 | 38.74 | 0.07 | 0.79 | 14.53 | 1
August | 24 | 12PM to 1PM | 82.9 | 74.9 | 72 | 123.2 | 39.23 | 0.0698 | 0.79 | 14.59 | 1
August | 24 | 1PM to 2PM | 84 | 75.9 | 73 | 127.9 | 40.24 | 0.0696 | 0.82 | 14.63 | 1
August | 24 | 2PM to 3PM | 84.9 | 75.4 | 72 | 123.2 | 39.72 | 0.0695 | 0.79 | 14.64 | 1
August | 24 | 3PM to 4PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
August | 24 | 4PM to 5PM | 84 | 74.6 | 71.1 | 119.4 | 38.9 | 0.0697 | 0.77 | 14.6 | 1
August | 24 | 5PM to 6PM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
August | 24 | 6PM to 7PM | 82 | 71.4 | 66.9 | 103.2 | 35.88 | 0.07 | 0.67 | 14.5 | 1
August | 24 | 7PM to 8PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
August | 24 | 8PM to 9PM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
August | 24 | 9PM to 10PM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
August | 24 | 10PM to 11PM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
August | 24 | 11PM to 12AM | 71.1 | 70.3 | 70 | 115 | 35 | 0.0714 | 0.74 | 14.24 | 1
August | 25 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
August | 25 | 1AM to 2AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
August | 25 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
August | 25 | 3AM to 4AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
August | 25 | 4AM to 5AM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
August | 25 | 5AM to 6AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
August | 25 | 6AM to 7AM | 66 | 62.7 | 61 | 83.5 | 28.85 | 0.0723 | 0.54 | 14.01 | 1
August | 25 | 7AM to 8AM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
August | 25 | 8AM to 9AM | 75.9 | 64.2 | 57.9 | 74.7 | 29.9 | 0.071 | 0.48 | 14.24 | 1
August | 25 | 9AM to 10AM | 82 | 65.7 | 57 | 72.3 | 31.02 | 0.0702 | 0.47 | 14.4 | 1
August | 25 | 10AM to 11AM | 84 | 64.3 | 53.1 | 62.4 | 29.96 | 0.07 | 0.41 | 14.42 | 1
August | 25 | 11AM to 12PM | 84.9 | 65.1 | 54 | 64.5 | 30.51 | 0.0699 | 0.42 | 14.45 | 1
August | 25 | 12PM to 1PM | 86 | 65.9 | 55 | 67.2 | 31.19 | 0.0697 | 0.44 | 14.48 | 1
August | 25 | 1PM to 2PM | 88 | 65.6 | 53.1 | 62.4 | 30.93 | 0.0695 | 0.41 | 14.52 | 1
August | 25 | 2PM to 3PM | 88 | 66.6 | 55 | 67.2 | 31.68 | 0.0695 | 0.44 | 14.54 | 1
August | 25 | 3PM to 4PM | 89.1 | 67.3 | 55.9 | 69.4 | 32.3 | 0.0693 | 0.45 | 14.57 | 1
August | 25 | 4PM to 5PM | 88 | 67 | 55.9 | 69.4 | 32.03 | 0.0694 | 0.45 | 14.54 | 1
August | 25 | 5PM to 6PM | 86 | 66.4 | 55.9 | 69.4 | 31.55 | 0.0697 | 0.45 | 14.49 | 1
August | 25 | 6PM to 7PM | 84 | 65.8 | 55.9 | 69.4 | 31.06 | 0.0699 | 0.45 | 14.44 | 1
August | 25 | 7PM to 8PM | 79 | 65.8 | 59 | 77.7 | 31.12 | 0.0705 | 0.5 | 14.33 | 1
August | 25 | 8PM to 9PM | 79 | 65.2 | 57.9 | 74.7 | 30.65 | 0.0706 | 0.48 | 14.32 | 1
August | 25 | 9PM to 10PM | 78.1 | 64.9 | 57.9 | 74.7 | 30.43 | 0.0707 | 0.48 | 14.3 | 1
August | 25 | 10PM to 11PM | 75.9 | 64.2 | 57.9 | 74.7 | 29.9 | 0.071 | 0.48 | 14.24 | 1
August | 25 | 11PM to 12AM | 75 | 64.5 | 59 | 77.7 | 30.15 | 0.0711 | 0.5 | 14.23 | 1
August | 26 | 12AM to 1AM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
August | 26 | 1AM to 2AM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
August | 26 | 2AM to 3AM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
August | 26 | 3AM to 4AM | 71.1 | 62.6 | 57.9 | 74.7 | 28.71 | 0.0716 | 0.48 | 14.11 | 1
August | 26 | 4AM to 5AM | 71.1 | 62.6 | 57.9 | 74.7 | 28.71 | 0.0716 | 0.48 | 14.11 | 1
August | 26 | 5AM to 6AM | 71.1 | 63.2 | 59 | 77.7 | 29.18 | 0.0716 | 0.5 | 14.12 | 1
August | 26 | 6AM to 7AM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
August | 26 | 7AM to 8AM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
August | 26 | 8AM to 9AM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
August | 26 | 9AM to 10AM | 81 | 68.6 | 63 | 89.6 | 33.48 | 0.0702 | 0.58 | 14.42 | 1
August | 26 | 10AM to 11AM | 84 | 70.2 | 64 | 93.2 | 34.79 | 0.0698 | 0.6 | 14.52 | 1
August | 26 | 11AM to 12PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
August | 26 | 12PM to 1PM | 89.1 | 71 | 63 | 89.6 | 35.47 | 0.0692 | 0.58 | 14.64 | 1
August | 26 | 1PM to 2PM | 91 | 68.9 | 57.9 | 74.7 | 33.6 | 0.069 | 0.48 | 14.64 | 1
August | 26 | 2PM to 3PM | 88 | 70.2 | 62.1 | 86.8 | 34.76 | 0.0693 | 0.56 | 14.6 | 1
August | 26 | 3PM to 4PM | 88 | 70.2 | 62.1 | 86.8 | 34.76 | 0.0693 | 0.56 | 14.6 | 1
August | 26 | 4PM to 5PM | 87.1 | 68.8 | 60.1 | 80.8 | 33.59 | 0.0695 | 0.52 | 14.56 | 1
August | 26 | 5PM to 6PM | 87.1 | 69.3 | 61 | 83.5 | 34.01 | 0.0695 | 0.54 | 14.57 | 1
August | 26 | 6PM to 7PM | 84 | 70.2 | 64 | 93.2 | 34.79 | 0.0698 | 0.6 | 14.52 | 1
August | 26 | 7PM to 8PM | 81 | 70.5 | 66 | 100 | 35.1 | 0.0702 | 0.64 | 14.46 | 1
August | 26 | 8PM to 9PM | 81 | 70.5 | 66 | 100 | 35.1 | 0.0702 | 0.64 | 14.46 | 1
August | 26 | 9PM to 10PM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
August | 26 | 10PM to 11PM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
August | 26 | 11PM to 12AM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
August | 27 | 12AM to 1AM | 73.9 | 66.5 | 63 | 89.6 | 31.76 | 0.0711 | 0.58 | 14.24 | 1
August | 27 | 1AM to 2AM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
August | 27 | 2AM to 3AM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
August | 27 | 3AM to 4AM | 71.1 | 66.3 | 64 | 93.2 | 31.6 | 0.0715 | 0.6 | 14.17 | 1
August | 27 | 4AM to 5AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
August | 27 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
August | 27 | 6AM to 7AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
August | 27 | 7AM to 8AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
August | 27 | 8AM to 9AM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
August | 27 | 9AM to 10AM | 81 | 71.1 | 66.9 | 103.2 | 35.61 | 0.0701 | 0.67 | 14.47 | 1
August | 27 | 10AM to 11AM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
August | 27 | 11AM to 12PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
August | 27 | 12PM to 1PM | 89.1 | 72.8 | 66 | 100 | 37.1 | 0.0691 | 0.64 | 14.67 | 1
August | 27 | 1PM to 2PM | 89.1 | 72.1 | 64.9 | 96.2 | 36.51 | 0.0691 | 0.62 | 14.66 | 1
August | 27 | 2PM to 3PM | 89.1 | 70.5 | 62.1 | 86.8 | 35.02 | 0.0692 | 0.56 | 14.63 | 1
August | 27 | 3PM to 4PM | 89.1 | 70.5 | 62.1 | 86.8 | 35.02 | 0.0692 | 0.56 | 14.63 | 1
August | 27 | 4PM to 5PM | 88 | 70.2 | 62.1 | 86.8 | 34.76 | 0.0693 | 0.56 | 14.6 | 1
August | 27 | 5PM to 6PM | 86 | 71.3 | 64.9 | 96.2 | 35.75 | 0.0695 | 0.62 | 14.58 | 1
August | 27 | 6PM to 7PM | 84 | 70.2 | 64 | 93.2 | 34.79 | 0.0698 | 0.6 | 14.52 | 1
August | 27 | 7PM to 8PM | 81 | 69.3 | 64 | 93.2 | 34.03 | 0.0702 | 0.6 | 14.43 | 1
August | 27 | 8PM to 9PM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
August | 27 | 9PM to 10PM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
August | 27 | 10PM to 11PM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
August | 27 | 11PM to 12AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
August | 28 | 12AM to 1AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
August | 28 | 1AM to 2AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
August | 28 | 2AM to 3AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
August | 28 | 3AM to 4AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
August | 28 | 4AM to 5AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
August | 28 | 5AM to 6AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
August | 28 | 6AM to 7AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
August | 28 | 7AM to 8AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
August | 28 | 8AM to 9AM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
August | 28 | 9AM to 10AM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
August | 28 | 10AM to 11AM | 80.1 | 70.8 | 66.9 | 103.2 | 35.39 | 0.0703 | 0.67 | 14.44 | 1
August | 28 | 11AM to 12PM | 82 | 70.8 | 66 | 100 | 35.37 | 0.07 | 0.64 | 14.49 | 1
August | 28 | 12PM to 1PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
August | 28 | 1PM to 2PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
August | 28 | 2PM to 3PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
August | 28 | 3PM to 4PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
August | 28 | 4PM to 5PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
August | 28 | 5PM to 6PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
August | 28 | 6PM to 7PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
August | 28 | 7PM to 8PM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
August | 28 | 8PM to 9PM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
August | 28 | 9PM to 10PM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
August | 28 | 10PM to 11PM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
August | 28 | 11PM to 12AM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
August | 29 | 12AM to 1AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
August | 29 | 1AM to 2AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 29 | 2AM to 3AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 29 | 3AM to 4AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
August | 29 | 4AM to 5AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 29 | 5AM to 6AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
August | 29 | 6AM to 7AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 29 | 7AM to 8AM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
August | 29 | 8AM to 9AM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
August | 29 | 9AM to 10AM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
August | 29 | 10AM to 11AM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
August | 29 | 11AM to 12PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
August | 29 | 12PM to 1PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
August | 29 | 1PM to 2PM | 91 | 72.7 | 64.9 | 96.2 | 36.99 | 0.0689 | 0.62 | 14.71 | 1
August | 29 | 2PM to 3PM | 91.9 | 71.8 | 63 | 89.6 | 36.18 | 0.0688 | 0.58 | 14.72 | 1
August | 29 | 3PM to 4PM | 90 | 71.9 | 64 | 93.2 | 36.25 | 0.0691 | 0.6 | 14.67 | 1
August | 29 | 4PM to 5PM | 90 | 71.9 | 64 | 93.2 | 36.25 | 0.0691 | 0.6 | 14.67 | 1
August | 29 | 5PM to 6PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
August | 29 | 6PM to 7PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
August | 29 | 7PM to 8PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
August | 29 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 111.4 | 36.18 | 0.0705 | 0.72 | 14.42 | 1
August | 29 | 9PM to 10PM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
August | 29 | 10PM to 11PM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
August | 29 | 11PM to 12AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
August | 30 | 12AM to 1AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
August | 30 | 1AM to 2AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
August | 30 | 2AM to 3AM | 70 | 69.3 | 69.1 | 111.4 | 34.18 | 0.0715 | 0.72 | 14.2 | 1
August | 30 | 3AM to 4AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
August | 30 | 4AM to 5AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
August | 30 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
August | 30 | 6AM to 7AM | 68 | 66.6 | 66 | 100 | 31.91 | 0.0719 | 0.64 | 14.11 | 1
August | 30 | 7AM to 8AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
August | 30 | 8AM to 9AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
August | 30 | 9AM to 10AM | 77 | 69.9 | 66.9 | 103.2 | 34.63 | 0.0707 | 0.67 | 14.36 | 1
August | 30 | 10AM to 11AM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
August | 30 | 11AM to 12PM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
August | 30 | 12PM to 1PM | 80.1 | 71.5 | 68 | 107.2 | 36.02 | 0.0702 | 0.69 | 14.46 | 1
August | 30 | 1PM to 2PM | 84.9 | 72.2 | 66.9 | 103.2 | 36.59 | 0.0696 | 0.67 | 14.57 | 1
August | 30 | 2PM to 3PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
August | 30 | 3PM to 4PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
August | 30 | 4PM to 5PM | 87.1 | 72.8 | 66.9 | 103.2 | 37.12 | 0.0694 | 0.67 | 14.63 | 1
August | 30 | 5PM to 6PM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
August | 30 | 6PM to 7PM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
August | 30 | 7PM to 8PM | 75.9 | 69.6 | 66.9 | 103.2 | 34.37 | 0.0708 | 0.67 | 14.33 | 1
August | 30 | 8PM to 9PM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
August | 30 | 9PM to 10PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
August | 30 | 10PM to 11PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
August | 30 | 11PM to 12AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
August | 31 | 12AM to 1AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
August | 31 | 1AM to 2AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
August | 31 | 2AM to 3AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
August | 31 | 3AM to 4AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
August | 31 | 4AM to 5AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
August | 31 | 5AM to 6AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
August | 31 | 6AM to 7AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
August | 31 | 7AM to 8AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
August | 31 | 8AM to 9AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
August | 31 | 9AM to 10AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
August | 31 | 10AM to 11AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
August | 31 | 11AM to 12PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
August | 31 | 12PM to 1PM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
August | 31 | 1PM to 2PM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
August | 31 | 2PM to 3PM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
August | 31 | 3PM to 4PM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
August | 31 | 4PM to 5PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
August | 31 | 5PM to 6PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
August | 31 | 6PM to 7PM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
August | 31 | 7PM to 8PM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
August | 31 | 8PM to 9PM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
August | 31 | 9PM to 10PM | 70.9 | 67.8 | 66.4 | 101.3 | 32.82 | 0.0715 | 0.65 | 14.19 | 1
August | 31 | 10PM to 11PM | 70.7 | 67.4 | 65.8 | 99.3 | 32.48 | 0.0715 | 0.64 | 14.18 | 1
August | 31 | 11PM to 12AM | 70.5 | 66.9 | 65.3 | 97.5 | 32.14 | 0.0716 | 0.63 | 14.17 | 1
September | 1 | 12AM to 1AM | 70.5 | 66.5 | 64.6 | 95 | 31.75 | 0.0716 | 0.61 | 14.16 | 1
September | 1 | 1AM to 2AM | 70.3 | 66.1 | 64 | 93.2 | 31.42 | 0.0716 | 0.6 | 14.15 | 1
September | 1 | 2AM to 3AM | 70.2 | 65.7 | 63.5 | 91.4 | 31.1 | 0.0716 | 0.59 | 14.14 | 1
September | 1 | 3AM to 4AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
September | 1 | 4AM to 5AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
September | 1 | 5AM to 6AM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
September | 1 | 6AM to 7AM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
September | 1 | 7AM to 8AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
September | 1 | 8AM to 9AM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
September | 1 | 9AM to 10AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
September | 1 | 10AM to 11AM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
September | 1 | 11AM to 12PM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
September | 1 | 12PM to 1PM | 77 | 67.5 | 63 | 89.6 | 32.51 | 0.0707 | 0.58 | 14.32 | 1
September | 1 | 1PM to 2PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
September | 1 | 2PM to 3PM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
September | 1 | 3PM to 4PM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
September | 1 | 4PM to 5PM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
September | 1 | 5PM to 6PM | 75 | 66.8 | 63 | 89.6 | 32.02 | 0.071 | 0.58 | 14.26 | 1
September | 1 | 6PM to 7PM | 73.9 | 66.5 | 63 | 89.6 | 31.76 | 0.0711 | 0.58 | 14.24 | 1
September | 1 | 7PM to 8PM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
September | 1 | 8PM to 9PM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
September | 1 | 9PM to 10PM | 72 | 67.1 | 64.9 | 96.2 | 32.3 | 0.0714 | 0.62 | 14.2 | 1
September | 1 | 10PM to 11PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
September | 1 | 11PM to 12AM | 66.2 | 63.8 | 62.6 | 88.5 | 29.67 | 0.0722 | 0.57 | 14.03 | 1
September | 2 | 12AM to 1AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
September | 2 | 1AM to 2AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
September | 2 | 2AM to 3AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
September | 2 | 3AM to 4AM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
September | 2 | 4AM to 5AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
September | 2 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
September | 2 | 6AM to 7AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
September | 2 | 7AM to 8AM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
September | 2 | 8AM to 9AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
September | 2 | 9AM to 10AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 2 | 10AM to 11AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
September | 2 | 11AM to 12PM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
September | 2 | 12PM to 1PM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
September | 2 | 1PM to 2PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
September | 2 | 2PM to 3PM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
September | 2 | 3PM to 4PM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
September | 2 | 4PM to 5PM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
September | 2 | 5PM to 6PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 2 | 6PM to 7PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 2 | 7PM to 8PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 2 | 8PM to 9PM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 2 | 9PM to 10PM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 2 | 10PM to 11PM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 2 | 11PM to 12AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 3 | 12AM to 1AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 3 | 1AM to 2AM | 71.6 | 70.3 | 69.8 | 114.2 | 35.02 | 0.0713 | 0.73 | 14.25 | 1
September | 3 | 2AM to 3AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
September | 3 | 3AM to 4AM | 71.1 | 69.8 | 69.3 | 112.1 | 34.56 | 0.0714 | 0.72 | 14.23 | 1
September | 3 | 4AM to 5AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
September | 3 | 5AM to 6AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
September | 3 | 6AM to 7AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
September | 3 | 7AM to 8AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 3 | 8AM to 9AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 3 | 9AM to 10AM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
September | 3 | 10AM to 11AM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
September | 3 | 11AM to 12PM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
September | 3 | 12PM to 1PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
September | 3 | 1PM to 2PM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
September | 3 | 2PM to 3PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
September | 3 | 3PM to 4PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
September | 3 | 4PM to 5PM | 86 | 72.5 | 66.9 | 103.2 | 36.85 | 0.0695 | 0.67 | 14.6 | 1
September | 3 | 5PM to 6PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
September | 3 | 6PM to 7PM | 78.1 | 69 | 64.9 | 96.2 | 33.8 | 0.0706 | 0.62 | 14.37 | 1
September | 3 | 7PM to 8PM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
September | 3 | 8PM to 9PM | 72 | 67.1 | 64.9 | 96.2 | 32.3 | 0.0714 | 0.62 | 14.2 | 1
September | 3 | 9PM to 10PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 3 | 10PM to 11PM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
September | 3 | 11PM to 12AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
September | 4 | 12AM to 1AM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
September | 4 | 1AM to 2AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
September | 4 | 2AM to 3AM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
September | 4 | 3AM to 4AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
September | 4 | 4AM to 5AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
September | 4 | 5AM to 6AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
September | 4 | 6AM to 7AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
September | 4 | 7AM to 8AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 4 | 8AM to 9AM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
September | 4 | 9AM to 10AM | 80.1 | 72.2 | 69.1 | 111.4 | 36.67 | 0.0702 | 0.72 | 14.47 | 1
September | 4 | 10AM to 11AM | 82.9 | 74.3 | 71.1 | 119.4 | 38.63 | 0.0698 | 0.77 | 14.57 | 1
September | 4 | 11AM to 12PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
September | 4 | 12PM to 1PM | 82 | 72.1 | 68 | 107.2 | 36.51 | 0.07 | 0.69 | 14.51 | 1
September | 4 | 1PM to 2PM | 79 | 72.5 | 70 | 115 | 36.96 | 0.0703 | 0.74 | 14.45 | 1
September | 4 | 2PM to 3PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
September | 4 | 3PM to 4PM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
September | 4 | 4PM to 5PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
September | 4 | 5PM to 6PM | 81 | 70.5 | 66 | 100 | 35.1 | 0.0702 | 0.64 | 14.46 | 1
September | 4 | 6PM to 7PM | 77 | 69.4 | 66 | 100 | 34.13 | 0.0707 | 0.64 | 14.35 | 1
September | 4 | 7PM to 8PM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
September | 4 | 8PM to 9PM | 77 | 69.9 | 66.9 | 103.2 | 34.63 | 0.0707 | 0.67 | 14.36 | 1
September | 4 | 9PM to 10PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
September | 4 | 10PM to 11PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 4 | 11PM to 12AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
September | 5 | 12AM to 1AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 5 | 1AM to 2AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 5 | 2AM to 3AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 5 | 3AM to 4AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
September | 5 | 4AM to 5AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 5 | 5AM to 6AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 5 | 6AM to 7AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 5 | 7AM to 8AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 5 | 8AM to 9AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
September | 5 | 9AM to 10AM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
September | 5 | 10AM to 11AM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
September | 5 | 11AM to 12PM | 82 | 73.3 | 70 | 115 | 37.72 | 0.0699 | 0.74 | 14.53 | 1
September | 5 | 12PM to 1PM | 84 | 73.3 | 69.1 | 111.4 | 37.65 | 0.0697 | 0.72 | 14.58 | 1
September | 5 | 1PM to 2PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
September | 5 | 2PM to 3PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
September | 5 | 3PM to 4PM | 82.9 | 70.4 | 64.9 | 96.2 | 35 | 0.0699 | 0.62 | 14.5 | 1
September | 5 | 4PM to 5PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
September | 5 | 5PM to 6PM | 84 | 70.7 | 64.9 | 96.2 | 35.26 | 0.0698 | 0.62 | 14.53 | 1
September | 5 | 6PM to 7PM | 81 | 69.8 | 64.9 | 96.2 | 34.51 | 0.0702 | 0.62 | 14.44 | 1
September | 5 | 7PM to 8PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
September | 5 | 8PM to 9PM | 80.1 | 70.2 | 66 | 100 | 34.88 | 0.0703 | 0.64 | 14.43 | 1
September | 5 | 9PM to 10PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
September | 5 | 10PM to 11PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
September | 5 | 11PM to 12AM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
September | 6 | 12AM to 1AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
September | 6 | 1AM to 2AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
September | 6 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
September | 6 | 3AM to 4AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 6 | 4AM to 5AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
September | 6 | 5AM to 6AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 6 | 6AM to 7AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 6 | 7AM to 8AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
September | 6 | 8AM to 9AM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
September | 6 | 9AM to 10AM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
September | 6 | 10AM to 11AM | 84 | 73.3 | 69.1 | 111.4 | 37.65 | 0.0697 | 0.72 | 14.58 | 1
September | 6 | 11AM to 12PM | 87.1 | 74.7 | 70 | 115 | 38.96 | 0.0693 | 0.74 | 14.67 | 1
September | 6 | 12PM to 1PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
September | 6 | 1PM to 2PM | 88 | 74.9 | 70 | 115 | 39.19 | 0.0692 | 0.74 | 14.69 | 1
September | 6 | 2PM to 3PM | 84.9 | 72.8 | 68 | 107.2 | 37.22 | 0.0696 | 0.69 | 14.59 | 1
September | 6 | 3PM to 4PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
September | 6 | 4PM to 5PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
September | 6 | 5PM to 6PM | 84.9 | 73.5 | 69.1 | 111.4 | 37.87 | 0.0696 | 0.72 | 14.6 | 1
September | 6 | 6PM to 7PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
September | 6 | 7PM to 8PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
September | 6 | 8PM to 9PM | 80.1 | 72.2 | 69.1 | 111.4 | 36.67 | 0.0702 | 0.72 | 14.47 | 1
September | 6 | 9PM to 10PM | 80.1 | 72.8 | 70 | 115 | 37.23 | 0.0702 | 0.74 | 14.48 | 1
September | 6 | 10PM to 11PM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
September | 6 | 11PM to 12AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
September | 7 | 12AM to 1AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
September | 7 | 1AM to 2AM | 73.9 | 71.1 | 70 | 115 | 35.72 | 0.071 | 0.74 | 14.32 | 1
September | 7 | 2AM to 3AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 7 | 3AM to 4AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 7 | 4AM to 5AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 7 | 5AM to 6AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 7 | 6AM to 7AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 7 | 7AM to 8AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
September | 7 | 8AM to 9AM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
September | 7 | 9AM to 10AM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
September | 7 | 10AM to 11AM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
September | 7 | 11AM to 12PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
September | 7 | 12PM to 1PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
September | 7 | 1PM to 2PM | 88 | 73.7 | 68 | 107.2 | 37.97 | 0.0692 | 0.69 | 14.67 | 1
September | 7 | 2PM to 3PM | 89.1 | 73.3 | 66.9 | 103.2 | 37.61 | 0.0691 | 0.67 | 14.68 | 1
September | 7 | 3PM to 4PM | 89.1 | 74.6 | 69.1 | 111.4 | 38.89 | 0.0691 | 0.72 | 14.71 | 1
September | 7 | 4PM to 5PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
September | 7 | 5PM to 6PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
September | 7 | 6PM to 7PM | 82.9 | 73 | 69.1 | 111.4 | 37.38 | 0.0698 | 0.72 | 14.55 | 1
September | 7 | 7PM to 8PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
September | 7 | 8PM to 9PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
September | 7 | 9PM to 10PM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
September | 7 | 10PM to 11PM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
September | 7 | 11PM to 12AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 8 | 12AM to 1AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 8 | 1AM to 2AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
September | 8 | 2AM to 3AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
September | 8 | 3AM to 4AM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
September | 8 | 4AM to 5AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
September | 8 | 5AM to 6AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
September | 8 | 6AM to 7AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 8 | 7AM to 8AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
September | 8 | 8AM to 9AM | 79 | 71.2 | 68 | 107.2 | 35.75 | 0.0704 | 0.69 | 14.43 | 1
September | 8 | 9AM to 10AM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
September | 8 | 10AM to 11AM | 84.9 | 74.1 | 70 | 115 | 38.43 | 0.0696 | 0.74 | 14.61 | 1
September | 8 | 11AM to 12PM | 87.1 | 74.1 | 69.1 | 111.4 | 38.4 | 0.0693 | 0.72 | 14.66 | 1
September | 8 | 12PM to 1PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
September | 8 | 1PM to 2PM | 88 | 73 | 66.9 | 103.2 | 37.34 | 0.0692 | 0.67 | 14.66 | 1
September | 8 | 2PM to 3PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
September | 8 | 3PM to 4PM | 88 | 71.8 | 64.9 | 96.2 | 36.24 | 0.0693 | 0.62 | 14.63 | 1
September | 8 | 4PM to 5PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
September | 8 | 5PM to 6PM | 84 | 71.4 | 66 | 100 | 35.86 | 0.0698 | 0.64 | 14.54 | 1
September | 8 | 6PM to 7PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
September | 8 | 7PM to 8PM | 82 | 71.4 | 66.9 | 103.2 | 35.88 | 0.07 | 0.67 | 14.5 | 1
September | 8 | 8PM to 9PM | 78.1 | 70.9 | 68 | 107.2 | 35.53 | 0.0705 | 0.69 | 14.4 | 1
September | 8 | 9PM to 10PM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
September | 8 | 10PM to 11PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
September | 8 | 11PM to 12AM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
September | 9 | 12AM to 1AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
September | 9 | 1AM to 2AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
September | 9 | 2AM to 3AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
September | 9 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
September | 9 | 4AM to 5AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
September | 9 | 5AM to 6AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
September | 9 | 6AM to 7AM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
September | 9 | 7AM to 8AM | 77 | 70.6 | 68 | 107.2 | 35.26 | 0.0706 | 0.69 | 14.37 | 1
September | 9 | 8AM to 9AM | 82.9 | 73.6 | 70 | 115 | 37.94 | 0.0698 | 0.74 | 14.56 | 1
September | 9 | 9AM to 10AM | 84 | 73.9 | 70 | 115 | 38.21 | 0.0697 | 0.74 | 14.59 | 1
September | 9 | 10AM to 11AM | 87.1 | 75.4 | 71.1 | 119.4 | 39.66 | 0.0693 | 0.77 | 14.68 | 1
September | 9 | 11AM to 12PM | 86 | 74.4 | 70 | 115 | 38.7 | 0.0694 | 0.74 | 14.64 | 1
September | 9 | 12PM to 1PM | 87.1 | 73.4 | 68 | 107.2 | 37.75 | 0.0693 | 0.69 | 14.64 | 1
September | 9 | 1PM to 2PM | 80.1 | 70.8 | 66.9 | 103.2 | 35.39 | 0.0703 | 0.67 | 14.44 | 1
September | 9 | 2PM to 3PM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
September | 9 | 3PM to 4PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 9 | 4PM to 5PM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
September | 9 | 5PM to 6PM | 75 | 70.1 | 68 | 107.2 | 34.77 | 0.0709 | 0.69 | 14.32 | 1
September | 9 | 6PM to 7PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 9 | 7PM to 8PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 9 | 8PM to 9PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 9 | 9PM to 10PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
September | 9 | 10PM to 11PM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 9 | 11PM to 12AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 10 | 12AM to 1AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 10 | 1AM to 2AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 10 | 2AM to 3AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
September | 10 | 3AM to 4AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 10 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
September | 10 | 5AM to 6AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 10 | 6AM to 7AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 10 | 7AM to 8AM | 73.4 | 69.6 | 68 | 107.2 | 34.37 | 0.0711 | 0.69 | 14.28 | 1
September | 10 | 8AM to 9AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 10 | 9AM to 10AM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 10 | 10AM to 11AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
September | 10 | 11AM to 12PM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
September | 10 | 12PM to 1PM | 78.1 | 70.2 | 66.9 | 103.2 | 34.9 | 0.0705 | 0.67 | 14.39 | 1
September | 10 | 1PM to 2PM | 79 | 71.9 | 69.1 | 111.4 | 36.4 | 0.0704 | 0.72 | 14.44 | 1
September | 10 | 2PM to 3PM | 81 | 71.8 | 68 | 107.2 | 36.24 | 0.0701 | 0.69 | 14.48 | 1
September | 10 | 3PM to 4PM | 82.9 | 71.6 | 66.9 | 103.2 | 36.1 | 0.0699 | 0.67 | 14.52 | 1
September | 10 | 4PM to 5PM | 82.4 | 72.2 | 68 | 107.2 | 36.6 | 0.0699 | 0.69 | 14.52 | 1
September | 10 | 5PM to 6PM | 80.1 | 72.2 | 69.1 | 111.4 | 36.67 | 0.0702 | 0.72 | 14.47 | 1
September | 10 | 6PM to 7PM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
September | 10 | 7PM to 8PM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
September | 10 | 8PM to 9PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 10 | 9PM to 10PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 10 | 10PM to 11PM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
September | 10 | 11PM to 12AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
September | 11 | 12AM to 1AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
September | 11 | 1AM to 2AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 11 | 2AM to 3AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
September | 11 | 3AM to 4AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
September | 11 | 4AM to 5AM | 69.1 | 67 | 66 | 100 | 32.18 | 0.0717 | 0.64 | 14.14 | 1
September | 11 | 5AM to 6AM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
September | 11 | 6AM to 7AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
September | 11 | 7AM to 8AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
September | 11 | 8AM to 9AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 11 | 9AM to 10AM | 77 | 72 | 70 | 115 | 36.47 | 0.0706 | 0.74 | 14.4 | 1
September | 11 | 10AM to 11AM | 80.1 | 73.5 | 71.1 | 119.4 | 37.92 | 0.0702 | 0.77 | 14.5 | 1
September | 11 | 11AM to 12PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
September | 11 | 12PM to 1PM | 81 | 73.1 | 70 | 115 | 37.45 | 0.0701 | 0.74 | 14.51 | 1
September | 11 | 1PM to 2PM | 82 | 72.8 | 69.1 | 111.4 | 37.16 | 0.07 | 0.72 | 14.52 | 1
September | 11 | 2PM to 3PM | 84.9 | 73.5 | 69.1 | 111.4 | 37.87 | 0.0696 | 0.72 | 14.6 | 1
September | 11 | 3PM to 4PM | 86 | 73.1 | 68 | 107.2 | 37.48 | 0.0695 | 0.69 | 14.62 | 1
September | 11 | 4PM to 5PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
September | 11 | 5PM to 6PM | 80.1 | 68.4 | 63 | 89.6 | 33.26 | 0.0703 | 0.58 | 14.4 | 1
September | 11 | 6PM to 7PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
September | 11 | 7PM to 8PM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
September | 11 | 8PM to 9PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 11 | 9PM to 10PM | 73.9 | 67.8 | 64.9 | 96.2 | 32.78 | 0.0711 | 0.62 | 14.26 | 1
September | 11 | 10PM to 11PM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
September | 11 | 11PM to 12AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
September | 12 | 12AM to 1AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 12 | 1AM to 2AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
September | 12 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
September | 12 | 3AM to 4AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 12 | 4AM to 5AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 12 | 5AM to 6AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 12 | 6AM to 7AM | 68 | 65.3 | 64 | 93.2 | 30.85 | 0.0719 | 0.6 | 14.09 | 1
September | 12 | 7AM to 8AM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
September | 12 | 8AM to 9AM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
September | 12 | 9AM to 10AM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
September | 12 | 10AM to 11AM | 82 | 71.4 | 66.9 | 103.2 | 35.88 | 0.07 | 0.67 | 14.5 | 1
September | 12 | 11AM to 12PM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
September | 12 | 12PM to 1PM | 84 | 71.9 | 66.9 | 103.2 | 36.36 | 0.0697 | 0.67 | 14.55 | 1
September | 12 | 1PM to 2PM | 84.9 | 71.6 | 66 | 100 | 36.08 | 0.0697 | 0.64 | 14.56 | 1
September | 12 | 2PM to 3PM | 87.1 | 71.6 | 64.9 | 96.2 | 36.02 | 0.0694 | 0.62 | 14.61 | 1
September | 12 | 3PM to 4PM | 86 | 70.7 | 64 | 93.2 | 35.27 | 0.0696 | 0.6 | 14.57 | 1
September | 12 | 4PM to 5PM | 84.9 | 70.4 | 64 | 93.2 | 35.01 | 0.0697 | 0.6 | 14.54 | 1
September | 12 | 5PM to 6PM | 82 | 69.6 | 64 | 93.2 | 34.3 | 0.0701 | 0.6 | 14.46 | 1
September | 12 | 6PM to 7PM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
September | 12 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 96.2 | 33.27 | 0.0708 | 0.62 | 14.31 | 1
September | 12 | 8PM to 9PM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
September | 12 | 9PM to 10PM | 73.9 | 67.8 | 64.9 | 96.2 | 32.78 | 0.0711 | 0.62 | 14.26 | 1
September | 12 | 10PM to 11PM | 73 | 66.9 | 64 | 93.2 | 32.09 | 0.0712 | 0.6 | 14.22 | 1
September | 12 | 11PM to 12AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
September | 13 | 12AM to 1AM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
September | 13 | 1AM to 2AM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
September | 13 | 2AM to 3AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
September | 13 | 3AM to 4AM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
September | 13 | 4AM to 5AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
September | 13 | 5AM to 6AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
September | 13 | 6AM to 7AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
September | 13 | 7AM to 8AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
September | 13 | 8AM to 9AM | 69.1 | 58.7 | 52 | 59.9 | 25.93 | 0.072 | 0.39 | 14.01 | 1
September | 13 | 9AM to 10AM | 71.1 | 57.9 | 48.9 | 53.4 | 25.4 | 0.0717 | 0.35 | 14.04 | 1
September | 13 | 10AM to 11AM | 73 | 59.1 | 50 | 55.6 | 26.23 | 0.0715 | 0.36 | 14.1 | 1
September | 13 | 11AM to 12PM | 73 | 59.1 | 50 | 55.6 | 26.23 | 0.0715 | 0.36 | 14.1 | 1
September | 13 | 12PM to 1PM | 75 | 60.4 | 51.1 | 58 | 27.07 | 0.0712 | 0.38 | 14.16 | 1
September | 13 | 1PM to 2PM | 75.2 | 59.9 | 50 | 55.6 | 26.75 | 0.0712 | 0.36 | 14.16 | 1
September | 13 | 2PM to 3PM | 78.1 | 60.9 | 50 | 55.6 | 27.45 | 0.0708 | 0.36 | 14.24 | 1
September | 13 | 3PM to 4PM | 75.9 | 60.2 | 50 | 55.6 | 26.93 | 0.0711 | 0.36 | 14.18 | 1
September | 13 | 4PM to 5PM | 73.9 | 59.5 | 50 | 55.6 | 26.45 | 0.0713 | 0.36 | 14.13 | 1
September | 13 | 5PM to 6PM | 72 | 58.2 | 48.9 | 53.4 | 25.62 | 0.0716 | 0.35 | 14.07 | 1
September | 13 | 6PM to 7PM | 69.1 | 58.2 | 51.1 | 58 | 25.62 | 0.072 | 0.38 | 14.01 | 1
September | 13 | 7PM to 8PM | 64.9 | 57.1 | 52 | 59.9 | 24.92 | 0.0725 | 0.39 | 13.9 | 1
September | 13 | 8PM to 9PM | 64 | 57.4 | 53.1 | 62.4 | 25.09 | 0.0727 | 0.41 | 13.89 | 1
September | 13 | 9PM to 10PM | 62.1 | 56.6 | 53.1 | 62.4 | 24.6 | 0.0729 | 0.41 | 13.83 | 1
September | 13 | 10PM to 11PM | 60.8 | 56.4 | 53.6 | 63.7 | 24.49 | 0.0731 | 0.41 | 13.8 | 1
September | 13 | 11PM to 12AM | 60.1 | 55.9 | 53.1 | 62.4 | 24.12 | 0.0732 | 0.41 | 13.78 | 1
September | 14 | 12AM to 1AM | 57.9 | 54.4 | 52 | 59.9 | 23.21 | 0.0735 | 0.39 | 13.72 | 1
September | 14 | 1AM to 2AM | 57.9 | 54.4 | 52 | 59.9 | 23.21 | 0.0735 | 0.39 | 13.72 | 1
September | 14 | 2AM to 3AM | 57 | 54 | 52 | 59.9 | 22.99 | 0.0737 | 0.39 | 13.69 | 1
September | 14 | 3AM to 4AM | 55 | 52.7 | 51.1 | 58 | 22.2 | 0.074 | 0.38 | 13.63 | 1
September | 14 | 4AM to 5AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
September | 14 | 5AM to 6AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
September | 14 | 6AM to 7AM | 55 | 52.7 | 51.1 | 58 | 22.2 | 0.074 | 0.38 | 13.63 | 1
September | 14 | 7AM to 8AM | 59 | 55.4 | 53.1 | 62.4 | 23.86 | 0.0734 | 0.41 | 13.75 | 1
September | 14 | 8AM to 9AM | 64.9 | 57.7 | 53.1 | 62.4 | 25.31 | 0.0725 | 0.41 | 13.91 | 1
September | 14 | 9AM to 10AM | 69.1 | 57.7 | 50 | 55.6 | 25.26 | 0.072 | 0.36 | 14 | 1
September | 14 | 10AM to 11AM | 72 | 58.2 | 48.9 | 53.4 | 25.62 | 0.0716 | 0.35 | 14.07 | 1
September | 14 | 11AM to 12PM | 73.9 | 57.7 | 46 | 47.9 | 25.23 | 0.0714 | 0.31 | 14.1 | 1
September | 14 | 12PM to 1PM | 77 | 57.6 | 43 | 42.5 | 25.14 | 0.071 | 0.28 | 14.17 | 1
September | 14 | 1PM to 2PM | 78.1 | 58 | 43 | 42.5 | 25.4 | 0.0709 | 0.28 | 14.19 | 1
September | 14 | 2PM to 3PM | 79 | 58.7 | 44.1 | 44.4 | 25.91 | 0.0707 | 0.29 | 14.22 | 1
September | 14 | 3PM to 4PM | 78.1 | 59.2 | 46 | 47.9 | 26.24 | 0.0708 | 0.31 | 14.21 | 1
September | 14 | 4PM to 5PM | 77 | 59.2 | 46.9 | 49.6 | 26.24 | 0.071 | 0.32 | 14.19 | 1
September | 14 | 5PM to 6PM | 73.9 | 58.5 | 48 | 51.6 | 25.82 | 0.0714 | 0.34 | 14.11 | 1
September | 14 | 6PM to 7PM | 71.1 | 57.5 | 48 | 51.6 | 25.12 | 0.0718 | 0.34 | 14.04 | 1
September | 14 | 7PM to 8PM | 71.1 | 57.9 | 48.9 | 53.4 | 25.4 | 0.0717 | 0.35 | 14.04 | 1
September | 14 | 8PM to 9PM | 68 | 56.7 | 48.9 | 53.4 | 24.65 | 0.0722 | 0.35 | 13.96 | 1
September | 14 | 9PM to 10PM | 66 | 57.1 | 51.1 | 58 | 24.88 | 0.0724 | 0.38 | 13.92 | 1
September | 14 | 10PM to 11PM | 63 | 55.9 | 51.1 | 58 | 24.13 | 0.0728 | 0.38 | 13.84 | 1
September | 14 | 11PM to 12AM | 63 | 56.4 | 52 | 59.9 | 24.44 | 0.0728 | 0.39 | 13.85 | 1
September | 15 | 12AM to 1AM | 61 | 55.6 | 52 | 59.9 | 23.96 | 0.0731 | 0.39 | 13.8 | 1
September | 15 | 1AM to 2AM | 60.1 | 55.3 | 52 | 59.9 | 23.74 | 0.0732 | 0.39 | 13.77 | 1
September | 15 | 2AM to 3AM | 59 | 54.3 | 51.1 | 58 | 23.17 | 0.0734 | 0.38 | 13.74 | 1
September | 15 | 3AM to 4AM | 59 | 54.3 | 51.1 | 58 | 23.17 | 0.0734 | 0.38 | 13.74 | 1
September | 15 | 4AM to 5AM | 59 | 54.3 | 51.1 | 58 | 23.17 | 0.0734 | 0.38 | 13.74 | 1
September | 15 | 5AM to 6AM | 57.9 | 53.9 | 51.1 | 58 | 22.9 | 0.0735 | 0.38 | 13.71 | 1
September | 15 | 6AM to 7AM | 59 | 54.8 | 52 | 59.9 | 23.47 | 0.0734 | 0.39 | 13.74 | 1
September | 15 | 7AM to 8AM | 66 | 58.1 | 53.1 | 62.4 | 25.57 | 0.0724 | 0.41 | 13.94 | 1
September | 15 | 8AM to 9AM | 71.1 | 58.9 | 51.1 | 58 | 26.1 | 0.0717 | 0.38 | 14.06 | 1
September | 15 | 9AM to 10AM | 75 | 60.8 | 52 | 59.9 | 27.38 | 0.0712 | 0.39 | 14.17 | 1
September | 15 | 10AM to 11AM | 78.1 | 62.4 | 53.1 | 62.4 | 28.51 | 0.0708 | 0.41 | 14.26 | 1
September | 15 | 11AM to 12PM | 80.1 | 63 | 53.1 | 62.4 | 29 | 0.0705 | 0.41 | 14.31 | 1
September | 15 | 12PM to 1PM | 82 | 64.1 | 54 | 64.5 | 29.81 | 0.0702 | 0.42 | 14.37 | 1
September | 15 | 1PM to 2PM | 82.9 | 65.4 | 55.9 | 69.4 | 30.8 | 0.0701 | 0.45 | 14.41 | 1
September | 15 | 2PM to 3PM | 84.9 | 66.6 | 57 | 72.3 | 31.73 | 0.0698 | 0.47 | 14.47 | 1
September | 15 | 3PM to 4PM | 84 | 66.3 | 57 | 72.3 | 31.51 | 0.0699 | 0.47 | 14.45 | 1
September | 15 | 4PM to 5PM | 82 | 65.7 | 57 | 72.3 | 31.02 | 0.0702 | 0.47 | 14.4 | 1
September | 15 | 5PM to 6PM | 81 | 66.4 | 59 | 77.7 | 31.61 | 0.0703 | 0.5 | 14.38 | 1
September | 15 | 6PM to 7PM | 79 | 65.8 | 59 | 77.7 | 31.12 | 0.0705 | 0.5 | 14.33 | 1
September | 15 | 7PM to 8PM | 78.1 | 65.5 | 59 | 77.7 | 30.9 | 0.0707 | 0.5 | 14.31 | 1
September | 15 | 8PM to 9PM | 77 | 64.5 | 57.9 | 74.7 | 30.17 | 0.0708 | 0.48 | 14.27 | 1
September | 15 | 9PM to 10PM | 75 | 63.9 | 57.9 | 74.7 | 29.68 | 0.0711 | 0.48 | 14.22 | 1
September | 15 | 10PM to 11PM | 75.9 | 63.7 | 57 | 72.3 | 29.52 | 0.071 | 0.47 | 14.23 | 1
September | 15 | 11PM to 12AM | 73.9 | 63.5 | 57.9 | 74.7 | 29.42 | 0.0712 | 0.48 | 14.19 | 1
September | 16 | 12AM to 1AM | 73.9 | 63.5 | 57.9 | 74.7 | 29.42 | 0.0712 | 0.48 | 14.19 | 1
September | 16 | 1AM to 2AM | 73 | 63.9 | 59 | 77.7 | 29.67 | 0.0713 | 0.5 | 14.17 | 1
September | 16 | 2AM to 3AM | 73 | 64.5 | 60.1 | 80.8 | 30.15 | 0.0713 | 0.52 | 14.18 | 1
September | 16 | 3AM to 4AM | 72 | 65.3 | 62.1 | 86.8 | 30.82 | 0.0714 | 0.56 | 14.17 | 1
September | 16 | 4AM to 5AM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
September | 16 | 5AM to 6AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 16 | 6AM to 7AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 16 | 7AM to 8AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 16 | 8AM to 9AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
September | 16 | 9AM to 10AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
September | 16 | 10AM to 11AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
September | 16 | 11AM to 12PM | 79 | 74.6 | 73 | 127.9 | 38.99 | 0.0703 | 0.82 | 14.49 | 1
September | 16 | 12PM to 1PM | 82 | 75.4 | 73 | 127.9 | 39.75 | 0.0699 | 0.82 | 14.58 | 1
September | 16 | 1PM to 2PM | 80.1 | 74.9 | 73 | 127.9 | 39.26 | 0.0701 | 0.82 | 14.52 | 1
September | 16 | 2PM to 3PM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
September | 16 | 3PM to 4PM | 75 | 73.6 | 73 | 127.9 | 38.01 | 0.0708 | 0.82 | 14.39 | 1
September | 16 | 4PM to 5PM | 78.1 | 75 | 73.9 | 132 | 39.4 | 0.0703 | 0.85 | 14.48 | 1
September | 16 | 5PM to 6PM | 78.1 | 75 | 73.9 | 132 | 39.4 | 0.0703 | 0.85 | 14.48 | 1
September | 16 | 6PM to 7PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
September | 16 | 7PM to 8PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
September | 16 | 8PM to 9PM | 77 | 74.1 | 73 | 127.9 | 38.5 | 0.0705 | 0.82 | 14.44 | 1
September | 16 | 9PM to 10PM | 77 | 74.1 | 73 | 127.9 | 38.5 | 0.0705 | 0.82 | 14.44 | 1
September | 16 | 10PM to 11PM | 75.9 | 73.8 | 73 | 127.9 | 38.23 | 0.0707 | 0.82 | 14.41 | 1
September | 16 | 11PM to 12AM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
September | 17 | 12AM to 1AM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
September | 17 | 1AM to 2AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 17 | 2AM to 3AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 17 | 3AM to 4AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 17 | 4AM to 5AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
September | 17 | 5AM to 6AM | 72 | 70.5 | 70 | 115 | 35.23 | 0.0713 | 0.74 | 14.26 | 1
September | 17 | 6AM to 7AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
September | 17 | 7AM to 8AM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
September | 17 | 8AM to 9AM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
September | 17 | 9AM to 10AM | 75.9 | 71.7 | 70 | 115 | 36.2 | 0.0707 | 0.74 | 14.37 | 1
September | 17 | 10AM to 11AM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
September | 17 | 11AM to 12PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
September | 17 | 12PM to 1PM | 81 | 72.5 | 69.1 | 111.4 | 36.89 | 0.0701 | 0.72 | 14.49 | 1
September | 17 | 1PM to 2PM | 81 | 71.8 | 68 | 107.2 | 36.24 | 0.0701 | 0.69 | 14.48 | 1
September | 17 | 2PM to 3PM | 82.9 | 72.3 | 68 | 107.2 | 36.73 | 0.0699 | 0.69 | 14.53 | 1
September | 17 | 3PM to 4PM | 80.1 | 70.8 | 66.9 | 103.2 | 35.39 | 0.0703 | 0.67 | 14.44 | 1
September | 17 | 4PM to 5PM | 77 | 69.4 | 66 | 100 | 34.13 | 0.0707 | 0.64 | 14.35 | 1
September | 17 | 5PM to 6PM | 75.9 | 68.4 | 64.9 | 96.2 | 33.27 | 0.0708 | 0.62 | 14.31 | 1
September | 17 | 6PM to 7PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
September | 17 | 7PM to 8PM | 70 | 62.8 | 59 | 77.7 | 28.92 | 0.0717 | 0.5 | 14.09 | 1
September | 17 | 8PM to 9PM | 68 | 62.2 | 59 | 77.7 | 28.43 | 0.072 | 0.5 | 14.04 | 1
September | 17 | 9PM to 10PM | 66 | 61.5 | 59 | 77.7 | 27.95 | 0.0723 | 0.5 | 13.99 | 1
September | 17 | 10PM to 11PM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
September | 17 | 11PM to 12AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
September | 18 | 12AM to 1AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
September | 18 | 1AM to 2AM | 60.1 | 58.2 | 57 | 72.3 | 25.65 | 0.0731 | 0.47 | 13.81 | 1
September | 18 | 2AM to 3AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
September | 18 | 3AM to 4AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
September | 18 | 4AM to 5AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
September | 18 | 5AM to 6AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
September | 18 | 6AM to 7AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
September | 18 | 7AM to 8AM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
September | 18 | 8AM to 9AM | 66 | 60.8 | 57.9 | 74.7 | 27.48 | 0.0723 | 0.48 | 13.98 | 1
September | 18 | 9AM to 10AM | 71.1 | 62.1 | 57 | 72.3 | 28.34 | 0.0716 | 0.47 | 14.1 | 1
September | 18 | 10AM to 11AM | 73.9 | 62.5 | 55.9 | 69.4 | 28.6 | 0.0713 | 0.45 | 14.17 | 1
September | 18 | 11AM to 12PM | 75.9 | 63.1 | 55.9 | 69.4 | 29.08 | 0.071 | 0.45 | 14.22 | 1
September | 18 | 12PM to 1PM | 78.1 | 64.9 | 57.9 | 74.7 | 30.43 | 0.0707 | 0.48 | 14.3 | 1
September | 18 | 1PM to 2PM | 77 | 64.5 | 57.9 | 74.7 | 30.17 | 0.0708 | 0.48 | 14.27 | 1
September | 18 | 2PM to 3PM | 73.9 | 62.5 | 55.9 | 69.4 | 28.6 | 0.0713 | 0.45 | 14.17 | 1
September | 18 | 3PM to 4PM | 78.1 | 63.8 | 55.9 | 69.4 | 29.61 | 0.0707 | 0.45 | 14.28 | 1
September | 18 | 4PM to 5PM | 75.9 | 62.1 | 54 | 64.5 | 28.32 | 0.071 | 0.42 | 14.21 | 1
September | 18 | 5PM to 6PM | 73 | 61.1 | 54 | 64.5 | 27.61 | 0.0714 | 0.42 | 14.13 | 1
September | 18 | 6PM to 7PM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
September | 18 | 7PM to 8PM | 66 | 58.1 | 53.1 | 62.4 | 25.57 | 0.0724 | 0.41 | 13.94 | 1
September | 18 | 8PM to 9PM | 64.9 | 57.7 | 53.1 | 62.4 | 25.31 | 0.0725 | 0.41 | 13.91 | 1
September | 18 | 9PM to 10PM | 63 | 57 | 53.1 | 62.4 | 24.82 | 0.0728 | 0.41 | 13.86 | 1
September | 18 | 10PM to 11PM | 64 | 56.8 | 52 | 59.9 | 24.7 | 0.0727 | 0.39 | 13.88 | 1
September | 18 | 11PM to 12AM | 64 | 56.8 | 52 | 59.9 | 24.7 | 0.0727 | 0.39 | 13.88 | 1
September | 19 | 12AM to 1AM | 62.1 | 56 | 52 | 59.9 | 24.22 | 0.0729 | 0.39 | 13.83 | 1
September | 19 | 1AM to 2AM | 60.1 | 55.9 | 53.1 | 62.4 | 24.12 | 0.0732 | 0.41 | 13.78 | 1
September | 19 | 2AM to 3AM | 59 | 55.4 | 53.1 | 62.4 | 23.86 | 0.0734 | 0.41 | 13.75 | 1
September | 19 | 3AM to 4AM | 57.9 | 54.4 | 52 | 59.9 | 23.21 | 0.0735 | 0.39 | 13.72 | 1
September | 19 | 4AM to 5AM | 57.9 | 54.4 | 52 | 59.9 | 23.21 | 0.0735 | 0.39 | 13.72 | 1
September | 19 | 5AM to 6AM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
September | 19 | 6AM to 7AM | 61 | 55.6 | 52 | 59.9 | 23.96 | 0.0731 | 0.39 | 13.8 | 1
September | 19 | 7AM to 8AM | 64 | 56.3 | 51.1 | 58 | 24.39 | 0.0727 | 0.38 | 13.87 | 1
September | 19 | 8AM to 9AM | 66.9 | 58.4 | 53.1 | 62.4 | 25.79 | 0.0723 | 0.41 | 13.96 | 1
September | 19 | 9AM to 10AM | 70 | 58 | 50 | 55.6 | 25.48 | 0.0719 | 0.36 | 14.02 | 1
September | 19 | 10AM to 11AM | 73.9 | 60.4 | 52 | 59.9 | 27.12 | 0.0713 | 0.39 | 14.14 | 1
September | 19 | 11AM to 12PM | 75 | 60.8 | 52 | 59.9 | 27.38 | 0.0712 | 0.39 | 14.17 | 1
September | 19 | 12PM to 1PM | 77 | 62 | 53.1 | 62.4 | 28.25 | 0.0709 | 0.41 | 14.23 | 1
September | 19 | 1PM to 2PM | 75.9 | 61.6 | 53.1 | 62.4 | 27.99 | 0.071 | 0.41 | 14.2 | 1
September | 19 | 2PM to 3PM | 77 | 62 | 53.1 | 62.4 | 28.25 | 0.0709 | 0.41 | 14.23 | 1
September | 19 | 3PM to 4PM | 78.1 | 62.4 | 53.1 | 62.4 | 28.51 | 0.0708 | 0.41 | 14.26 | 1
September | 19 | 4PM to 5PM | 77 | 62.5 | 54 | 64.5 | 28.58 | 0.0709 | 0.42 | 14.24 | 1
September | 19 | 5PM to 6PM | 75 | 61.3 | 53.1 | 62.4 | 27.77 | 0.0712 | 0.41 | 14.18 | 1
September | 19 | 6PM to 7PM | 71.1 | 60.4 | 54 | 64.5 | 27.13 | 0.0717 | 0.42 | 14.08 | 1
September | 19 | 7PM to 8PM | 69.1 | 60.3 | 55 | 67.2 | 27.06 | 0.0719 | 0.44 | 14.03 | 1
September | 19 | 8PM to 9PM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
September | 19 | 9PM to 10PM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
September | 19 | 10PM to 11PM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
September | 19 | 11PM to 12AM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
September | 20 | 12AM to 1AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
September | 20 | 1AM to 2AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
September | 20 | 2AM to 3AM | 61 | 56.7 | 54 | 64.5 | 24.67 | 0.0731 | 0.42 | 13.81 | 1
September | 20 | 3AM to 4AM | 61 | 56.7 | 54 | 64.5 | 24.67 | 0.0731 | 0.42 | 13.81 | 1
September | 20 | 4AM to 5AM | 60.1 | 56.4 | 54 | 64.5 | 24.45 | 0.0732 | 0.42 | 13.79 | 1
September | 20 | 5AM to 6AM | 60.1 | 56.4 | 54 | 64.5 | 24.45 | 0.0732 | 0.42 | 13.79 | 1
September | 20 | 6AM to 7AM | 61 | 55.6 | 52 | 59.9 | 23.96 | 0.0731 | 0.39 | 13.8 | 1
September | 20 | 7AM to 8AM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
September | 20 | 8AM to 9AM | 68 | 60.4 | 55.9 | 69.4 | 27.15 | 0.0721 | 0.45 | 14.01 | 1
September | 20 | 9AM to 10AM | 73 | 61.1 | 54 | 64.5 | 27.61 | 0.0714 | 0.42 | 14.13 | 1
September | 20 | 10AM to 11AM | 75.9 | 62.1 | 54 | 64.5 | 28.32 | 0.071 | 0.42 | 14.21 | 1
September | 20 | 11AM to 12PM | 75 | 61.8 | 54 | 64.5 | 28.1 | 0.0712 | 0.42 | 14.18 | 1
September | 20 | 12PM to 1PM | 77 | 63 | 55 | 67.2 | 28.99 | 0.0709 | 0.44 | 14.25 | 1
September | 20 | 1PM to 2PM | 77 | 62.5 | 54 | 64.5 | 28.58 | 0.0709 | 0.42 | 14.24 | 1
September | 20 | 2PM to 3PM | 78.1 | 62.8 | 54 | 64.5 | 28.84 | 0.0707 | 0.42 | 14.27 | 1
September | 20 | 3PM to 4PM | 78.1 | 63.4 | 55 | 67.2 | 29.26 | 0.0707 | 0.44 | 14.27 | 1
September | 20 | 4PM to 5PM | 77 | 62.5 | 54 | 64.5 | 28.58 | 0.0709 | 0.42 | 14.24 | 1
September | 20 | 5PM to 6PM | 75 | 61.8 | 54 | 64.5 | 28.1 | 0.0712 | 0.42 | 14.18 | 1
September | 20 | 6PM to 7PM | 72 | 61.3 | 55 | 67.2 | 27.76 | 0.0715 | 0.44 | 14.11 | 1
September | 20 | 7PM to 8PM | 70 | 61.1 | 55.9 | 69.4 | 27.63 | 0.0718 | 0.45 | 14.07 | 1
September | 20 | 8PM to 9PM | 69.1 | 60.8 | 55.9 | 69.4 | 27.41 | 0.0719 | 0.45 | 14.04 | 1
September | 20 | 9PM to 10PM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
September | 20 | 10PM to 11PM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
September | 20 | 11PM to 12AM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
September | 21 | 12AM to 1AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
September | 21 | 1AM to 2AM | 66.9 | 60 | 55.9 | 69.4 | 26.88 | 0.0722 | 0.45 | 13.98 | 1
September | 21 | 2AM to 3AM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
September | 21 | 3AM to 4AM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
September | 21 | 4AM to 5AM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
September | 21 | 5AM to 6AM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
September | 21 | 6AM to 7AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
September | 21 | 7AM to 8AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
September | 21 | 8AM to 9AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
September | 21 | 9AM to 10AM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
September | 21 | 10AM to 11AM | 77 | 66.3 | 61 | 83.5 | 31.54 | 0.0708 | 0.54 | 14.3 | 1
September | 21 | 11AM to 12PM | 77 | 66.9 | 62.1 | 86.8 | 32.06 | 0.0708 | 0.56 | 14.31 | 1
September | 21 | 12PM to 1PM | 78.1 | 68.4 | 64 | 93.2 | 33.33 | 0.0706 | 0.6 | 14.36 | 1
September | 21 | 1PM to 2PM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
September | 21 | 2PM to 3PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 21 | 3PM to 4PM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
September | 21 | 4PM to 5PM | 66.9 | 65.6 | 64.9 | 96.2 | 31.06 | 0.0721 | 0.62 | 14.07 | 1
September | 21 | 5PM to 6PM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
September | 21 | 6PM to 7PM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
September | 21 | 7PM to 8PM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
September | 21 | 8PM to 9PM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
September | 21 | 9PM to 10PM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
September | 21 | 10PM to 11PM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
September | 21 | 11PM to 12AM | 66 | 64.7 | 64 | 93.2 | 30.36 | 0.0722 | 0.6 | 14.04 | 1
September | 22 | 12AM to 1AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
September | 22 | 1AM to 2AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
September | 22 | 2AM to 3AM | 64 | 62.7 | 62.1 | 86.8 | 28.88 | 0.0725 | 0.56 | 13.96 | 1
September | 22 | 3AM to 4AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
September | 22 | 4AM to 5AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 22 | 5AM to 6AM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
September | 22 | 6AM to 7AM | 60.1 | 58.7 | 57.9 | 74.7 | 26.03 | 0.0731 | 0.48 | 13.82 | 1
September | 22 | 7AM to 8AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
September | 22 | 8AM to 9AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
September | 22 | 9AM to 10AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
September | 22 | 10AM to 11AM | 73.9 | 64.2 | 59 | 77.7 | 29.89 | 0.0712 | 0.5 | 14.2 | 1
September | 22 | 11AM to 12PM | 77 | 62.5 | 54 | 64.5 | 28.58 | 0.0709 | 0.42 | 14.24 | 1
September | 22 | 12PM to 1PM | 79 | 62.2 | 52 | 59.9 | 28.35 | 0.0707 | 0.39 | 14.27 | 1
September | 22 | 1PM to 2PM | 80.1 | 63.5 | 54 | 64.5 | 29.33 | 0.0705 | 0.42 | 14.32 | 1
September | 22 | 2PM to 3PM | 80.1 | 63.5 | 54 | 64.5 | 29.33 | 0.0705 | 0.42 | 14.32 | 1
September | 22 | 3PM to 4PM | 80.1 | 63 | 53.1 | 62.4 | 29 | 0.0705 | 0.41 | 14.31 | 1
September | 22 | 4PM to 5PM | 79 | 63.1 | 54 | 64.5 | 29.06 | 0.0706 | 0.42 | 14.29 | 1
September | 22 | 5PM to 6PM | 75.9 | 61.6 | 53.1 | 62.4 | 27.99 | 0.071 | 0.41 | 14.2 | 1
September | 22 | 6PM to 7PM | 72 | 60.7 | 54 | 64.5 | 27.35 | 0.0716 | 0.42 | 14.1 | 1
September | 22 | 7PM to 8PM | 71.1 | 61 | 55 | 67.2 | 27.54 | 0.0717 | 0.44 | 14.09 | 1
September | 22 | 8PM to 9PM | 66.9 | 60 | 55.9 | 69.4 | 26.88 | 0.0722 | 0.45 | 13.98 | 1
September | 22 | 9PM to 10PM | 66 | 59.7 | 55.9 | 69.4 | 26.66 | 0.0723 | 0.45 | 13.96 | 1
September | 22 | 10PM to 11PM | 64.9 | 59.3 | 55.9 | 69.4 | 26.4 | 0.0725 | 0.45 | 13.93 | 1
September | 22 | 11PM to 12AM | 64 | 59 | 55.9 | 69.4 | 26.18 | 0.0726 | 0.45 | 13.91 | 1
September | 23 | 12AM to 1AM | 64 | 59 | 55.9 | 69.4 | 26.18 | 0.0726 | 0.45 | 13.91 | 1
September | 23 | 1AM to 2AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
September | 23 | 2AM to 3AM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
September | 23 | 3AM to 4AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
September | 23 | 4AM to 5AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
September | 23 | 5AM to 6AM | 61 | 56.7 | 54 | 64.5 | 24.67 | 0.0731 | 0.42 | 13.81 | 1
September | 23 | 6AM to 7AM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
September | 23 | 7AM to 8AM | 68 | 60.4 | 55.9 | 69.4 | 27.15 | 0.0721 | 0.45 | 14.01 | 1
September | 23 | 8AM to 9AM | 72 | 62.9 | 57.9 | 74.7 | 28.93 | 0.0715 | 0.48 | 14.14 | 1
September | 23 | 9AM to 10AM | 77 | 64.5 | 57.9 | 74.7 | 30.17 | 0.0708 | 0.48 | 14.27 | 1
September | 23 | 10AM to 11AM | 80.1 | 65 | 57 | 72.3 | 30.54 | 0.0704 | 0.47 | 14.34 | 1
September | 23 | 11AM to 12PM | 82 | 65.1 | 55.9 | 69.4 | 30.58 | 0.0702 | 0.45 | 14.39 | 1
September | 23 | 12PM to 1PM | 84 | 65.8 | 55.9 | 69.4 | 31.06 | 0.0699 | 0.45 | 14.44 | 1
September | 23 | 1PM to 2PM | 84.9 | 66.6 | 57 | 72.3 | 31.73 | 0.0698 | 0.47 | 14.47 | 1
September | 23 | 2PM to 3PM | 84 | 66.8 | 57.9 | 74.7 | 31.89 | 0.0699 | 0.48 | 14.46 | 1
September | 23 | 3PM to 4PM | 84 | 65.8 | 55.9 | 69.4 | 31.06 | 0.0699 | 0.45 | 14.44 | 1
September | 23 | 4PM to 5PM | 82 | 65.7 | 57 | 72.3 | 31.02 | 0.0702 | 0.47 | 14.4 | 1
September | 23 | 5PM to 6PM | 79 | 66.4 | 60.1 | 80.8 | 31.61 | 0.0705 | 0.52 | 14.34 | 1
September | 23 | 6PM to 7PM | 75.9 | 65.4 | 60.1 | 80.8 | 30.86 | 0.0709 | 0.52 | 14.26 | 1
September | 23 | 7PM to 8PM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
September | 23 | 8PM to 9PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
September | 23 | 9PM to 10PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
September | 23 | 10PM to 11PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
September | 23 | 11PM to 12AM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
September | 24 | 12AM to 1AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
September | 24 | 1AM to 2AM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
September | 24 | 2AM to 3AM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
September | 24 | 3AM to 4AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
September | 24 | 4AM to 5AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
September | 24 | 5AM to 6AM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
September | 24 | 6AM to 7AM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
September | 24 | 7AM to 8AM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
September | 24 | 8AM to 9AM | 73.9 | 65.3 | 61 | 83.5 | 30.79 | 0.0712 | 0.54 | 14.22 | 1
September | 24 | 9AM to 10AM | 79 | 65.2 | 57.9 | 74.7 | 30.65 | 0.0706 | 0.48 | 14.32 | 1
September | 24 | 10AM to 11AM | 82 | 66.7 | 59 | 77.7 | 31.87 | 0.0702 | 0.5 | 14.41 | 1
September | 24 | 11AM to 12PM | 82.9 | 67.6 | 60.1 | 80.8 | 32.58 | 0.07 | 0.52 | 14.45 | 1
September | 24 | 12PM to 1PM | 84 | 67.9 | 60.1 | 80.8 | 32.84 | 0.0699 | 0.52 | 14.48 | 1
September | 24 | 1PM to 2PM | 82.9 | 67.6 | 60.1 | 80.8 | 32.58 | 0.07 | 0.52 | 14.45 | 1
September | 24 | 2PM to 3PM | 84 | 69 | 62.1 | 86.8 | 33.78 | 0.0698 | 0.56 | 14.5 | 1
September | 24 | 3PM to 4PM | 84 | 68.4 | 61 | 83.5 | 33.26 | 0.0699 | 0.54 | 14.48 | 1
September | 24 | 4PM to 5PM | 82 | 67.3 | 60.1 | 80.8 | 32.36 | 0.0701 | 0.52 | 14.42 | 1
September | 24 | 5PM to 6PM | 80.1 | 67.8 | 62.1 | 86.8 | 32.81 | 0.0704 | 0.56 | 14.39 | 1
September | 24 | 6PM to 7PM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
September | 24 | 7PM to 8PM | 77 | 65.8 | 60.1 | 80.8 | 31.12 | 0.0708 | 0.52 | 14.29 | 1
September | 24 | 8PM to 9PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
September | 24 | 9PM to 10PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
September | 24 | 10PM to 11PM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
September | 24 | 11PM to 12AM | 73 | 65.7 | 62.1 | 86.8 | 31.09 | 0.0713 | 0.56 | 14.2 | 1
September | 25 | 12AM to 1AM | 72 | 64.1 | 60.1 | 80.8 | 29.89 | 0.0715 | 0.52 | 14.15 | 1
September | 25 | 1AM to 2AM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
September | 25 | 2AM to 3AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
September | 25 | 3AM to 4AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
September | 25 | 4AM to 5AM | 66.9 | 63 | 61 | 83.5 | 29.07 | 0.0721 | 0.54 | 14.03 | 1
September | 25 | 5AM to 6AM | 66.9 | 61.8 | 59 | 77.7 | 28.17 | 0.0722 | 0.5 | 14.01 | 1
September | 25 | 6AM to 7AM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
September | 25 | 7AM to 8AM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
September | 25 | 8AM to 9AM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
September | 25 | 9AM to 10AM | 80.1 | 66.7 | 60.1 | 80.8 | 31.87 | 0.0704 | 0.52 | 14.37 | 1
September | 25 | 10AM to 11AM | 82.9 | 67 | 59 | 77.7 | 32.09 | 0.07 | 0.5 | 14.44 | 1
September | 25 | 11AM to 12PM | 84 | 66.8 | 57.9 | 74.7 | 31.89 | 0.0699 | 0.48 | 14.46 | 1
September | 25 | 12PM to 1PM | 82 | 65.7 | 57 | 72.3 | 31.02 | 0.0702 | 0.47 | 14.4 | 1
September | 25 | 1PM to 2PM | 87.1 | 68.3 | 59 | 77.7 | 33.11 | 0.0695 | 0.5 | 14.55 | 1
September | 25 | 2PM to 3PM | 84.9 | 67 | 57.9 | 74.7 | 32.11 | 0.0698 | 0.48 | 14.48 | 1
September | 25 | 3PM to 4PM | 84.9 | 67.6 | 59 | 77.7 | 32.58 | 0.0698 | 0.5 | 14.49 | 1
September | 25 | 4PM to 5PM | 84 | 67.9 | 60.1 | 80.8 | 32.84 | 0.0699 | 0.52 | 14.48 | 1
September | 25 | 5PM to 6PM | 81 | 67.5 | 61 | 83.5 | 32.51 | 0.0703 | 0.54 | 14.4 | 1
September | 25 | 6PM to 7PM | 78.1 | 67.2 | 62.1 | 86.8 | 32.33 | 0.0706 | 0.56 | 14.34 | 1
September | 25 | 7PM to 8PM | 77 | 66.9 | 62.1 | 86.8 | 32.06 | 0.0708 | 0.56 | 14.31 | 1
September | 25 | 8PM to 9PM | 77 | 66.9 | 62.1 | 86.8 | 32.06 | 0.0708 | 0.56 | 14.31 | 1
September | 25 | 9PM to 10PM | 73.9 | 66.5 | 63 | 89.6 | 31.76 | 0.0711 | 0.58 | 14.24 | 1
September | 25 | 10PM to 11PM | 71.1 | 65.6 | 63 | 89.6 | 31.05 | 0.0715 | 0.58 | 14.16 | 1
September | 25 | 11PM to 12AM | 75 | 65.7 | 61 | 83.5 | 31.06 | 0.071 | 0.54 | 14.24 | 1
September | 26 | 12AM to 1AM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
September | 26 | 1AM to 2AM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
September | 26 | 2AM to 3AM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
September | 26 | 3AM to 4AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
September | 26 | 4AM to 5AM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
September | 26 | 5AM to 6AM | 68 | 64 | 62.1 | 86.8 | 29.85 | 0.072 | 0.56 | 14.07 | 1
September | 26 | 6AM to 7AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
September | 26 | 7AM to 8AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
September | 26 | 8AM to 9AM | 72 | 67.1 | 64.9 | 96.2 | 32.3 | 0.0714 | 0.62 | 14.2 | 1
September | 26 | 9AM to 10AM | 75 | 69.4 | 66.9 | 103.2 | 34.15 | 0.0709 | 0.67 | 14.31 | 1
September | 26 | 10AM to 11AM | 77 | 69.4 | 66 | 100 | 34.13 | 0.0707 | 0.64 | 14.35 | 1
September | 26 | 11AM to 12PM | 82 | 70.1 | 64.9 | 96.2 | 34.78 | 0.07 | 0.62 | 14.47 | 1
September | 26 | 12PM to 1PM | 81 | 68.6 | 63 | 89.6 | 33.48 | 0.0702 | 0.58 | 14.42 | 1
September | 26 | 1PM to 2PM | 82 | 68.4 | 62.1 | 86.8 | 33.3 | 0.0701 | 0.56 | 14.44 | 1
September | 26 | 2PM to 3PM | 84 | 69 | 62.1 | 86.8 | 33.78 | 0.0698 | 0.56 | 14.5 | 1
September | 26 | 3PM to 4PM | 82 | 68.4 | 62.1 | 86.8 | 33.3 | 0.0701 | 0.56 | 14.44 | 1
September | 26 | 4PM to 5PM | 82 | 69 | 63 | 89.6 | 33.75 | 0.0701 | 0.58 | 14.45 | 1
September | 26 | 5PM to 6PM | 81 | 68.6 | 63 | 89.6 | 33.48 | 0.0702 | 0.58 | 14.42 | 1
September | 26 | 6PM to 7PM | 78.1 | 68.4 | 64 | 93.2 | 33.33 | 0.0706 | 0.6 | 14.36 | 1
September | 26 | 7PM to 8PM | 78.1 | 68.4 | 64 | 93.2 | 33.33 | 0.0706 | 0.6 | 14.36 | 1
September | 26 | 8PM to 9PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
September | 26 | 9PM to 10PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
September | 26 | 10PM to 11PM | 75.9 | 67.8 | 64 | 93.2 | 32.8 | 0.0709 | 0.6 | 14.3 | 1
September | 26 | 11PM to 12AM | 75 | 68.1 | 64.9 | 96.2 | 33.05 | 0.071 | 0.62 | 14.29 | 1
September | 27 | 12AM to 1AM | 75 | 68.1 | 64.9 | 96.2 | 33.05 | 0.071 | 0.62 | 14.29 | 1
September | 27 | 1AM to 2AM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
September | 27 | 2AM to 3AM | 73.9 | 68.5 | 66 | 100 | 33.37 | 0.0711 | 0.64 | 14.27 | 1
September | 27 | 3AM to 4AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 27 | 4AM to 5AM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
September | 27 | 5AM to 6AM | 73 | 67.5 | 64.9 | 96.2 | 32.56 | 0.0712 | 0.62 | 14.23 | 1
September | 27 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
September | 27 | 7AM to 8AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 27 | 8AM to 9AM | 72 | 69.2 | 68 | 107.2 | 34.02 | 0.0713 | 0.69 | 14.24 | 1
September | 27 | 9AM to 10AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
September | 27 | 10AM to 11AM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 27 | 11AM to 12PM | 73.9 | 69.8 | 68 | 107.2 | 34.51 | 0.071 | 0.69 | 14.29 | 1
September | 27 | 12PM to 1PM | 73.9 | 70.5 | 69.1 | 111.4 | 35.16 | 0.071 | 0.72 | 14.31 | 1
September | 27 | 1PM to 2PM | 75.9 | 71.1 | 69.1 | 111.4 | 35.65 | 0.0708 | 0.72 | 14.36 | 1
September | 27 | 2PM to 3PM | 77 | 71.4 | 69.1 | 111.4 | 35.91 | 0.0706 | 0.72 | 14.39 | 1
September | 27 | 3PM to 4PM | 78.1 | 72.3 | 70 | 115 | 36.74 | 0.0704 | 0.74 | 14.43 | 1
September | 27 | 4PM to 5PM | 75.9 | 72.4 | 71.1 | 119.4 | 36.9 | 0.0707 | 0.77 | 14.38 | 1
September | 27 | 5PM to 6PM | 73.9 | 71.9 | 71.1 | 119.4 | 36.41 | 0.071 | 0.77 | 14.33 | 1
September | 27 | 6PM to 7PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 27 | 7PM to 8PM | 73 | 70.2 | 69.1 | 111.4 | 34.93 | 0.0711 | 0.72 | 14.28 | 1
September | 27 | 8PM to 9PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
September | 27 | 9PM to 10PM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 27 | 10PM to 11PM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 27 | 11PM to 12AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 28 | 12AM to 1AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 28 | 1AM to 2AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 28 | 2AM to 3AM | 72 | 69.9 | 69.1 | 111.4 | 34.67 | 0.0713 | 0.72 | 14.25 | 1
September | 28 | 3AM to 4AM | 71.1 | 68.9 | 68 | 107.2 | 33.8 | 0.0714 | 0.69 | 14.22 | 1
September | 28 | 4AM to 5AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
September | 28 | 5AM to 6AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
September | 28 | 6AM to 7AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
September | 28 | 7AM to 8AM | 71.1 | 67.6 | 66 | 100 | 32.66 | 0.0715 | 0.64 | 14.19 | 1
September | 28 | 8AM to 9AM | 73 | 69.5 | 68 | 107.2 | 34.29 | 0.0712 | 0.69 | 14.27 | 1
September | 28 | 9AM to 10AM | 75 | 70.8 | 69.1 | 111.4 | 35.42 | 0.0709 | 0.72 | 14.33 | 1
September | 28 | 10AM to 11AM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
September | 28 | 11AM to 12PM | 73 | 70.9 | 70 | 115 | 35.49 | 0.0711 | 0.74 | 14.29 | 1
September | 28 | 12PM to 1PM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
September | 28 | 1PM to 2PM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
September | 28 | 2PM to 3PM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
September | 28 | 3PM to 4PM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
September | 28 | 4PM to 5PM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
September | 28 | 5PM to 6PM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
September | 28 | 6PM to 7PM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
September | 28 | 7PM to 8PM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
September | 28 | 8PM to 9PM | 60.1 | 56.4 | 54 | 64.5 | 24.45 | 0.0732 | 0.42 | 13.79 | 1
September | 28 | 9PM to 10PM | 59 | 55.9 | 54 | 64.5 | 24.19 | 0.0733 | 0.42 | 13.76 | 1
September | 28 | 10PM to 11PM | 57 | 54.7 | 53.1 | 62.4 | 23.37 | 0.0736 | 0.41 | 13.7 | 1
September | 28 | 11PM to 12AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
September | 29 | 12AM to 1AM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
September | 29 | 1AM to 2AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
September | 29 | 2AM to 3AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
September | 29 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 58 | 21.72 | 0.0742 | 0.38 | 13.58 | 1
September | 29 | 4AM to 5AM | 54 | 52.3 | 51.1 | 58 | 21.94 | 0.0741 | 0.38 | 13.61 | 1
September | 29 | 5AM to 6AM | 55 | 52.7 | 51.1 | 58 | 22.2 | 0.074 | 0.38 | 13.63 | 1
September | 29 | 6AM to 7AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
September | 29 | 7AM to 8AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
September | 29 | 8AM to 9AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
September | 29 | 9AM to 10AM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
September | 29 | 10AM to 11AM | 66.9 | 61.2 | 57.9 | 74.7 | 27.7 | 0.0722 | 0.48 | 14 | 1
September | 29 | 11AM to 12PM | 68 | 62.2 | 59 | 77.7 | 28.43 | 0.072 | 0.5 | 14.04 | 1
September | 29 | 12PM to 1PM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
September | 29 | 1PM to 2PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
September | 29 | 2PM to 3PM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
September | 29 | 3PM to 4PM | 69.1 | 62.5 | 59 | 77.7 | 28.7 | 0.0719 | 0.5 | 14.07 | 1
September | 29 | 4PM to 5PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
September | 29 | 5PM to 6PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
September | 29 | 6PM to 7PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
September | 29 | 7PM to 8PM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
September | 29 | 8PM to 9PM | 66.9 | 61.2 | 57.9 | 74.7 | 27.7 | 0.0722 | 0.48 | 14 | 1
September | 29 | 9PM to 10PM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
September | 29 | 10PM to 11PM | 64.9 | 60.5 | 57.9 | 74.7 | 27.22 | 0.0725 | 0.48 | 13.95 | 1
September | 29 | 11PM to 12AM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
September | 30 | 12AM to 1AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 30 | 1AM to 2AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
September | 30 | 2AM to 3AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 30 | 3AM to 4AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 30 | 4AM to 5AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 30 | 5AM to 6AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 30 | 6AM to 7AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 30 | 7AM to 8AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
September | 30 | 8AM to 9AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
September | 30 | 9AM to 10AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
September | 30 | 10AM to 11AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
September | 30 | 11AM to 12PM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
September | 30 | 12PM to 1PM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
September | 30 | 1PM to 2PM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
September | 30 | 2PM to 3PM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
September | 30 | 3PM to 4PM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
September | 30 | 4PM to 5PM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
September | 30 | 5PM to 6PM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
September | 30 | 6PM to 7PM | 62.1 | 58.9 | 57 | 72.3 | 26.13 | 0.0729 | 0.47 | 13.86 | 1
September | 30 | 7PM to 8PM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
September | 30 | 8PM to 9PM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
September | 30 | 9PM to 10PM | 61.3 | 59.6 | 58.6 | 76.7 | 26.64 | 0.0729 | 0.5 | 13.86 | 1
September | 30 | 10PM to 11PM | 61.9 | 60.3 | 59.4 | 78.7 | 27.09 | 0.0729 | 0.51 | 13.88 | 1
September | 30 | 11PM to 12AM | 62.2 | 60.8 | 60.1 | 80.8 | 27.51 | 0.0728 | 0.52 | 13.9 | 1
October | 1 | 12AM to 1AM | 62.8 | 61.5 | 60.8 | 82.9 | 27.97 | 0.0727 | 0.54 | 13.92 | 1
October | 1 | 1AM to 2AM | 63.1 | 62.1 | 61.5 | 85.1 | 28.4 | 0.0726 | 0.55 | 13.93 | 1
October | 1 | 2AM to 3AM | 63.7 | 62.7 | 62.2 | 87.3 | 28.88 | 0.0726 | 0.57 | 13.95 | 1
October | 1 | 3AM to 4AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
October | 1 | 4AM to 5AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
October | 1 | 5AM to 6AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
October | 1 | 6AM to 7AM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
October | 1 | 7AM to 8AM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
October | 1 | 8AM to 9AM | 66.9 | 65 | 64 | 93.2 | 30.58 | 0.0721 | 0.6 | 14.06 | 1
October | 1 | 9AM to 10AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
October | 1 | 10AM to 11AM | 68 | 65.9 | 64.9 | 96.2 | 31.32 | 0.0719 | 0.62 | 14.1 | 1
October | 1 | 11AM to 12PM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
October | 1 | 12PM to 1PM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
October | 1 | 1PM to 2PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
October | 1 | 2PM to 3PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
October | 1 | 3PM to 4PM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
October | 1 | 4PM to 5PM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
October | 1 | 5PM to 6PM | 73 | 68.2 | 66 | 100 | 33.15 | 0.0712 | 0.64 | 14.24 | 1
October | 1 | 6PM to 7PM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
October | 1 | 7PM to 8PM | 71.1 | 68.2 | 66.9 | 103.2 | 33.17 | 0.0714 | 0.67 | 14.2 | 1
October | 1 | 8PM to 9PM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
October | 1 | 9PM to 10PM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
October | 1 | 10PM to 11PM | 69.1 | 67.6 | 66.9 | 103.2 | 32.68 | 0.0717 | 0.67 | 14.15 | 1
October | 1 | 11PM to 12AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
October | 2 | 12AM to 1AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
October | 2 | 1AM to 2AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
October | 2 | 2AM to 3AM | 68 | 67.3 | 66.9 | 103.2 | 32.42 | 0.0719 | 0.67 | 14.12 | 1
October | 2 | 3AM to 4AM | 66 | 66 | 66 | 100 | 31.42 | 0.0722 | 0.64 | 14.06 | 1
October | 2 | 4AM to 5AM | 64.9 | 64.9 | 64.9 | 96.2 | 30.57 | 0.0723 | 0.62 | 14.02 | 1
October | 2 | 5AM to 6AM | 64 | 64 | 64 | 93.2 | 29.87 | 0.0725 | 0.6 | 13.98 | 1
October | 2 | 6AM to 7AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
October | 2 | 7AM to 8AM | 64.9 | 64.3 | 64 | 93.2 | 30.1 | 0.0723 | 0.6 | 14.01 | 1
October | 2 | 8AM to 9AM | 70 | 66.5 | 64.9 | 96.2 | 31.81 | 0.0716 | 0.62 | 14.15 | 1
October | 2 | 9AM to 10AM | 73.9 | 67.2 | 64 | 93.2 | 32.31 | 0.0711 | 0.6 | 14.25 | 1
October | 2 | 10AM to 11AM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
October | 2 | 11AM to 12PM | 77 | 67.5 | 63 | 89.6 | 32.51 | 0.0707 | 0.58 | 14.32 | 1
October | 2 | 12PM to 1PM | 77 | 68.1 | 64 | 93.2 | 33.06 | 0.0707 | 0.6 | 14.33 | 1
October | 2 | 1PM to 2PM | 80.1 | 67.8 | 62.1 | 86.8 | 32.81 | 0.0704 | 0.56 | 14.39 | 1
October | 2 | 2PM to 3PM | 80.1 | 68.4 | 63 | 89.6 | 33.26 | 0.0703 | 0.58 | 14.4 | 1
October | 2 | 3PM to 4PM | 80.1 | 69 | 64 | 93.2 | 33.81 | 0.0703 | 0.6 | 14.41 | 1
October | 2 | 4PM to 5PM | 78.1 | 67.8 | 63 | 89.6 | 32.77 | 0.0706 | 0.58 | 14.35 | 1
October | 2 | 5PM to 6PM | 75.9 | 67.1 | 63 | 89.6 | 32.24 | 0.0709 | 0.58 | 14.29 | 1
October | 2 | 6PM to 7PM | 73.9 | 67.2 | 64 | 93.2 | 32.31 | 0.0711 | 0.6 | 14.25 | 1
October | 2 | 7PM to 8PM | 71.1 | 66.9 | 64.9 | 96.2 | 32.08 | 0.0715 | 0.62 | 14.18 | 1
October | 2 | 8PM to 9PM | 69.1 | 66.3 | 64.9 | 96.2 | 31.59 | 0.0718 | 0.62 | 14.13 | 1
October | 2 | 9PM to 10PM | 64 | 59 | 55.9 | 69.4 | 26.18 | 0.0726 | 0.45 | 13.91 | 1
October | 2 | 10PM to 11PM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
October | 2 | 11PM to 12AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
October | 3 | 12AM to 1AM | 59 | 56.6 | 55 | 67.2 | 24.6 | 0.0733 | 0.44 | 13.77 | 1
October | 3 | 1AM to 2AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
October | 3 | 2AM to 3AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
October | 3 | 3AM to 4AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 3 | 4AM to 5AM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
October | 3 | 5AM to 6AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 3 | 6AM to 7AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 3 | 7AM to 8AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 3 | 8AM to 9AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
October | 3 | 9AM to 10AM | 66.9 | 57.9 | 52 | 59.9 | 25.41 | 0.0723 | 0.39 | 13.95 | 1
October | 3 | 10AM to 11AM | 71.1 | 61 | 55 | 67.2 | 27.54 | 0.0717 | 0.44 | 14.09 | 1
October | 3 | 11AM to 12PM | 70 | 56.2 | 46 | 47.9 | 24.27 | 0.0719 | 0.31 | 14 | 1
October | 3 | 12PM to 1PM | 71.1 | 56.6 | 46 | 47.9 | 24.53 | 0.0718 | 0.31 | 14.03 | 1
October | 3 | 1PM to 2PM | 71.1 | 56.1 | 45 | 45.9 | 24.23 | 0.0718 | 0.3 | 14.02 | 1
October | 3 | 2PM to 3PM | 72 | 55.3 | 42.1 | 41.1 | 23.69 | 0.0717 | 0.27 | 14.03 | 1
October | 3 | 3PM to 4PM | 71.1 | 55.3 | 43 | 42.5 | 23.7 | 0.0718 | 0.28 | 14.01 | 1
October | 3 | 4PM to 5PM | 70 | 54.9 | 43 | 42.5 | 23.44 | 0.072 | 0.28 | 13.98 | 1
October | 3 | 5PM to 6PM | 66 | 53.3 | 43 | 42.5 | 22.48 | 0.0725 | 0.28 | 13.88 | 1
October | 3 | 6PM to 7PM | 62.1 | 52.5 | 45 | 45.9 | 22.04 | 0.073 | 0.3 | 13.78 | 1
October | 3 | 7PM to 8PM | 57 | 50.9 | 46 | 47.9 | 21.12 | 0.0737 | 0.31 | 13.66 | 1
October | 3 | 8PM to 9PM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
October | 3 | 9PM to 10PM | 55 | 50.5 | 46.9 | 49.6 | 20.9 | 0.074 | 0.32 | 13.61 | 1
October | 3 | 10PM to 11PM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
October | 3 | 11PM to 12AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
October | 4 | 12AM to 1AM | 50 | 48.3 | 46.9 | 49.6 | 19.67 | 0.0747 | 0.32 | 13.47 | 1
October | 4 | 1AM to 2AM | 50 | 48.3 | 46.9 | 49.6 | 19.67 | 0.0747 | 0.32 | 13.47 | 1
October | 4 | 2AM to 3AM | 48 | 47.4 | 46.9 | 49.6 | 19.19 | 0.075 | 0.32 | 13.42 | 1
October | 4 | 3AM to 4AM | 46.9 | 46.5 | 46 | 47.9 | 18.67 | 0.0752 | 0.31 | 13.39 | 1
October | 4 | 4AM to 5AM | 46 | 45.5 | 45 | 45.9 | 18.15 | 0.0753 | 0.3 | 13.36 | 1
October | 4 | 5AM to 6AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
October | 4 | 6AM to 7AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
October | 4 | 7AM to 8AM | 46.9 | 45.4 | 44.1 | 44.4 | 18.13 | 0.0752 | 0.29 | 13.38 | 1
October | 4 | 8AM to 9AM | 50 | 46.3 | 43 | 42.5 | 18.59 | 0.0748 | 0.28 | 13.45 | 1
October | 4 | 9AM to 10AM | 57 | 49.1 | 42.1 | 41.1 | 20.07 | 0.0738 | 0.27 | 13.63 | 1
October | 4 | 10AM to 11AM | 59 | 49.9 | 42.1 | 41.1 | 20.55 | 0.0735 | 0.27 | 13.69 | 1
October | 4 | 11AM to 12PM | 62.1 | 50.4 | 39.9 | 37.8 | 20.77 | 0.0731 | 0.25 | 13.76 | 1
October | 4 | 12PM to 1PM | 66 | 52.9 | 42.1 | 41.1 | 22.25 | 0.0725 | 0.27 | 13.87 | 1
October | 4 | 1PM to 2PM | 66.9 | 54.1 | 44.1 | 44.4 | 22.98 | 0.0724 | 0.29 | 13.91 | 1
October | 4 | 2PM to 3PM | 70 | 55.7 | 45 | 45.9 | 23.96 | 0.0719 | 0.3 | 13.99 | 1
October | 4 | 3PM to 4PM | 69.1 | 55.8 | 46 | 47.9 | 24.05 | 0.0721 | 0.31 | 13.97 | 1
October | 4 | 4PM to 5PM | 69.1 | 55.8 | 46 | 47.9 | 24.05 | 0.0721 | 0.31 | 13.97 | 1
October | 4 | 5PM to 6PM | 68 | 56.3 | 48 | 51.6 | 24.37 | 0.0722 | 0.34 | 13.96 | 1
October | 4 | 6PM to 7PM | 66 | 56 | 48.9 | 53.4 | 24.17 | 0.0724 | 0.35 | 13.91 | 1
October | 4 | 7PM to 8PM | 61 | 54.5 | 50 | 55.6 | 23.29 | 0.0731 | 0.36 | 13.78 | 1
October | 4 | 8PM to 9PM | 63 | 54.8 | 48.9 | 53.4 | 23.43 | 0.0729 | 0.35 | 13.83 | 1
October | 4 | 9PM to 10PM | 63 | 55.3 | 50 | 55.6 | 23.77 | 0.0728 | 0.36 | 13.84 | 1
October | 4 | 10PM to 11PM | 62.1 | 55 | 50 | 55.6 | 23.55 | 0.073 | 0.36 | 13.81 | 1
October | 4 | 11PM to 12AM | 61 | 54.5 | 50 | 55.6 | 23.29 | 0.0731 | 0.36 | 13.78 | 1
October | 5 | 12AM to 1AM | 61 | 54.5 | 50 | 55.6 | 23.29 | 0.0731 | 0.36 | 13.78 | 1
October | 5 | 1AM to 2AM | 59 | 53.8 | 50 | 55.6 | 22.81 | 0.0734 | 0.36 | 13.73 | 1
October | 5 | 2AM to 3AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
October | 5 | 3AM to 4AM | 55.9 | 52.5 | 50 | 55.6 | 22.06 | 0.0738 | 0.36 | 13.65 | 1
October | 5 | 4AM to 5AM | 55 | 52.7 | 51.1 | 58 | 22.2 | 0.074 | 0.38 | 13.63 | 1
October | 5 | 5AM to 6AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 5 | 6AM to 7AM | 48.9 | 48.9 | 48.9 | 53.4 | 20.01 | 0.0749 | 0.35 | 13.46 | 1
October | 5 | 7AM to 8AM | 48.9 | 48.4 | 48 | 51.6 | 19.73 | 0.0749 | 0.34 | 13.45 | 1
October | 5 | 8AM to 9AM | 53.1 | 50.2 | 48 | 51.6 | 20.74 | 0.0743 | 0.34 | 13.56 | 1
October | 5 | 9AM to 10AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
October | 5 | 10AM to 11AM | 61 | 55.1 | 51.1 | 58 | 23.65 | 0.0731 | 0.38 | 13.79 | 1
October | 5 | 11AM to 12PM | 66 | 58.1 | 53.1 | 62.4 | 25.57 | 0.0724 | 0.41 | 13.94 | 1
October | 5 | 12PM to 1PM | 68 | 58.8 | 53.1 | 62.4 | 26.05 | 0.0721 | 0.41 | 13.99 | 1
October | 5 | 1PM to 2PM | 68 | 58.8 | 53.1 | 62.4 | 26.05 | 0.0721 | 0.41 | 13.99 | 1
October | 5 | 2PM to 3PM | 69.1 | 59.7 | 54 | 64.5 | 26.65 | 0.072 | 0.42 | 14.03 | 1
October | 5 | 3PM to 4PM | 68 | 58.3 | 52 | 59.9 | 25.67 | 0.0721 | 0.39 | 13.98 | 1
October | 5 | 4PM to 5PM | 64.9 | 56.7 | 51.1 | 58 | 24.61 | 0.0726 | 0.38 | 13.9 | 1
October | 5 | 5PM to 6PM | 62.1 | 55.5 | 51.1 | 58 | 23.91 | 0.073 | 0.38 | 13.82 | 1
October | 5 | 6PM to 7PM | 59 | 53.8 | 50 | 55.6 | 22.81 | 0.0734 | 0.36 | 13.73 | 1
October | 5 | 7PM to 8PM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
October | 5 | 8PM to 9PM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
October | 5 | 9PM to 10PM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
October | 5 | 10PM to 11PM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
October | 5 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 49.6 | 19.93 | 0.0746 | 0.32 | 13.5 | 1
October | 6 | 12AM to 1AM | 50 | 48.3 | 46.9 | 49.6 | 19.67 | 0.0747 | 0.32 | 13.47 | 1
October | 6 | 1AM to 2AM | 48.9 | 48.4 | 48 | 51.6 | 19.73 | 0.0749 | 0.34 | 13.45 | 1
October | 6 | 2AM to 3AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
October | 6 | 3AM to 4AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
October | 6 | 4AM to 5AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
October | 6 | 5AM to 6AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
October | 6 | 6AM to 7AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
October | 6 | 7AM to 8AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
October | 6 | 8AM to 9AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
October | 6 | 9AM to 10AM | 57.9 | 51.3 | 46 | 47.9 | 21.34 | 0.0736 | 0.31 | 13.68 | 1
October | 6 | 10AM to 11AM | 61 | 52.6 | 46 | 47.9 | 22.08 | 0.0732 | 0.31 | 13.76 | 1
October | 6 | 11AM to 12PM | 64 | 52.9 | 44.1 | 44.4 | 22.28 | 0.0728 | 0.29 | 13.83 | 1
October | 6 | 12PM to 1PM | 64.9 | 52.8 | 43 | 42.5 | 22.21 | 0.0727 | 0.28 | 13.85 | 1
October | 6 | 1PM to 2PM | 66.9 | 54.1 | 44.1 | 44.4 | 22.98 | 0.0724 | 0.29 | 13.91 | 1
October | 6 | 2PM to 3PM | 68 | 55.4 | 46 | 47.9 | 23.79 | 0.0722 | 0.31 | 13.95 | 1
October | 6 | 3PM to 4PM | 69.1 | 54.1 | 42.1 | 41.1 | 22.99 | 0.0721 | 0.27 | 13.95 | 1
October | 6 | 4PM to 5PM | 68 | 53.7 | 42.1 | 41.1 | 22.73 | 0.0722 | 0.27 | 13.92 | 1
October | 6 | 5PM to 6PM | 64.9 | 51.2 | 39 | 36.4 | 21.26 | 0.0727 | 0.24 | 13.83 | 1
October | 6 | 6PM to 7PM | 62.1 | 50 | 39 | 36.4 | 20.57 | 0.0731 | 0.24 | 13.75 | 1
October | 6 | 7PM to 8PM | 59 | 50.3 | 43 | 42.5 | 20.77 | 0.0735 | 0.28 | 13.69 | 1
October | 6 | 8PM to 9PM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
October | 6 | 9PM to 10PM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
October | 6 | 10PM to 11PM | 53.1 | 50.2 | 48 | 51.6 | 20.74 | 0.0743 | 0.34 | 13.56 | 1
October | 6 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
October | 7 | 12AM to 1AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
October | 7 | 1AM to 2AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
October | 7 | 2AM to 3AM | 51.1 | 48.3 | 46 | 47.9 | 19.67 | 0.0746 | 0.31 | 13.5 | 1
October | 7 | 3AM to 4AM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
October | 7 | 4AM to 5AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
October | 7 | 5AM to 6AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
October | 7 | 6AM to 7AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
October | 7 | 7AM to 8AM | 52 | 48.7 | 46 | 47.9 | 19.89 | 0.0745 | 0.31 | 13.52 | 1
October | 7 | 8AM to 9AM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
October | 7 | 9AM to 10AM | 60.1 | 52.6 | 46.9 | 49.6 | 22.12 | 0.0733 | 0.32 | 13.74 | 1
October | 7 | 10AM to 11AM | 66.9 | 53.6 | 43 | 42.5 | 22.69 | 0.0724 | 0.28 | 13.9 | 1
October | 7 | 11AM to 12PM | 69.1 | 55 | 44.1 | 44.4 | 23.5 | 0.0721 | 0.29 | 13.96 | 1
October | 7 | 12PM to 1PM | 71.1 | 56.1 | 45 | 45.9 | 24.23 | 0.0718 | 0.3 | 14.02 | 1
October | 7 | 1PM to 2PM | 73 | 55.3 | 41 | 39.4 | 23.69 | 0.0716 | 0.26 | 14.05 | 1
October | 7 | 2PM to 3PM | 73.9 | 55.2 | 39.9 | 37.8 | 23.65 | 0.0715 | 0.25 | 14.07 | 1
October | 7 | 3PM to 4PM | 75.9 | 55.7 | 39 | 36.4 | 23.92 | 0.0712 | 0.24 | 14.12 | 1
October | 7 | 4PM to 5PM | 73.9 | 55.2 | 39.9 | 37.8 | 23.65 | 0.0715 | 0.25 | 14.07 | 1
October | 7 | 5PM to 6PM | 70 | 55.7 | 45 | 45.9 | 23.96 | 0.0719 | 0.3 | 13.99 | 1
October | 7 | 6PM to 7PM | 66 | 55 | 46.9 | 49.6 | 23.57 | 0.0725 | 0.32 | 13.9 | 1
October | 7 | 7PM to 8PM | 64 | 53.8 | 46 | 47.9 | 22.82 | 0.0727 | 0.31 | 13.84 | 1
October | 7 | 8PM to 9PM | 63 | 53.8 | 46.9 | 49.6 | 22.82 | 0.0729 | 0.32 | 13.82 | 1
October | 7 | 9PM to 10PM | 61 | 53.5 | 48 | 51.6 | 22.66 | 0.0731 | 0.34 | 13.77 | 1
October | 7 | 10PM to 11PM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
October | 7 | 11PM to 12AM | 57.9 | 51.7 | 46.9 | 49.6 | 21.6 | 0.0736 | 0.32 | 13.68 | 1
October | 8 | 12AM to 1AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
October | 8 | 1AM to 2AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
October | 8 | 2AM to 3AM | 55 | 50.5 | 46.9 | 49.6 | 20.9 | 0.074 | 0.32 | 13.61 | 1
October | 8 | 3AM to 4AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
October | 8 | 4AM to 5AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
October | 8 | 5AM to 6AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
October | 8 | 6AM to 7AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
October | 8 | 7AM to 8AM | 55.9 | 51.9 | 48.9 | 53.4 | 21.72 | 0.0739 | 0.35 | 13.64 | 1
October | 8 | 8AM to 9AM | 64 | 55.2 | 48.9 | 53.4 | 23.69 | 0.0727 | 0.35 | 13.86 | 1
October | 8 | 9AM to 10AM | 68 | 58.8 | 53.1 | 62.4 | 26.05 | 0.0721 | 0.41 | 13.99 | 1
October | 8 | 10AM to 11AM | 73.9 | 62 | 55 | 67.2 | 28.25 | 0.0713 | 0.44 | 14.16 | 1
October | 8 | 11AM to 12PM | 75 | 62.8 | 55.9 | 69.4 | 28.86 | 0.0711 | 0.45 | 14.2 | 1
October | 8 | 12PM to 1PM | 75.9 | 63.7 | 57 | 72.3 | 29.52 | 0.071 | 0.47 | 14.23 | 1
October | 8 | 1PM to 2PM | 80.1 | 65.5 | 57.9 | 74.7 | 30.92 | 0.0704 | 0.48 | 14.35 | 1
October | 8 | 2PM to 3PM | 81 | 65.8 | 57.9 | 74.7 | 31.14 | 0.0703 | 0.48 | 14.37 | 1
October | 8 | 3PM to 4PM | 81 | 65.8 | 57.9 | 74.7 | 31.14 | 0.0703 | 0.48 | 14.37 | 1
October | 8 | 4PM to 5PM | 80.1 | 65.5 | 57.9 | 74.7 | 30.92 | 0.0704 | 0.48 | 14.35 | 1
October | 8 | 5PM to 6PM | 75 | 63.9 | 57.9 | 74.7 | 29.68 | 0.0711 | 0.48 | 14.22 | 1
October | 8 | 6PM to 7PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
October | 8 | 7PM to 8PM | 69.1 | 62.5 | 59 | 77.7 | 28.7 | 0.0719 | 0.5 | 14.07 | 1
October | 8 | 8PM to 9PM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
October | 8 | 9PM to 10PM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
October | 8 | 10PM to 11PM | 64 | 60.1 | 57.9 | 74.7 | 27 | 0.0726 | 0.48 | 13.92 | 1
October | 8 | 11PM to 12AM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
October | 9 | 12AM to 1AM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
October | 9 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
October | 9 | 2AM to 3AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
October | 9 | 3AM to 4AM | 59 | 55.9 | 54 | 64.5 | 24.19 | 0.0733 | 0.42 | 13.76 | 1
October | 9 | 4AM to 5AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
October | 9 | 5AM to 6AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
October | 9 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 62.4 | 23.11 | 0.0738 | 0.41 | 13.67 | 1
October | 9 | 7AM to 8AM | 64 | 59 | 55.9 | 69.4 | 26.18 | 0.0726 | 0.45 | 13.91 | 1
October | 9 | 8AM to 9AM | 70 | 62.2 | 57.9 | 74.7 | 28.45 | 0.0718 | 0.48 | 14.08 | 1
October | 9 | 9AM to 10AM | 72 | 62.9 | 57.9 | 74.7 | 28.93 | 0.0715 | 0.48 | 14.14 | 1
October | 9 | 10AM to 11AM | 75.9 | 64.8 | 59 | 77.7 | 30.37 | 0.071 | 0.5 | 14.25 | 1
October | 9 | 11AM to 12PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
October | 9 | 12PM to 1PM | 79 | 65.8 | 59 | 77.7 | 31.12 | 0.0705 | 0.5 | 14.33 | 1
October | 9 | 1PM to 2PM | 81 | 67 | 60.1 | 80.8 | 32.09 | 0.0703 | 0.52 | 14.39 | 1
October | 9 | 2PM to 3PM | 82 | 67.3 | 60.1 | 80.8 | 32.36 | 0.0701 | 0.52 | 14.42 | 1
October | 9 | 3PM to 4PM | 82 | 67.3 | 60.1 | 80.8 | 32.36 | 0.0701 | 0.52 | 14.42 | 1
October | 9 | 4PM to 5PM | 80.1 | 66.7 | 60.1 | 80.8 | 31.87 | 0.0704 | 0.52 | 14.37 | 1
October | 9 | 5PM to 6PM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
October | 9 | 6PM to 7PM | 73 | 65 | 61 | 83.5 | 30.57 | 0.0713 | 0.54 | 14.19 | 1
October | 9 | 7PM to 8PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
October | 9 | 8PM to 9PM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
October | 9 | 9PM to 10PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
October | 9 | 10PM to 11PM | 66 | 62.7 | 61 | 83.5 | 28.85 | 0.0723 | 0.54 | 14.01 | 1
October | 9 | 11PM to 12AM | 66 | 62.7 | 61 | 83.5 | 28.85 | 0.0723 | 0.54 | 14.01 | 1
October | 10 | 12AM to 1AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
October | 10 | 1AM to 2AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
October | 10 | 2AM to 3AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
October | 10 | 3AM to 4AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
October | 10 | 4AM to 5AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
October | 10 | 5AM to 6AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
October | 10 | 6AM to 7AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
October | 10 | 7AM to 8AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
October | 10 | 8AM to 9AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
October | 10 | 9AM to 10AM | 73.9 | 65.3 | 61 | 83.5 | 30.79 | 0.0712 | 0.54 | 14.22 | 1
October | 10 | 10AM to 11AM | 79 | 67.5 | 62.1 | 86.8 | 32.55 | 0.0705 | 0.56 | 14.36 | 1
October | 10 | 11AM to 12PM | 82 | 69.6 | 64 | 93.2 | 34.3 | 0.0701 | 0.6 | 14.46 | 1
October | 10 | 12PM to 1PM | 82.9 | 69.2 | 63 | 89.6 | 33.97 | 0.07 | 0.58 | 14.48 | 1
October | 10 | 1PM to 2PM | 84.9 | 69.8 | 63 | 89.6 | 34.45 | 0.0697 | 0.58 | 14.53 | 1
October | 10 | 2PM to 3PM | 84 | 69 | 62.1 | 86.8 | 33.78 | 0.0698 | 0.56 | 14.5 | 1
October | 10 | 3PM to 4PM | 86 | 69 | 61 | 83.5 | 33.75 | 0.0696 | 0.54 | 14.54 | 1
October | 10 | 4PM to 5PM | 84 | 68.4 | 61 | 83.5 | 33.26 | 0.0699 | 0.54 | 14.48 | 1
October | 10 | 5PM to 6PM | 79 | 68.7 | 64 | 93.2 | 33.55 | 0.0705 | 0.6 | 14.38 | 1
October | 10 | 6PM to 7PM | 73.9 | 67.2 | 64 | 93.2 | 32.31 | 0.0711 | 0.6 | 14.25 | 1
October | 10 | 7PM to 8PM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
October | 10 | 8PM to 9PM | 70 | 66 | 64 | 93.2 | 31.33 | 0.0717 | 0.6 | 14.14 | 1
October | 10 | 9PM to 10PM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
October | 10 | 10PM to 11PM | 69.1 | 65.7 | 64 | 93.2 | 31.11 | 0.0718 | 0.6 | 14.12 | 1
October | 10 | 11PM to 12AM | 68 | 64.6 | 63 | 89.6 | 30.3 | 0.0719 | 0.58 | 14.08 | 1
October | 11 | 12AM to 1AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
October | 11 | 1AM to 2AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
October | 11 | 2AM to 3AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
October | 11 | 3AM to 4AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
October | 11 | 4AM to 5AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
October | 11 | 5AM to 6AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
October | 11 | 6AM to 7AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
October | 11 | 7AM to 8AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
October | 11 | 8AM to 9AM | 69.1 | 63.7 | 61 | 83.5 | 29.6 | 0.0718 | 0.54 | 14.09 | 1
October | 11 | 9AM to 10AM | 73 | 65.7 | 62.1 | 86.8 | 31.09 | 0.0713 | 0.56 | 14.2 | 1
October | 11 | 10AM to 11AM | 78.1 | 68.4 | 64 | 93.2 | 33.33 | 0.0706 | 0.6 | 14.36 | 1
October | 11 | 11AM to 12PM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
October | 11 | 12PM to 1PM | 81 | 69.8 | 64.9 | 96.2 | 34.51 | 0.0702 | 0.62 | 14.44 | 1
October | 11 | 1PM to 2PM | 82 | 70.1 | 64.9 | 96.2 | 34.78 | 0.07 | 0.62 | 14.47 | 1
October | 11 | 2PM to 3PM | 81 | 68.1 | 62.1 | 86.8 | 33.03 | 0.0702 | 0.56 | 14.41 | 1
October | 11 | 3PM to 4PM | 79 | 62.7 | 53.1 | 62.4 | 28.73 | 0.0706 | 0.41 | 14.28 | 1
October | 11 | 4PM to 5PM | 75.9 | 56.8 | 42.1 | 41.1 | 24.65 | 0.0712 | 0.27 | 14.13 | 1
October | 11 | 5PM to 6PM | 72 | 56.1 | 44.1 | 44.4 | 24.2 | 0.0717 | 0.29 | 14.04 | 1
October | 11 | 6PM to 7PM | 66.9 | 52.8 | 41 | 39.4 | 22.2 | 0.0724 | 0.26 | 13.89 | 1
October | 11 | 7PM to 8PM | 64.9 | 50.8 | 37.9 | 34.9 | 21.03 | 0.0727 | 0.23 | 13.82 | 1
October | 11 | 8PM to 9PM | 61 | 49.1 | 37.9 | 34.9 | 20.07 | 0.0733 | 0.23 | 13.72 | 1
October | 11 | 9PM to 10PM | 57.9 | 48.2 | 39 | 36.4 | 19.56 | 0.0737 | 0.24 | 13.64 | 1
October | 11 | 10PM to 11PM | 57.9 | 48.2 | 39 | 36.4 | 19.56 | 0.0737 | 0.24 | 13.64 | 1
October | 11 | 11PM to 12AM | 55.9 | 46.5 | 37 | 33.7 | 18.66 | 0.074 | 0.22 | 13.58 | 1
October | 12 | 12AM to 1AM | 54 | 45.6 | 37 | 33.7 | 18.18 | 0.0743 | 0.22 | 13.53 | 1
October | 12 | 1AM to 2AM | 53.1 | 44.7 | 36 | 32.3 | 17.74 | 0.0744 | 0.21 | 13.5 | 1
October | 12 | 2AM to 3AM | 52 | 44.2 | 36 | 32.3 | 17.48 | 0.0746 | 0.21 | 13.47 | 1
October | 12 | 3AM to 4AM | 50 | 43.7 | 37 | 33.7 | 17.22 | 0.0748 | 0.22 | 13.43 | 1
October | 12 | 4AM to 5AM | 48.9 | 43.5 | 37.9 | 34.9 | 17.15 | 0.075 | 0.23 | 13.4 | 1
October | 12 | 5AM to 6AM | 46.9 | 42.6 | 37.9 | 34.9 | 16.67 | 0.0753 | 0.23 | 13.35 | 1
October | 12 | 6AM to 7AM | 45 | 42.1 | 39 | 36.4 | 16.42 | 0.0756 | 0.24 | 13.3 | 1
October | 12 | 7AM to 8AM | 50 | 45.4 | 41 | 39.4 | 18.1 | 0.0748 | 0.26 | 13.44 | 1
October | 12 | 8AM to 9AM | 55.9 | 48.6 | 42.1 | 41.1 | 19.8 | 0.0739 | 0.27 | 13.61 | 1
October | 12 | 9AM to 10AM | 59 | 49.9 | 42.1 | 41.1 | 20.55 | 0.0735 | 0.27 | 13.69 | 1
October | 12 | 10AM to 11AM | 64 | 52.1 | 42.1 | 41.1 | 21.77 | 0.0728 | 0.27 | 13.82 | 1
October | 12 | 11AM to 12PM | 64.9 | 52.5 | 42.1 | 41.1 | 21.99 | 0.0727 | 0.27 | 13.84 | 1
October | 12 | 12PM to 1PM | 66.9 | 53.3 | 42.1 | 41.1 | 22.47 | 0.0724 | 0.27 | 13.9 | 1
October | 12 | 1PM to 2PM | 69.1 | 53.3 | 39.9 | 37.8 | 22.47 | 0.0721 | 0.25 | 13.94 | 1
October | 12 | 2PM to 3PM | 69.1 | 53 | 39 | 36.4 | 22.27 | 0.0721 | 0.24 | 13.94 | 1
October | 12 | 3PM to 4PM | 69.1 | 52.2 | 37 | 33.7 | 21.84 | 0.0721 | 0.22 | 13.93 | 1
October | 12 | 4PM to 5PM | 68 | 52.9 | 39.9 | 37.8 | 22.21 | 0.0723 | 0.25 | 13.91 | 1
October | 12 | 5PM to 6PM | 64 | 50.9 | 39 | 36.4 | 21.05 | 0.0728 | 0.24 | 13.8 | 1
October | 12 | 6PM to 7PM | 57.9 | 48.5 | 39.9 | 37.8 | 19.77 | 0.0737 | 0.25 | 13.65 | 1
October | 12 | 7PM to 8PM | 55 | 48.2 | 42.1 | 41.1 | 19.58 | 0.0741 | 0.27 | 13.58 | 1
October | 12 | 8PM to 9PM | 54 | 48.1 | 43 | 42.5 | 19.55 | 0.0742 | 0.28 | 13.56 | 1
October | 12 | 9PM to 10PM | 52 | 47.2 | 43 | 42.5 | 19.07 | 0.0745 | 0.28 | 13.51 | 1
October | 12 | 10PM to 11PM | 50 | 45.4 | 41 | 39.4 | 18.1 | 0.0748 | 0.26 | 13.44 | 1
October | 12 | 11PM to 12AM | 48 | 43.6 | 39 | 36.4 | 17.16 | 0.0751 | 0.24 | 13.38 | 1
October | 13 | 12AM to 1AM | 48 | 43.6 | 39 | 36.4 | 17.16 | 0.0751 | 0.24 | 13.38 | 1
October | 13 | 1AM to 2AM | 46.9 | 42.6 | 37.9 | 34.9 | 16.67 | 0.0753 | 0.23 | 13.35 | 1
October | 13 | 2AM to 3AM | 46 | 41.7 | 37 | 33.7 | 16.26 | 0.0754 | 0.22 | 13.32 | 1
October | 13 | 3AM to 4AM | 44.1 | 40.7 | 37 | 33.7 | 15.78 | 0.0757 | 0.22 | 13.27 | 1
October | 13 | 4AM to 5AM | 43 | 40.2 | 37 | 33.7 | 15.52 | 0.0759 | 0.22 | 13.24 | 1
October | 13 | 5AM to 6AM | 42.1 | 39.7 | 37 | 33.7 | 15.3 | 0.076 | 0.22 | 13.22 | 1
October | 13 | 6AM to 7AM | 42.1 | 39.7 | 37 | 33.7 | 15.3 | 0.076 | 0.22 | 13.22 | 1
October | 13 | 7AM to 8AM | 51.1 | 45.9 | 41 | 39.4 | 18.36 | 0.0746 | 0.26 | 13.47 | 1
October | 13 | 8AM to 9AM | 54 | 46.8 | 39.9 | 37.8 | 18.81 | 0.0742 | 0.25 | 13.54 | 1
October | 13 | 9AM to 10AM | 55.9 | 48.1 | 41 | 39.4 | 19.54 | 0.0739 | 0.26 | 13.6 | 1
October | 13 | 10AM to 11AM | 59 | 49.9 | 42.1 | 41.1 | 20.55 | 0.0735 | 0.27 | 13.69 | 1
October | 13 | 11AM to 12PM | 62.1 | 50 | 39 | 36.4 | 20.57 | 0.0731 | 0.24 | 13.75 | 1
October | 13 | 12PM to 1PM | 64 | 50.9 | 39 | 36.4 | 21.05 | 0.0728 | 0.24 | 13.8 | 1
October | 13 | 1PM to 2PM | 69.1 | 53 | 39 | 36.4 | 22.27 | 0.0721 | 0.24 | 13.94 | 1
October | 13 | 2PM to 3PM | 71.1 | 53.8 | 39 | 36.4 | 22.75 | 0.0719 | 0.24 | 13.99 | 1
October | 13 | 3PM to 4PM | 72 | 54.9 | 41 | 39.4 | 23.42 | 0.0717 | 0.26 | 14.02 | 1
October | 13 | 4PM to 5PM | 70 | 53.7 | 39.9 | 37.8 | 22.69 | 0.072 | 0.25 | 13.97 | 1
October | 13 | 5PM to 6PM | 66 | 52.9 | 42.1 | 41.1 | 22.25 | 0.0725 | 0.27 | 13.87 | 1
October | 13 | 6PM to 7PM | 61 | 51.7 | 44.1 | 44.4 | 21.54 | 0.0732 | 0.29 | 13.75 | 1
October | 13 | 7PM to 8PM | 57 | 50 | 44.1 | 44.4 | 20.57 | 0.0738 | 0.29 | 13.64 | 1
October | 13 | 8PM to 9PM | 55.9 | 49.5 | 44.1 | 44.4 | 20.31 | 0.0739 | 0.29 | 13.62 | 1
October | 13 | 9PM to 10PM | 54 | 47.7 | 42.1 | 41.1 | 19.32 | 0.0742 | 0.27 | 13.55 | 1
October | 13 | 10PM to 11PM | 55 | 47.7 | 41 | 39.4 | 19.32 | 0.0741 | 0.26 | 13.58 | 1
October | 13 | 11PM to 12AM | 53.1 | 46 | 39 | 36.4 | 18.39 | 0.0744 | 0.24 | 13.52 | 1
October | 14 | 12AM to 1AM | 51.1 | 46.4 | 42.1 | 41.1 | 18.62 | 0.0746 | 0.27 | 13.48 | 1
October | 14 | 1AM to 2AM | 51.1 | 46.8 | 43 | 42.5 | 18.85 | 0.0746 | 0.28 | 13.48 | 1
October | 14 | 2AM to 3AM | 50 | 46.3 | 43 | 42.5 | 18.59 | 0.0748 | 0.28 | 13.45 | 1
October | 14 | 3AM to 4AM | 46 | 43 | 39.9 | 37.8 | 16.89 | 0.0754 | 0.25 | 13.33 | 1
October | 14 | 4AM to 5AM | 46.9 | 43.4 | 39.9 | 37.8 | 17.11 | 0.0753 | 0.25 | 13.36 | 1
October | 14 | 5AM to 6AM | 46.9 | 44.5 | 42.1 | 41.1 | 17.62 | 0.0752 | 0.27 | 13.37 | 1
October | 14 | 6AM to 7AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
October | 14 | 7AM to 8AM | 53.1 | 49.2 | 46 | 47.9 | 20.16 | 0.0743 | 0.31 | 13.55 | 1
October | 14 | 8AM to 9AM | 57 | 50.9 | 46 | 47.9 | 21.12 | 0.0737 | 0.31 | 13.66 | 1
October | 14 | 9AM to 10AM | 62.1 | 52.5 | 45 | 45.9 | 22.04 | 0.073 | 0.3 | 13.78 | 1
October | 14 | 10AM to 11AM | 66.9 | 55 | 46 | 47.9 | 23.52 | 0.0723 | 0.31 | 13.92 | 1
October | 14 | 11AM to 12PM | 68 | 55.8 | 46.9 | 49.6 | 24.05 | 0.0722 | 0.32 | 13.95 | 1
October | 14 | 12PM to 1PM | 70 | 55.7 | 45 | 45.9 | 23.96 | 0.0719 | 0.3 | 13.99 | 1
October | 14 | 1PM to 2PM | 72 | 56.5 | 45 | 45.9 | 24.45 | 0.0717 | 0.3 | 14.04 | 1
October | 14 | 2PM to 3PM | 72 | 56.5 | 45 | 45.9 | 24.45 | 0.0717 | 0.3 | 14.04 | 1
October | 14 | 3PM to 4PM | 72 | 56.9 | 46 | 47.9 | 24.75 | 0.0717 | 0.31 | 14.05 | 1
October | 14 | 4PM to 5PM | 72 | 56.5 | 45 | 45.9 | 24.45 | 0.0717 | 0.3 | 14.04 | 1
October | 14 | 5PM to 6PM | 69.1 | 55.3 | 45 | 45.9 | 23.75 | 0.0721 | 0.3 | 13.97 | 1
October | 14 | 6PM to 7PM | 66.9 | 55 | 46 | 47.9 | 23.52 | 0.0723 | 0.31 | 13.92 | 1
October | 14 | 7PM to 8PM | 64 | 54.8 | 48 | 51.6 | 23.41 | 0.0727 | 0.34 | 13.85 | 1
October | 14 | 8PM to 9PM | 61 | 53 | 46.9 | 49.6 | 22.34 | 0.0732 | 0.32 | 13.76 | 1
October | 14 | 9PM to 10PM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
October | 14 | 10PM to 11PM | 59 | 51.8 | 46 | 47.9 | 21.6 | 0.0735 | 0.31 | 13.71 | 1
October | 14 | 11PM to 12AM | 55.9 | 50.5 | 46 | 47.9 | 20.86 | 0.0739 | 0.31 | 13.63 | 1
October | 15 | 12AM to 1AM | 55 | 50.1 | 46 | 47.9 | 20.64 | 0.074 | 0.31 | 13.6 | 1
October | 15 | 1AM to 2AM | 54 | 49.6 | 46 | 47.9 | 20.37 | 0.0742 | 0.31 | 13.57 | 1
October | 15 | 2AM to 3AM | 54 | 48.6 | 44.1 | 44.4 | 19.83 | 0.0742 | 0.29 | 13.56 | 1
October | 15 | 3AM to 4AM | 54 | 48.6 | 44.1 | 44.4 | 19.83 | 0.0742 | 0.29 | 13.56 | 1
October | 15 | 4AM to 5AM | 51.1 | 47.3 | 44.1 | 44.4 | 19.13 | 0.0746 | 0.29 | 13.49 | 1
October | 15 | 5AM to 6AM | 52 | 47.8 | 44.1 | 44.4 | 19.35 | 0.0745 | 0.29 | 13.51 | 1
October | 15 | 6AM to 7AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
October | 15 | 7AM to 8AM | 54 | 50.1 | 46.9 | 49.6 | 20.63 | 0.0742 | 0.32 | 13.58 | 1
October | 15 | 8AM to 9AM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
October | 15 | 9AM to 10AM | 63 | 57.5 | 54 | 64.5 | 25.15 | 0.0728 | 0.42 | 13.86 | 1
October | 15 | 10AM to 11AM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
October | 15 | 11AM to 12PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
October | 15 | 12PM to 1PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
October | 15 | 1PM to 2PM | 75 | 63.4 | 57 | 72.3 | 29.3 | 0.0711 | 0.47 | 14.21 | 1
October | 15 | 2PM to 3PM | 73.9 | 62.5 | 55.9 | 69.4 | 28.6 | 0.0713 | 0.45 | 14.17 | 1
October | 15 | 3PM to 4PM | 75.9 | 63.1 | 55.9 | 69.4 | 29.08 | 0.071 | 0.45 | 14.22 | 1
October | 15 | 4PM to 5PM | 75 | 62.8 | 55.9 | 69.4 | 28.86 | 0.0711 | 0.45 | 14.2 | 1
October | 15 | 5PM to 6PM | 72 | 61.8 | 55.9 | 69.4 | 28.12 | 0.0715 | 0.45 | 14.12 | 1
October | 15 | 6PM to 7PM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
October | 15 | 7PM to 8PM | 68 | 61 | 57 | 72.3 | 27.59 | 0.0721 | 0.47 | 14.02 | 1
October | 15 | 8PM to 9PM | 66.9 | 61.2 | 57.9 | 74.7 | 27.7 | 0.0722 | 0.48 | 14 | 1
October | 15 | 9PM to 10PM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
October | 15 | 10PM to 11PM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
October | 15 | 11PM to 12AM | 60.1 | 58.2 | 57 | 72.3 | 25.65 | 0.0731 | 0.47 | 13.81 | 1
October | 16 | 12AM to 1AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
October | 16 | 1AM to 2AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
October | 16 | 2AM to 3AM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
October | 16 | 3AM to 4AM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
October | 16 | 4AM to 5AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
October | 16 | 5AM to 6AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
October | 16 | 6AM to 7AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
October | 16 | 7AM to 8AM | 57.9 | 57.9 | 57.9 | 74.7 | 25.5 | 0.0734 | 0.48 | 13.76 | 1
October | 16 | 8AM to 9AM | 62.1 | 60.8 | 60.1 | 80.8 | 27.46 | 0.0728 | 0.52 | 13.89 | 1
October | 16 | 9AM to 10AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
October | 16 | 10AM to 11AM | 72 | 65.9 | 63 | 89.6 | 31.27 | 0.0714 | 0.58 | 14.18 | 1
October | 16 | 11AM to 12PM | 75.9 | 66.6 | 62.1 | 86.8 | 31.8 | 0.0709 | 0.56 | 14.28 | 1
October | 16 | 12PM to 1PM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
October | 16 | 1PM to 2PM | 77 | 66.3 | 61 | 83.5 | 31.54 | 0.0708 | 0.54 | 14.3 | 1
October | 16 | 2PM to 3PM | 77 | 66.3 | 61 | 83.5 | 31.54 | 0.0708 | 0.54 | 14.3 | 1
October | 16 | 3PM to 4PM | 77 | 66.3 | 61 | 83.5 | 31.54 | 0.0708 | 0.54 | 14.3 | 1
October | 16 | 4PM to 5PM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
October | 16 | 5PM to 6PM | 73.9 | 65.3 | 61 | 83.5 | 30.79 | 0.0712 | 0.54 | 14.22 | 1
October | 16 | 6PM to 7PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
October | 16 | 7PM to 8PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
October | 16 | 8PM to 9PM | 70 | 64 | 61 | 83.5 | 29.82 | 0.0717 | 0.54 | 14.11 | 1
October | 16 | 9PM to 10PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
October | 16 | 10PM to 11PM | 68 | 62.8 | 60.1 | 80.8 | 28.92 | 0.072 | 0.52 | 14.05 | 1
October | 16 | 11PM to 12AM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
October | 17 | 12AM to 1AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
October | 17 | 1AM to 2AM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
October | 17 | 2AM to 3AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
October | 17 | 3AM to 4AM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
October | 17 | 4AM to 5AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
October | 17 | 5AM to 6AM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
October | 17 | 6AM to 7AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
October | 17 | 7AM to 8AM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
October | 17 | 8AM to 9AM | 66 | 65.3 | 64.9 | 96.2 | 30.83 | 0.0722 | 0.62 | 14.05 | 1
October | 17 | 9AM to 10AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
October | 17 | 10AM to 11AM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
October | 17 | 11AM to 12PM | 75.9 | 70.3 | 68 | 107.2 | 35 | 0.0708 | 0.69 | 14.35 | 1
October | 17 | 12PM to 1PM | 78.1 | 69.7 | 66 | 100 | 34.39 | 0.0705 | 0.64 | 14.38 | 1
October | 17 | 1PM to 2PM | 77 | 68.7 | 64.9 | 96.2 | 33.54 | 0.0707 | 0.62 | 14.34 | 1
October | 17 | 2PM to 3PM | 79 | 69.9 | 66 | 100 | 34.61 | 0.0704 | 0.64 | 14.4 | 1
October | 17 | 3PM to 4PM | 79 | 69.3 | 64.9 | 96.2 | 34.02 | 0.0704 | 0.62 | 14.39 | 1
October | 17 | 4PM to 5PM | 78.1 | 69 | 64.9 | 96.2 | 33.8 | 0.0706 | 0.62 | 14.37 | 1
October | 17 | 5PM to 6PM | 75.9 | 69 | 66 | 100 | 33.86 | 0.0708 | 0.64 | 14.32 | 1
October | 17 | 6PM to 7PM | 75 | 68.8 | 66 | 100 | 33.64 | 0.0709 | 0.64 | 14.3 | 1
October | 17 | 7PM to 8PM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
October | 17 | 8PM to 9PM | 73.9 | 69 | 66.9 | 103.2 | 33.88 | 0.0711 | 0.67 | 14.28 | 1
October | 17 | 9PM to 10PM | 73 | 68.8 | 66.9 | 103.2 | 33.66 | 0.0712 | 0.67 | 14.26 | 1
October | 17 | 10PM to 11PM | 72 | 67.9 | 66 | 100 | 32.89 | 0.0713 | 0.64 | 14.22 | 1
October | 17 | 11PM to 12AM | 70 | 67.3 | 66 | 100 | 32.4 | 0.0716 | 0.64 | 14.16 | 1
October | 18 | 12AM to 1AM | 70 | 67.9 | 66.9 | 103.2 | 32.9 | 0.0716 | 0.67 | 14.17 | 1
October | 18 | 1AM to 2AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
October | 18 | 2AM to 3AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
October | 18 | 3AM to 4AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
October | 18 | 4AM to 5AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
October | 18 | 5AM to 6AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
October | 18 | 6AM to 7AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
October | 18 | 7AM to 8AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
October | 18 | 8AM to 9AM | 70 | 68.6 | 68 | 107.2 | 33.53 | 0.0716 | 0.69 | 14.19 | 1
October | 18 | 9AM to 10AM | 71.1 | 69.7 | 69.1 | 111.4 | 34.45 | 0.0714 | 0.72 | 14.23 | 1
October | 18 | 10AM to 11AM | 75 | 71.4 | 70 | 115 | 35.98 | 0.0709 | 0.74 | 14.35 | 1
October | 18 | 11AM to 12PM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
October | 18 | 12PM to 1PM | 75 | 72.2 | 71.1 | 119.4 | 36.67 | 0.0708 | 0.77 | 14.36 | 1
October | 18 | 1PM to 2PM | 77 | 72.7 | 71.1 | 119.4 | 37.16 | 0.0706 | 0.77 | 14.41 | 1
October | 18 | 2PM to 3PM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
October | 18 | 3PM to 4PM | 78.1 | 73.6 | 72 | 123.2 | 38.03 | 0.0704 | 0.79 | 14.45 | 1
October | 18 | 4PM to 5PM | 77 | 73.3 | 72 | 123.2 | 37.76 | 0.0705 | 0.79 | 14.43 | 1
October | 18 | 5PM to 6PM | 75.9 | 73 | 72 | 123.2 | 37.49 | 0.0707 | 0.79 | 14.4 | 1
October | 18 | 6PM to 7PM | 75 | 72.8 | 72 | 123.2 | 37.27 | 0.0708 | 0.79 | 14.37 | 1
October | 18 | 7PM to 8PM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
October | 18 | 8PM to 9PM | 73.9 | 72.5 | 72 | 123.2 | 37 | 0.0709 | 0.79 | 14.34 | 1
October | 18 | 9PM to 10PM | 73 | 71.6 | 71.1 | 119.4 | 36.18 | 0.0711 | 0.77 | 14.31 | 1
October | 18 | 10PM to 11PM | 73 | 72.3 | 72 | 123.2 | 36.78 | 0.0711 | 0.79 | 14.32 | 1
October | 18 | 11PM to 12AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
October | 19 | 12AM to 1AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
October | 19 | 1AM to 2AM | 72 | 72 | 72 | 123.2 | 36.51 | 0.0712 | 0.79 | 14.29 | 1
October | 19 | 2AM to 3AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
October | 19 | 3AM to 4AM | 71.1 | 71.1 | 71.1 | 119.4 | 35.69 | 0.0714 | 0.77 | 14.25 | 1
October | 19 | 4AM to 5AM | 70 | 70 | 70 | 115 | 34.74 | 0.0715 | 0.74 | 14.21 | 1
October | 19 | 5AM to 6AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
October | 19 | 6AM to 7AM | 66.9 | 66.3 | 66 | 100 | 31.64 | 0.072 | 0.64 | 14.08 | 1
October | 19 | 7AM to 8AM | 66.9 | 66.9 | 66.9 | 103.2 | 32.15 | 0.072 | 0.67 | 14.09 | 1
October | 19 | 8AM to 9AM | 68 | 68 | 68 | 107.2 | 33.04 | 0.0718 | 0.69 | 14.13 | 1
October | 19 | 9AM to 10AM | 69.1 | 68.3 | 68 | 107.2 | 33.31 | 0.0717 | 0.69 | 14.16 | 1
October | 19 | 10AM to 11AM | 72 | 68.5 | 66.9 | 103.2 | 33.39 | 0.0713 | 0.67 | 14.23 | 1
October | 19 | 11AM to 12PM | 72 | 67.1 | 64.9 | 96.2 | 32.3 | 0.0714 | 0.62 | 14.2 | 1
October | 19 | 12PM to 1PM | 72 | 66.6 | 64 | 93.2 | 31.82 | 0.0714 | 0.6 | 14.19 | 1
October | 19 | 1PM to 2PM | 75 | 67.5 | 64 | 93.2 | 32.57 | 0.071 | 0.6 | 14.28 | 1
October | 19 | 2PM to 3PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
October | 19 | 3PM to 4PM | 75.9 | 65.4 | 60.1 | 80.8 | 30.86 | 0.0709 | 0.52 | 14.26 | 1
October | 19 | 4PM to 5PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
October | 19 | 5PM to 6PM | 70 | 62.8 | 59 | 77.7 | 28.92 | 0.0717 | 0.5 | 14.09 | 1
October | 19 | 6PM to 7PM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
October | 19 | 7PM to 8PM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
October | 19 | 8PM to 9PM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
October | 19 | 9PM to 10PM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
October | 19 | 10PM to 11PM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
October | 19 | 11PM to 12AM | 59 | 55.4 | 53.1 | 62.4 | 23.86 | 0.0734 | 0.41 | 13.75 | 1
October | 20 | 12AM to 1AM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
October | 20 | 1AM to 2AM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
October | 20 | 2AM to 3AM | 54 | 51.1 | 48.9 | 53.4 | 21.23 | 0.0741 | 0.35 | 13.59 | 1
October | 20 | 3AM to 4AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
October | 20 | 4AM to 5AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
October | 20 | 5AM to 6AM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
October | 20 | 6AM to 7AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
October | 20 | 7AM to 8AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
October | 20 | 8AM to 9AM | 52 | 47.2 | 43 | 42.5 | 19.07 | 0.0745 | 0.28 | 13.51 | 1
October | 20 | 9AM to 10AM | 55.9 | 47.7 | 39.9 | 37.8 | 19.29 | 0.074 | 0.25 | 13.6 | 1
October | 20 | 10AM to 11AM | 60.1 | 49.9 | 41 | 39.4 | 20.54 | 0.0734 | 0.26 | 13.71 | 1
October | 20 | 11AM to 12PM | 63 | 50.7 | 39.9 | 37.8 | 20.99 | 0.073 | 0.25 | 13.78 | 1
October | 20 | 12PM to 1PM | 64.9 | 52 | 41 | 39.4 | 21.72 | 0.0727 | 0.26 | 13.84 | 1
October | 20 | 1PM to 2PM | 64 | 52.1 | 42.1 | 41.1 | 21.77 | 0.0728 | 0.27 | 13.82 | 1
October | 20 | 2PM to 3PM | 66.9 | 52.8 | 41 | 39.4 | 22.2 | 0.0724 | 0.26 | 13.89 | 1
October | 20 | 3PM to 4PM | 64.9 | 52 | 41 | 39.4 | 21.72 | 0.0727 | 0.26 | 13.84 | 1
October | 20 | 4PM to 5PM | 64 | 51.6 | 41 | 39.4 | 21.5 | 0.0728 | 0.26 | 13.81 | 1
October | 20 | 5PM to 6PM | 60.1 | 49.9 | 41 | 39.4 | 20.54 | 0.0734 | 0.26 | 13.71 | 1
October | 20 | 6PM to 7PM | 55.9 | 48.6 | 42.1 | 41.1 | 19.8 | 0.0739 | 0.27 | 13.61 | 1
October | 20 | 7PM to 8PM | 53.1 | 47.7 | 43 | 42.5 | 19.33 | 0.0743 | 0.28 | 13.53 | 1
October | 20 | 8PM to 9PM | 52 | 47.8 | 44.1 | 44.4 | 19.35 | 0.0745 | 0.29 | 13.51 | 1
October | 20 | 9PM to 10PM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
October | 20 | 10PM to 11PM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
October | 20 | 11PM to 12AM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
October | 21 | 12AM to 1AM | 50 | 46.9 | 44.1 | 44.4 | 18.87 | 0.0748 | 0.29 | 13.46 | 1
October | 21 | 1AM to 2AM | 51.1 | 46.8 | 43 | 42.5 | 18.85 | 0.0746 | 0.28 | 13.48 | 1
October | 21 | 2AM to 3AM | 48 | 45.4 | 43 | 42.5 | 18.11 | 0.0751 | 0.28 | 13.4 | 1
October | 21 | 3AM to 4AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
October | 21 | 4AM to 5AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
October | 21 | 5AM to 6AM | 46 | 44 | 42.1 | 41.1 | 17.4 | 0.0754 | 0.27 | 13.34 | 1
October | 21 | 6AM to 7AM | 48 | 45 | 42.1 | 41.1 | 17.88 | 0.0751 | 0.27 | 13.4 | 1
October | 21 | 7AM to 8AM | 52 | 46.8 | 42.1 | 41.1 | 18.84 | 0.0745 | 0.27 | 13.5 | 1
October | 21 | 8AM to 9AM | 57 | 50 | 44.1 | 44.4 | 20.57 | 0.0738 | 0.29 | 13.64 | 1
October | 21 | 9AM to 10AM | 61 | 52.6 | 46 | 47.9 | 22.08 | 0.0732 | 0.31 | 13.76 | 1
October | 21 | 10AM to 11AM | 66 | 55 | 46.9 | 49.6 | 23.57 | 0.0725 | 0.32 | 13.9 | 1
October | 21 | 11AM to 12PM | 68 | 55.4 | 46 | 47.9 | 23.79 | 0.0722 | 0.31 | 13.95 | 1
October | 21 | 12PM to 1PM | 68 | 54.9 | 45 | 45.9 | 23.48 | 0.0722 | 0.3 | 13.94 | 1
October | 21 | 1PM to 2PM | 70 | 55.7 | 45 | 45.9 | 23.96 | 0.0719 | 0.3 | 13.99 | 1
October | 21 | 2PM to 3PM | 72 | 56.1 | 44.1 | 44.4 | 24.2 | 0.0717 | 0.29 | 14.04 | 1
October | 21 | 3PM to 4PM | 72 | 56.1 | 44.1 | 44.4 | 24.2 | 0.0717 | 0.29 | 14.04 | 1
October | 21 | 4PM to 5PM | 70 | 55.7 | 45 | 45.9 | 23.96 | 0.0719 | 0.3 | 13.99 | 1
October | 21 | 5PM to 6PM | 66.9 | 54.1 | 44.1 | 44.4 | 22.98 | 0.0724 | 0.29 | 13.91 | 1
October | 21 | 6PM to 7PM | 66.9 | 54.5 | 45 | 45.9 | 23.22 | 0.0724 | 0.3 | 13.91 | 1
October | 21 | 7PM to 8PM | 59 | 53.2 | 48.9 | 53.4 | 22.46 | 0.0734 | 0.35 | 13.72 | 1
October | 21 | 8PM to 9PM | 61 | 53.5 | 48 | 51.6 | 22.66 | 0.0731 | 0.34 | 13.77 | 1
October | 21 | 9PM to 10PM | 57.9 | 52.3 | 48 | 51.6 | 21.92 | 0.0736 | 0.34 | 13.69 | 1
October | 21 | 10PM to 11PM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
October | 21 | 11PM to 12AM | 57 | 51.9 | 48 | 51.6 | 21.7 | 0.0737 | 0.34 | 13.67 | 1
October | 22 | 12AM to 1AM | 57 | 52.4 | 48.9 | 53.4 | 21.98 | 0.0737 | 0.35 | 13.67 | 1
October | 22 | 1AM to 2AM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
October | 22 | 2AM to 3AM | 57 | 53 | 50 | 55.6 | 22.32 | 0.0737 | 0.36 | 13.68 | 1
October | 22 | 3AM to 4AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
October | 22 | 4AM to 5AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
October | 22 | 5AM to 6AM | 55 | 52.1 | 50 | 55.6 | 21.84 | 0.074 | 0.36 | 13.63 | 1
October | 22 | 6AM to 7AM | 55 | 52.7 | 51.1 | 58 | 22.2 | 0.074 | 0.38 | 13.63 | 1
October | 22 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 58 | 22.42 | 0.0738 | 0.38 | 13.66 | 1
October | 22 | 8AM to 9AM | 59 | 55.4 | 53.1 | 62.4 | 23.86 | 0.0734 | 0.41 | 13.75 | 1
October | 22 | 9AM to 10AM | 62.1 | 55.5 | 51.1 | 58 | 23.91 | 0.073 | 0.38 | 13.82 | 1
October | 22 | 10AM to 11AM | 69.1 | 58.7 | 52 | 59.9 | 25.93 | 0.072 | 0.39 | 14.01 | 1
October | 22 | 11AM to 12PM | 72 | 59.3 | 51.1 | 58 | 26.32 | 0.0716 | 0.38 | 14.08 | 1
October | 22 | 12PM to 1PM | 73.9 | 59.5 | 50 | 55.6 | 26.45 | 0.0713 | 0.36 | 14.13 | 1
October | 22 | 1PM to 2PM | 73.9 | 58.9 | 48.9 | 53.4 | 26.1 | 0.0714 | 0.35 | 14.12 | 1
October | 22 | 2PM to 3PM | 73.9 | 58.9 | 48.9 | 53.4 | 26.1 | 0.0714 | 0.35 | 14.12 | 1
October | 22 | 3PM to 4PM | 73.9 | 58.5 | 48 | 51.6 | 25.82 | 0.0714 | 0.34 | 14.11 | 1
October | 22 | 4PM to 5PM | 72 | 57.8 | 48 | 51.6 | 25.34 | 0.0716 | 0.34 | 14.06 | 1
October | 22 | 5PM to 6PM | 69.1 | 57.1 | 48.9 | 53.4 | 24.91 | 0.072 | 0.35 | 13.99 | 1
October | 22 | 6PM to 7PM | 66 | 56.5 | 50 | 55.6 | 24.52 | 0.0724 | 0.36 | 13.92 | 1
October | 22 | 7PM to 8PM | 63 | 55.3 | 50 | 55.6 | 23.77 | 0.0728 | 0.36 | 13.84 | 1
October | 22 | 8PM to 9PM | 62.1 | 55.5 | 51.1 | 58 | 23.91 | 0.073 | 0.38 | 13.82 | 1
October | 22 | 9PM to 10PM | 61 | 54.5 | 50 | 55.6 | 23.29 | 0.0731 | 0.36 | 13.78 | 1
October | 22 | 10PM to 11PM | 57.9 | 53.9 | 51.1 | 58 | 22.9 | 0.0735 | 0.38 | 13.71 | 1
October | 22 | 11PM to 12AM | 57 | 53 | 50 | 55.6 | 22.32 | 0.0737 | 0.36 | 13.68 | 1
October | 23 | 12AM to 1AM | 55.9 | 52.5 | 50 | 55.6 | 22.06 | 0.0738 | 0.36 | 13.65 | 1
October | 23 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 58 | 22.42 | 0.0738 | 0.38 | 13.66 | 1
October | 23 | 2AM to 3AM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
October | 23 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 62.4 | 23.11 | 0.0738 | 0.41 | 13.67 | 1
October | 23 | 4AM to 5AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
October | 23 | 5AM to 6AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
October | 23 | 6AM to 7AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
October | 23 | 7AM to 8AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
October | 23 | 8AM to 9AM | 57.9 | 55 | 53.1 | 62.4 | 23.59 | 0.0735 | 0.41 | 13.72 | 1
October | 23 | 9AM to 10AM | 62.1 | 56.6 | 53.1 | 62.4 | 24.6 | 0.0729 | 0.41 | 13.83 | 1
October | 23 | 10AM to 11AM | 62.1 | 56.6 | 53.1 | 62.4 | 24.6 | 0.0729 | 0.41 | 13.83 | 1
October | 23 | 11AM to 12PM | 64 | 56.8 | 52 | 59.9 | 24.7 | 0.0727 | 0.39 | 13.88 | 1
October | 23 | 12PM to 1PM | 61 | 55.6 | 52 | 59.9 | 23.96 | 0.0731 | 0.39 | 13.8 | 1
October | 23 | 1PM to 2PM | 64 | 56.3 | 51.1 | 58 | 24.39 | 0.0727 | 0.38 | 13.87 | 1
October | 23 | 2PM to 3PM | 64 | 54.8 | 48 | 51.6 | 23.41 | 0.0727 | 0.34 | 13.85 | 1
October | 23 | 3PM to 4PM | 62.1 | 54 | 48 | 51.6 | 22.93 | 0.073 | 0.34 | 13.8 | 1
October | 23 | 4PM to 5PM | 60.1 | 54.2 | 50 | 55.6 | 23.07 | 0.0733 | 0.36 | 13.76 | 1
October | 23 | 5PM to 6PM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
October | 23 | 6PM to 7PM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
October | 23 | 7PM to 8PM | 55.9 | 53.6 | 52 | 59.9 | 22.73 | 0.0738 | 0.39 | 13.66 | 1
October | 23 | 8PM to 9PM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
October | 23 | 9PM to 10PM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
October | 23 | 10PM to 11PM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
October | 23 | 11PM to 12AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 24 | 12AM to 1AM | 54 | 53.4 | 53.1 | 62.4 | 22.63 | 0.0741 | 0.41 | 13.62 | 1
October | 24 | 1AM to 2AM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
October | 24 | 2AM to 3AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 24 | 3AM to 4AM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
October | 24 | 4AM to 5AM | 52 | 50.8 | 50 | 55.6 | 21.1 | 0.0744 | 0.36 | 13.55 | 1
October | 24 | 5AM to 6AM | 51.1 | 49.9 | 48.9 | 53.4 | 20.53 | 0.0746 | 0.35 | 13.52 | 1
October | 24 | 6AM to 7AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
October | 24 | 7AM to 8AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
October | 24 | 8AM to 9AM | 52 | 49.8 | 48 | 51.6 | 20.48 | 0.0744 | 0.34 | 13.53 | 1
October | 24 | 9AM to 10AM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
October | 24 | 10AM to 11AM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
October | 24 | 11AM to 12PM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
October | 24 | 12PM to 1PM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
October | 24 | 1PM to 2PM | 54 | 51.1 | 48.9 | 53.4 | 21.23 | 0.0741 | 0.35 | 13.59 | 1
October | 24 | 2PM to 3PM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
October | 24 | 3PM to 4PM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
October | 24 | 4PM to 5PM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
October | 24 | 5PM to 6PM | 51.1 | 51.1 | 51.1 | 58 | 21.24 | 0.0745 | 0.38 | 13.53 | 1
October | 24 | 6PM to 7PM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 24 | 7PM to 8PM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 24 | 8PM to 9PM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 24 | 9PM to 10PM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 24 | 10PM to 11PM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 24 | 11PM to 12AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 25 | 12AM to 1AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 25 | 1AM to 2AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 25 | 2AM to 3AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 25 | 3AM to 4AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 25 | 4AM to 5AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 25 | 5AM to 6AM | 48.9 | 48.9 | 48.9 | 53.4 | 20.01 | 0.0749 | 0.35 | 13.46 | 1
October | 25 | 6AM to 7AM | 46.9 | 46.9 | 46.9 | 49.6 | 18.93 | 0.0752 | 0.32 | 13.39 | 1
October | 25 | 7AM to 8AM | 45 | 44.5 | 44.1 | 44.4 | 17.65 | 0.0755 | 0.29 | 13.33 | 1
October | 25 | 8AM to 9AM | 46 | 45 | 44.1 | 44.4 | 17.91 | 0.0754 | 0.29 | 13.35 | 1
October | 25 | 9AM to 10AM | 46.9 | 43.9 | 41 | 39.4 | 17.36 | 0.0753 | 0.26 | 13.36 | 1
October | 25 | 10AM to 11AM | 48 | 43.1 | 37.9 | 34.9 | 16.93 | 0.0751 | 0.23 | 13.38 | 1
October | 25 | 11AM to 12PM | 51.1 | 44.6 | 37.9 | 34.9 | 17.67 | 0.0747 | 0.23 | 13.46 | 1
October | 25 | 12PM to 1PM | 53.1 | 44.7 | 36 | 32.3 | 17.74 | 0.0744 | 0.21 | 13.5 | 1
October | 25 | 1PM to 2PM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
October | 25 | 2PM to 3PM | 55 | 44.9 | 34 | 29.8 | 17.84 | 0.0741 | 0.2 | 13.55 | 1
October | 25 | 3PM to 4PM | 54 | 44.8 | 35.1 | 31.1 | 17.78 | 0.0743 | 0.2 | 13.52 | 1
October | 25 | 4PM to 5PM | 52 | 43.1 | 33.1 | 28.8 | 16.93 | 0.0746 | 0.19 | 13.46 | 1
October | 25 | 5PM to 6PM | 48.9 | 41.9 | 34 | 29.8 | 16.36 | 0.075 | 0.2 | 13.39 | 1
October | 25 | 6PM to 7PM | 46 | 40.5 | 34 | 29.8 | 15.66 | 0.0755 | 0.2 | 13.31 | 1
October | 25 | 7PM to 8PM | 45 | 40.4 | 35.1 | 31.1 | 15.6 | 0.0756 | 0.2 | 13.29 | 1
October | 25 | 8PM to 9PM | 43 | 39.3 | 35.1 | 31.1 | 15.12 | 0.0759 | 0.2 | 13.23 | 1
October | 25 | 9PM to 10PM | 42.1 | 39.2 | 36 | 32.3 | 15.08 | 0.076 | 0.21 | 13.21 | 1
October | 25 | 10PM to 11PM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
October | 25 | 11PM to 12AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
October | 26 | 12AM to 1AM | 39 | 37.6 | 36 | 32.3 | 14.34 | 0.0765 | 0.21 | 13.13 | 1
October | 26 | 1AM to 2AM | 39 | 37.2 | 35.1 | 31.1 | 14.17 | 0.0765 | 0.2 | 13.13 | 1
October | 26 | 2AM to 3AM | 39 | 37.2 | 35.1 | 31.1 | 14.17 | 0.0765 | 0.2 | 13.13 | 1
October | 26 | 3AM to 4AM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
October | 26 | 4AM to 5AM | 36 | 35.6 | 35.1 | 31.1 | 13.43 | 0.077 | 0.2 | 13.05 | 1
October | 26 | 5AM to 6AM | 36 | 35.6 | 35.1 | 31.1 | 13.43 | 0.077 | 0.2 | 13.05 | 1
October | 26 | 6AM to 7AM | 36 | 35.6 | 35.1 | 31.1 | 13.43 | 0.077 | 0.2 | 13.05 | 1
October | 26 | 7AM to 8AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
October | 26 | 8AM to 9AM | 46.9 | 42.2 | 37 | 33.7 | 16.48 | 0.0753 | 0.22 | 13.35 | 1
October | 26 | 9AM to 10AM | 54 | 46.8 | 39.9 | 37.8 | 18.81 | 0.0742 | 0.25 | 13.54 | 1
October | 26 | 10AM to 11AM | 57 | 48.1 | 39.9 | 37.8 | 19.55 | 0.0738 | 0.25 | 13.62 | 1
October | 26 | 11AM to 12PM | 61 | 49.5 | 39 | 36.4 | 20.3 | 0.0732 | 0.24 | 13.72 | 1
October | 26 | 12PM to 1PM | 62.1 | 50 | 39 | 36.4 | 20.57 | 0.0731 | 0.24 | 13.75 | 1
October | 26 | 1PM to 2PM | 64.9 | 50.8 | 37.9 | 34.9 | 21.03 | 0.0727 | 0.23 | 13.82 | 1
October | 26 | 2PM to 3PM | 66 | 51 | 37 | 33.7 | 21.1 | 0.0726 | 0.22 | 13.85 | 1
October | 26 | 3PM to 4PM | 64 | 50.4 | 37.9 | 34.9 | 20.81 | 0.0728 | 0.23 | 13.8 | 1
October | 26 | 4PM to 5PM | 64 | 50.4 | 37.9 | 34.9 | 20.81 | 0.0728 | 0.23 | 13.8 | 1
October | 26 | 5PM to 6PM | 57.9 | 49 | 41 | 39.4 | 20.02 | 0.0737 | 0.26 | 13.65 | 1
October | 26 | 6PM to 7PM | 55.9 | 48.6 | 42.1 | 41.1 | 19.8 | 0.0739 | 0.27 | 13.61 | 1
October | 26 | 7PM to 8PM | 54 | 47.7 | 42.1 | 41.1 | 19.32 | 0.0742 | 0.27 | 13.55 | 1
October | 26 | 8PM to 9PM | 52 | 47.2 | 43 | 42.5 | 19.07 | 0.0745 | 0.28 | 13.51 | 1
October | 26 | 9PM to 10PM | 48.9 | 45.8 | 43 | 42.5 | 18.33 | 0.0749 | 0.28 | 13.42 | 1
October | 26 | 10PM to 11PM | 51.1 | 47.3 | 44.1 | 44.4 | 19.13 | 0.0746 | 0.29 | 13.49 | 1
October | 26 | 11PM to 12AM | 51.1 | 48.3 | 46 | 47.9 | 19.67 | 0.0746 | 0.31 | 13.5 | 1
October | 27 | 12AM to 1AM | 53.1 | 47.7 | 43 | 42.5 | 19.33 | 0.0743 | 0.28 | 13.53 | 1
October | 27 | 1AM to 2AM | 52 | 47.8 | 44.1 | 44.4 | 19.35 | 0.0745 | 0.29 | 13.51 | 1
October | 27 | 2AM to 3AM | 52 | 47.8 | 44.1 | 44.4 | 19.35 | 0.0745 | 0.29 | 13.51 | 1
October | 27 | 3AM to 4AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
October | 27 | 4AM to 5AM | 48.9 | 47.4 | 46 | 47.9 | 19.15 | 0.0749 | 0.31 | 13.44 | 1
October | 27 | 5AM to 6AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
October | 27 | 6AM to 7AM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
October | 27 | 7AM to 8AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
October | 27 | 8AM to 9AM | 55 | 49.1 | 44.1 | 44.4 | 20.09 | 0.074 | 0.29 | 13.59 | 1
October | 27 | 9AM to 10AM | 57.9 | 49.9 | 43 | 42.5 | 20.51 | 0.0736 | 0.28 | 13.66 | 1
October | 27 | 10AM to 11AM | 60.1 | 51.7 | 45 | 45.9 | 21.56 | 0.0733 | 0.3 | 13.73 | 1
October | 27 | 11AM to 12PM | 62.1 | 53 | 46 | 47.9 | 22.34 | 0.073 | 0.31 | 13.79 | 1
October | 27 | 12PM to 1PM | 66.9 | 54.5 | 45 | 45.9 | 23.22 | 0.0724 | 0.3 | 13.91 | 1
October | 27 | 1PM to 2PM | 68 | 54.5 | 44.1 | 44.4 | 23.24 | 0.0722 | 0.29 | 13.93 | 1
October | 27 | 2PM to 3PM | 69.1 | 54.1 | 42.1 | 41.1 | 22.99 | 0.0721 | 0.27 | 13.95 | 1
October | 27 | 3PM to 4PM | 69.1 | 54.5 | 43 | 42.5 | 23.22 | 0.0721 | 0.28 | 13.96 | 1
October | 27 | 4PM to 5PM | 66.9 | 52.4 | 39.9 | 37.8 | 21.95 | 0.0724 | 0.25 | 13.88 | 1
October | 27 | 5PM to 6PM | 64.9 | 52 | 41 | 39.4 | 21.72 | 0.0727 | 0.26 | 13.84 | 1
October | 27 | 6PM to 7PM | 63 | 52 | 43 | 42.5 | 21.73 | 0.0729 | 0.28 | 13.8 | 1
October | 27 | 7PM to 8PM | 63 | 52.5 | 44.1 | 44.4 | 22.02 | 0.0729 | 0.29 | 13.8 | 1
October | 27 | 8PM to 9PM | 62.1 | 52.5 | 45 | 45.9 | 22.04 | 0.073 | 0.3 | 13.78 | 1
October | 27 | 9PM to 10PM | 62.1 | 53.5 | 46.9 | 49.6 | 22.6 | 0.073 | 0.32 | 13.79 | 1
October | 27 | 10PM to 11PM | 61 | 54 | 48.9 | 53.4 | 22.94 | 0.0731 | 0.35 | 13.78 | 1
October | 27 | 11PM to 12AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 28 | 12AM to 1AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 28 | 1AM to 2AM | 51.1 | 51.1 | 51.1 | 58 | 21.24 | 0.0745 | 0.38 | 13.53 | 1
October | 28 | 2AM to 3AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 28 | 3AM to 4AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 28 | 4AM to 5AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 28 | 5AM to 6AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 28 | 6AM to 7AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 28 | 7AM to 8AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 28 | 8AM to 9AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
October | 28 | 9AM to 10AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
October | 28 | 10AM to 11AM | 57.9 | 57.9 | 57.9 | 74.7 | 25.5 | 0.0734 | 0.48 | 13.76 | 1
October | 28 | 11AM to 12PM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
October | 28 | 12PM to 1PM | 60.1 | 60.1 | 60.1 | 80.8 | 26.98 | 0.0731 | 0.52 | 13.84 | 1
October | 28 | 1PM to 2PM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
October | 28 | 2PM to 3PM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
October | 28 | 3PM to 4PM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
October | 28 | 4PM to 5PM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
October | 28 | 5PM to 6PM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
October | 28 | 6PM to 7PM | 63 | 63 | 63 | 89.6 | 29.06 | 0.0726 | 0.58 | 13.94 | 1
October | 28 | 7PM to 8PM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
October | 28 | 8PM to 9PM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
October | 28 | 9PM to 10PM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
October | 28 | 10PM to 11PM | 60.1 | 60.1 | 60.1 | 80.8 | 26.98 | 0.0731 | 0.52 | 13.84 | 1
October | 28 | 11PM to 12AM | 60.1 | 60.1 | 60.1 | 80.8 | 26.98 | 0.0731 | 0.52 | 13.84 | 1
October | 29 | 12AM to 1AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
October | 29 | 1AM to 2AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
October | 29 | 2AM to 3AM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
October | 29 | 3AM to 4AM | 57.9 | 57.9 | 57.9 | 74.7 | 25.5 | 0.0734 | 0.48 | 13.76 | 1
October | 29 | 4AM to 5AM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
October | 29 | 5AM to 6AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
October | 29 | 6AM to 7AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
October | 29 | 7AM to 8AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
October | 29 | 8AM to 9AM | 54 | 53.4 | 53.1 | 62.4 | 22.63 | 0.0741 | 0.41 | 13.62 | 1
October | 29 | 9AM to 10AM | 55 | 53.9 | 53.1 | 62.4 | 22.89 | 0.0739 | 0.41 | 13.65 | 1
October | 29 | 10AM to 11AM | 57 | 54.7 | 53.1 | 62.4 | 23.37 | 0.0736 | 0.41 | 13.7 | 1
October | 29 | 11AM to 12PM | 57 | 54 | 52 | 59.9 | 22.99 | 0.0737 | 0.39 | 13.69 | 1
October | 29 | 12PM to 1PM | 59 | 54.8 | 52 | 59.9 | 23.47 | 0.0734 | 0.39 | 13.74 | 1
October | 29 | 1PM to 2PM | 57 | 53.5 | 51.1 | 58 | 22.68 | 0.0737 | 0.38 | 13.69 | 1
October | 29 | 2PM to 3PM | 55.9 | 53.1 | 51.1 | 58 | 22.42 | 0.0738 | 0.38 | 13.66 | 1
October | 29 | 3PM to 4PM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
October | 29 | 4PM to 5PM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
October | 29 | 5PM to 6PM | 50 | 49.4 | 48.9 | 53.4 | 20.27 | 0.0747 | 0.35 | 13.49 | 1
October | 29 | 6PM to 7PM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 29 | 7PM to 8PM | 48.9 | 48.9 | 48.9 | 53.4 | 20.01 | 0.0749 | 0.35 | 13.46 | 1
October | 29 | 8PM to 9PM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 29 | 9PM to 10PM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 29 | 10PM to 11PM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 29 | 11PM to 12AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 12AM to 1AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 1AM to 2AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 2AM to 3AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 3AM to 4AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 4AM to 5AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 5AM to 6AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 6AM to 7AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 7AM to 8AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 30 | 8AM to 9AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 30 | 9AM to 10AM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 30 | 10AM to 11AM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
October | 30 | 11AM to 12PM | 54 | 52.8 | 52 | 59.9 | 22.25 | 0.0741 | 0.39 | 13.61 | 1
October | 30 | 12PM to 1PM | 54 | 52.8 | 52 | 59.9 | 22.25 | 0.0741 | 0.39 | 13.61 | 1
October | 30 | 1PM to 2PM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
October | 30 | 2PM to 3PM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
October | 30 | 3PM to 4PM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 30 | 4PM to 5PM | 52 | 52 | 52 | 59.9 | 21.76 | 0.0744 | 0.39 | 13.56 | 1
October | 30 | 5PM to 6PM | 51.1 | 51.1 | 51.1 | 58 | 21.24 | 0.0745 | 0.38 | 13.53 | 1
October | 30 | 6PM to 7PM | 51.1 | 51.1 | 51.1 | 58 | 21.24 | 0.0745 | 0.38 | 13.53 | 1
October | 30 | 7PM to 8PM | 51.1 | 51.1 | 51.1 | 58 | 21.24 | 0.0745 | 0.38 | 13.53 | 1
October | 30 | 8PM to 9PM | 51.1 | 50.5 | 50 | 55.6 | 20.88 | 0.0745 | 0.36 | 13.52 | 1
October | 30 | 9PM to 10PM | 51.1 | 50.5 | 50 | 55.6 | 20.88 | 0.0745 | 0.36 | 13.52 | 1
October | 30 | 10PM to 11PM | 51.1 | 50.5 | 50 | 55.6 | 20.88 | 0.0745 | 0.36 | 13.52 | 1
October | 30 | 11PM to 12AM | 51.1 | 50.5 | 50 | 55.6 | 20.88 | 0.0745 | 0.36 | 13.52 | 1
October | 31 | 12AM to 1AM | 51.1 | 50.5 | 50 | 55.6 | 20.88 | 0.0745 | 0.36 | 13.52 | 1
October | 31 | 1AM to 2AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
October | 31 | 2AM to 3AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 31 | 3AM to 4AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
October | 31 | 4AM to 5AM | 46.9 | 46.9 | 46.9 | 49.6 | 18.93 | 0.0752 | 0.32 | 13.39 | 1
October | 31 | 5AM to 6AM | 46.9 | 46.9 | 46.9 | 49.6 | 18.93 | 0.0752 | 0.32 | 13.39 | 1
October | 31 | 6AM to 7AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
October | 31 | 7AM to 8AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
October | 31 | 8AM to 9AM | 46 | 45.5 | 45 | 45.9 | 18.15 | 0.0753 | 0.3 | 13.36 | 1
October | 31 | 9AM to 10AM | 51.1 | 48.3 | 46 | 47.9 | 19.67 | 0.0746 | 0.31 | 13.5 | 1
October | 31 | 10AM to 11AM | 55 | 50.1 | 46 | 47.9 | 20.64 | 0.074 | 0.31 | 13.6 | 1
October | 31 | 11AM to 12PM | 57.9 | 50.8 | 45 | 45.9 | 21.04 | 0.0736 | 0.3 | 13.67 | 1
October | 31 | 12PM to 1PM | 61 | 51.2 | 43 | 42.5 | 21.25 | 0.0732 | 0.28 | 13.74 | 1
October | 31 | 1PM to 2PM | 64 | 51.6 | 41 | 39.4 | 21.5 | 0.0728 | 0.26 | 13.81 | 1
October | 31 | 2PM to 3PM | 66 | 51.3 | 37.9 | 34.9 | 21.29 | 0.0726 | 0.23 | 13.85 | 1
October | 31 | 3PM to 4PM | 66 | 48.6 | 30 | 25.1 | 19.76 | 0.0726 | 0.16 | 13.82 | 1
October | 31 | 4PM to 5PM | 63 | 46.6 | 28 | 22.9 | 18.68 | 0.0731 | 0.15 | 13.73 | 1
October | 31 | 5PM to 6PM | 54 | 43.3 | 30.9 | 26.2 | 17.01 | 0.0743 | 0.17 | 13.51 | 1
October | 31 | 6PM to 7PM | 54 | 43.3 | 30.9 | 26.2 | 17.01 | 0.0743 | 0.17 | 13.51 | 1
October | 31 | 7PM to 8PM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
October | 31 | 8PM to 9PM | 48.9 | 41.2 | 32 | 27.5 | 16 | 0.075 | 0.18 | 13.38 | 1
October | 31 | 9PM to 10PM | 49.1 | 42.1 | 34.2 | 30 | 16.43 | 0.075 | 0.2 | 13.39 | 1
October | 31 | 10PM to 11PM | 49.3 | 43 | 36.3 | 32.7 | 16.9 | 0.075 | 0.21 | 13.4 | 1
October | 31 | 11PM to 12AM | 49.5 | 44 | 38.5 | 35.7 | 17.39 | 0.0749 | 0.23 | 13.42 | 1
November | 1 | 12AM to 1AM | 49.5 | 44.9 | 40.5 | 38.6 | 17.84 | 0.0749 | 0.25 | 13.43 | 1
November | 1 | 1AM to 2AM | 49.6 | 46 | 42.6 | 42 | 18.41 | 0.0748 | 0.27 | 13.44 | 1
November | 1 | 2AM to 3AM | 49.8 | 47.1 | 44.8 | 45.6 | 19.02 | 0.0748 | 0.3 | 13.46 | 1
November | 1 | 3AM to 4AM | 50 | 48.3 | 46.9 | 49.6 | 19.67 | 0.0747 | 0.32 | 13.47 | 1
November | 1 | 4AM to 5AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
November | 1 | 5AM to 6AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
November | 1 | 6AM to 7AM | 48.9 | 48.4 | 48 | 51.6 | 19.73 | 0.0749 | 0.34 | 13.45 | 1
November | 1 | 7AM to 8AM | 48.9 | 48.4 | 48 | 51.6 | 19.73 | 0.0749 | 0.34 | 13.45 | 1
November | 1 | 8AM to 9AM | 52 | 49.8 | 48 | 51.6 | 20.48 | 0.0744 | 0.34 | 13.53 | 1
November | 1 | 9AM to 10AM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
November | 1 | 10AM to 11AM | 60.1 | 53.6 | 48.9 | 53.4 | 22.72 | 0.0733 | 0.35 | 13.75 | 1
November | 1 | 11AM to 12PM | 64 | 56.3 | 51.1 | 58 | 24.39 | 0.0727 | 0.38 | 13.87 | 1
November | 1 | 12PM to 1PM | 68 | 58.3 | 52 | 59.9 | 25.67 | 0.0721 | 0.39 | 13.98 | 1
November | 1 | 1PM to 2PM | 69.1 | 58.7 | 52 | 59.9 | 25.93 | 0.072 | 0.39 | 14.01 | 1
November | 1 | 2PM to 3PM | 69.1 | 59.2 | 53.1 | 62.4 | 26.32 | 0.072 | 0.41 | 14.02 | 1
November | 1 | 3PM to 4PM | 70 | 60 | 54 | 64.5 | 26.87 | 0.0718 | 0.42 | 14.05 | 1
November | 1 | 4PM to 5PM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
November | 1 | 5PM to 6PM | 66 | 59.7 | 55.9 | 69.4 | 26.66 | 0.0723 | 0.45 | 13.96 | 1
November | 1 | 6PM to 7PM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
November | 1 | 7PM to 8PM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
November | 1 | 8PM to 9PM | 63 | 58.6 | 55.9 | 69.4 | 25.92 | 0.0728 | 0.45 | 13.88 | 1
November | 1 | 9PM to 10PM | 61 | 57.9 | 55.9 | 69.4 | 25.43 | 0.073 | 0.45 | 13.83 | 1
November | 1 | 10PM to 11PM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
November | 1 | 11PM to 12AM | 60.1 | 57.5 | 55.9 | 69.4 | 25.21 | 0.0732 | 0.45 | 13.8 | 1
November | 2 | 12AM to 1AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
November | 2 | 1AM to 2AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
November | 2 | 2AM to 3AM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
November | 2 | 3AM to 4AM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
November | 2 | 4AM to 5AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
November | 2 | 5AM to 6AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
November | 2 | 6AM to 7AM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
November | 2 | 7AM to 8AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
November | 2 | 8AM to 9AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
November | 2 | 9AM to 10AM | 66 | 60.8 | 57.9 | 74.7 | 27.48 | 0.0723 | 0.48 | 13.98 | 1
November | 2 | 10AM to 11AM | 68 | 61.5 | 57.9 | 74.7 | 27.96 | 0.072 | 0.48 | 14.03 | 1
November | 2 | 11AM to 12PM | 70 | 62.2 | 57.9 | 74.7 | 28.45 | 0.0718 | 0.48 | 14.08 | 1
November | 2 | 12PM to 1PM | 73.9 | 63.5 | 57.9 | 74.7 | 29.42 | 0.0712 | 0.48 | 14.19 | 1
November | 2 | 1PM to 2PM | 73.9 | 62.5 | 55.9 | 69.4 | 28.6 | 0.0713 | 0.45 | 14.17 | 1
November | 2 | 2PM to 3PM | 73 | 61.7 | 55 | 67.2 | 28.03 | 0.0714 | 0.44 | 14.14 | 1
November | 2 | 3PM to 4PM | 72 | 60.7 | 54 | 64.5 | 27.35 | 0.0716 | 0.42 | 14.1 | 1
November | 2 | 4PM to 5PM | 70 | 60 | 54 | 64.5 | 26.87 | 0.0718 | 0.42 | 14.05 | 1
November | 2 | 5PM to 6PM | 66.9 | 59.5 | 55 | 67.2 | 26.53 | 0.0722 | 0.44 | 13.98 | 1
November | 2 | 6PM to 7PM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
November | 2 | 7PM to 8PM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
November | 2 | 8PM to 9PM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
November | 2 | 9PM to 10PM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
November | 2 | 10PM to 11PM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
November | 2 | 11PM to 12AM | 59 | 56.6 | 55 | 67.2 | 24.6 | 0.0733 | 0.44 | 13.77 | 1
November | 3 | 12AM to 1AM | 59 | 55.9 | 54 | 64.5 | 24.19 | 0.0733 | 0.42 | 13.76 | 1
November | 3 | 1AM to 2AM | 59 | 56.6 | 55 | 67.2 | 24.6 | 0.0733 | 0.44 | 13.77 | 1
November | 3 | 2AM to 3AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
November | 3 | 3AM to 4AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
November | 3 | 4AM to 5AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
November | 3 | 5AM to 6AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
November | 3 | 6AM to 7AM | 55.9 | 54.7 | 54 | 64.5 | 23.44 | 0.0738 | 0.42 | 13.68 | 1
November | 3 | 7AM to 8AM | 57 | 55.2 | 54 | 64.5 | 23.7 | 0.0736 | 0.42 | 13.71 | 1
November | 3 | 8AM to 9AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
November | 3 | 9AM to 10AM | 68 | 61 | 57 | 72.3 | 27.59 | 0.0721 | 0.47 | 14.02 | 1
November | 3 | 10AM to 11AM | 71.1 | 62.1 | 57 | 72.3 | 28.34 | 0.0716 | 0.47 | 14.1 | 1
November | 3 | 11AM to 12PM | 71.1 | 62.6 | 57.9 | 74.7 | 28.71 | 0.0716 | 0.48 | 14.11 | 1
November | 3 | 12PM to 1PM | 70 | 62.2 | 57.9 | 74.7 | 28.45 | 0.0718 | 0.48 | 14.08 | 1
November | 3 | 1PM to 2PM | 71.1 | 63.2 | 59 | 77.7 | 29.18 | 0.0716 | 0.5 | 14.12 | 1
November | 3 | 2PM to 3PM | 71.1 | 63.2 | 59 | 77.7 | 29.18 | 0.0716 | 0.5 | 14.12 | 1
November | 3 | 3PM to 4PM | 70 | 62.2 | 57.9 | 74.7 | 28.45 | 0.0718 | 0.48 | 14.08 | 1
November | 3 | 4PM to 5PM | 70 | 62.8 | 59 | 77.7 | 28.92 | 0.0717 | 0.5 | 14.09 | 1
November | 3 | 5PM to 6PM | 68 | 62.2 | 59 | 77.7 | 28.43 | 0.072 | 0.5 | 14.04 | 1
November | 3 | 6PM to 7PM | 66.9 | 61.8 | 59 | 77.7 | 28.17 | 0.0722 | 0.5 | 14.01 | 1
November | 3 | 7PM to 8PM | 66 | 61.5 | 59 | 77.7 | 27.95 | 0.0723 | 0.5 | 13.99 | 1
November | 3 | 8PM to 9PM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
November | 3 | 9PM to 10PM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
November | 3 | 10PM to 11PM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
November | 3 | 11PM to 12AM | 64.9 | 61.1 | 59 | 77.7 | 27.68 | 0.0724 | 0.5 | 13.96 | 1
November | 4 | 12AM to 1AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
November | 4 | 1AM to 2AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
November | 4 | 2AM to 3AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
November | 4 | 3AM to 4AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
November | 4 | 4AM to 5AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
November | 4 | 5AM to 6AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
November | 4 | 6AM to 7AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
November | 4 | 7AM to 8AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
November | 4 | 8AM to 9AM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
November | 4 | 9AM to 10AM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
November | 4 | 10AM to 11AM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
November | 4 | 11AM to 12PM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
November | 4 | 12PM to 1PM | 62.1 | 61.4 | 61 | 83.5 | 27.88 | 0.0728 | 0.54 | 13.9 | 1
November | 4 | 1PM to 2PM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
November | 4 | 2PM to 3PM | 64.9 | 63 | 62.1 | 86.8 | 29.1 | 0.0724 | 0.56 | 13.99 | 1
November | 4 | 3PM to 4PM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
November | 4 | 4PM to 5PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
November | 4 | 5PM to 6PM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
November | 4 | 6PM to 7PM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
November | 4 | 7PM to 8PM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
November | 4 | 8PM to 9PM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
November | 4 | 9PM to 10PM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
November | 4 | 10PM to 11PM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
November | 4 | 11PM to 12AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
November | 5 | 12AM to 1AM | 61 | 59 | 57.9 | 74.7 | 26.25 | 0.073 | 0.48 | 13.84 | 1
November | 5 | 1AM to 2AM | 60.1 | 58.2 | 57 | 72.3 | 25.65 | 0.0731 | 0.47 | 13.81 | 1
November | 5 | 2AM to 3AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
November | 5 | 3AM to 4AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
November | 5 | 4AM to 5AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
November | 5 | 5AM to 6AM | 59 | 57.8 | 57 | 72.3 | 25.39 | 0.0733 | 0.47 | 13.78 | 1
November | 5 | 6AM to 7AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
November | 5 | 7AM to 8AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
November | 5 | 8AM to 9AM | 61 | 59.7 | 59 | 77.7 | 26.71 | 0.073 | 0.5 | 13.85 | 1
November | 5 | 9AM to 10AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
November | 5 | 10AM to 11AM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
November | 5 | 11AM to 12PM | 69.1 | 65 | 63 | 89.6 | 30.56 | 0.0718 | 0.58 | 14.11 | 1
November | 5 | 12PM to 1PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
November | 5 | 1PM to 2PM | 73.9 | 65.3 | 61 | 83.5 | 30.79 | 0.0712 | 0.54 | 14.22 | 1
November | 5 | 2PM to 3PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
November | 5 | 3PM to 4PM | 75.9 | 64.2 | 57.9 | 74.7 | 29.9 | 0.071 | 0.48 | 14.24 | 1
November | 5 | 4PM to 5PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
November | 5 | 5PM to 6PM | 66 | 63.4 | 62.1 | 86.8 | 29.37 | 0.0722 | 0.56 | 14.02 | 1
November | 5 | 6PM to 7PM | 64 | 63.3 | 63 | 89.6 | 29.32 | 0.0725 | 0.58 | 13.97 | 1
November | 5 | 7PM to 8PM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
November | 5 | 8PM to 9PM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
November | 5 | 9PM to 10PM | 60.1 | 60.1 | 60.1 | 80.8 | 26.98 | 0.0731 | 0.52 | 13.84 | 1
November | 5 | 10PM to 11PM | 59 | 59 | 59 | 77.7 | 26.23 | 0.0733 | 0.5 | 13.8 | 1
November | 5 | 11PM to 12AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
November | 6 | 12AM to 1AM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
November | 6 | 1AM to 2AM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
November | 6 | 2AM to 3AM | 54 | 53.4 | 53.1 | 62.4 | 22.63 | 0.0741 | 0.41 | 13.62 | 1
November | 6 | 3AM to 4AM | 52 | 50.8 | 50 | 55.6 | 21.1 | 0.0744 | 0.36 | 13.55 | 1
November | 6 | 4AM to 5AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
November | 6 | 5AM to 6AM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
November | 6 | 6AM to 7AM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
November | 6 | 7AM to 8AM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
November | 6 | 8AM to 9AM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
November | 6 | 9AM to 10AM | 57.9 | 54.4 | 52 | 59.9 | 23.21 | 0.0735 | 0.39 | 13.72 | 1
November | 6 | 10AM to 11AM | 63 | 55.3 | 50 | 55.6 | 23.77 | 0.0728 | 0.36 | 13.84 | 1
November | 6 | 11AM to 12PM | 64 | 54.8 | 48 | 51.6 | 23.41 | 0.0727 | 0.34 | 13.85 | 1
November | 6 | 12PM to 1PM | 66 | 55 | 46.9 | 49.6 | 23.57 | 0.0725 | 0.32 | 13.9 | 1
November | 6 | 1PM to 2PM | 69.1 | 52.6 | 37.9 | 34.9 | 22.03 | 0.0721 | 0.23 | 13.93 | 1
November | 6 | 2PM to 3PM | 69.1 | 50.9 | 33.1 | 28.8 | 21.07 | 0.0722 | 0.19 | 13.91 | 1
November | 6 | 3PM to 4PM | 69.1 | 50.9 | 33.1 | 28.8 | 21.07 | 0.0722 | 0.19 | 13.91 | 1
November | 6 | 4PM to 5PM | 66 | 49.3 | 32 | 27.5 | 20.14 | 0.0726 | 0.18 | 13.83 | 1
November | 6 | 5PM to 6PM | 62.1 | 45.8 | 27 | 21.8 | 18.28 | 0.0732 | 0.14 | 13.71 | 1
November | 6 | 6PM to 7PM | 57.9 | 44.5 | 28.9 | 23.9 | 17.61 | 0.0738 | 0.16 | 13.6 | 1
November | 6 | 7PM to 8PM | 55 | 43.5 | 30 | 25.1 | 17.11 | 0.0742 | 0.16 | 13.53 | 1
November | 6 | 8PM to 9PM | 54 | 43 | 30 | 25.1 | 16.85 | 0.0743 | 0.16 | 13.5 | 1
November | 6 | 9PM to 10PM | 52 | 42.3 | 30.9 | 26.2 | 16.53 | 0.0746 | 0.17 | 13.46 | 1
November | 6 | 10PM to 11PM | 51.1 | 41.5 | 30 | 25.1 | 16.15 | 0.0747 | 0.16 | 13.43 | 1
November | 6 | 11PM to 12AM | 48.9 | 40 | 28.9 | 23.9 | 15.44 | 0.0751 | 0.16 | 13.37 | 1
November | 7 | 12AM to 1AM | 48 | 39.6 | 28.9 | 23.9 | 15.22 | 0.0752 | 0.16 | 13.34 | 1
November | 7 | 1AM to 2AM | 46.9 | 38.7 | 28 | 22.9 | 14.81 | 0.0754 | 0.15 | 13.31 | 1
November | 7 | 2AM to 3AM | 46 | 38.2 | 28 | 22.9 | 14.59 | 0.0755 | 0.15 | 13.29 | 1
November | 7 | 3AM to 4AM | 45 | 37.6 | 28 | 22.9 | 14.33 | 0.0757 | 0.15 | 13.26 | 1
November | 7 | 4AM to 5AM | 44.1 | 37.1 | 28 | 22.9 | 14.11 | 0.0758 | 0.15 | 13.24 | 1
November | 7 | 5AM to 6AM | 43 | 36.9 | 28.9 | 23.9 | 14.01 | 0.0759 | 0.16 | 13.21 | 1
November | 7 | 6AM to 7AM | 42.1 | 36.1 | 28 | 22.9 | 13.64 | 0.0761 | 0.15 | 13.19 | 1
November | 7 | 7AM to 8AM | 43 | 37.3 | 30 | 25.1 | 14.19 | 0.0759 | 0.16 | 13.22 | 1
November | 7 | 8AM to 9AM | 48 | 40.8 | 32 | 27.5 | 15.78 | 0.0752 | 0.18 | 13.36 | 1
November | 7 | 9AM to 10AM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
November | 7 | 10AM to 11AM | 57 | 44.4 | 30 | 25.1 | 17.59 | 0.0739 | 0.16 | 13.58 | 1
November | 7 | 11AM to 12PM | 61 | 46.3 | 30 | 25.1 | 18.54 | 0.0733 | 0.16 | 13.69 | 1
November | 7 | 12PM to 1PM | 64 | 47.1 | 28 | 22.9 | 18.94 | 0.0729 | 0.15 | 13.76 | 1
November | 7 | 1PM to 2PM | 64.9 | 46.9 | 26.1 | 20.9 | 18.84 | 0.0728 | 0.14 | 13.78 | 1
November | 7 | 2PM to 3PM | 66 | 47.4 | 26.1 | 20.9 | 19.1 | 0.0726 | 0.14 | 13.81 | 1
November | 7 | 3PM to 4PM | 64.9 | 46.6 | 25 | 19.8 | 18.68 | 0.0728 | 0.13 | 13.78 | 1
November | 7 | 4PM to 5PM | 62.1 | 45.6 | 26.1 | 20.9 | 18.14 | 0.0732 | 0.14 | 13.7 | 1
November | 7 | 5PM to 6PM | 55.9 | 42.6 | 26.1 | 20.9 | 16.67 | 0.0741 | 0.14 | 13.54 | 1
November | 7 | 6PM to 7PM | 53.1 | 41.2 | 26.1 | 20.9 | 15.97 | 0.0745 | 0.14 | 13.47 | 1
November | 7 | 7PM to 8PM | 50 | 39.9 | 27 | 21.8 | 15.37 | 0.0749 | 0.14 | 13.39 | 1
November | 7 | 8PM to 9PM | 48.9 | 39.7 | 28 | 22.9 | 15.29 | 0.0751 | 0.15 | 13.36 | 1
November | 7 | 9PM to 10PM | 46.9 | 39 | 28.9 | 23.9 | 14.96 | 0.0754 | 0.16 | 13.32 | 1
November | 7 | 10PM to 11PM | 46.9 | 39 | 28.9 | 23.9 | 14.96 | 0.0754 | 0.16 | 13.32 | 1
November | 7 | 11PM to 12AM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
November | 8 | 12AM to 1AM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
November | 8 | 1AM to 2AM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
November | 8 | 2AM to 3AM | 41 | 35.8 | 28.9 | 23.9 | 13.53 | 0.0762 | 0.16 | 13.16 | 1
November | 8 | 3AM to 4AM | 41 | 35.8 | 28.9 | 23.9 | 13.53 | 0.0762 | 0.16 | 13.16 | 1
November | 8 | 4AM to 5AM | 37.9 | 33.3 | 27 | 21.8 | 12.46 | 0.0767 | 0.14 | 13.07 | 1
November | 8 | 5AM to 6AM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
November | 8 | 6AM to 7AM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
November | 8 | 7AM to 8AM | 39.9 | 35.6 | 30 | 25.1 | 13.46 | 0.0764 | 0.16 | 13.14 | 1
November | 8 | 8AM to 9AM | 48.9 | 40.8 | 30.9 | 26.2 | 15.8 | 0.075 | 0.17 | 13.37 | 1
November | 8 | 9AM to 10AM | 53.1 | 42.8 | 30.9 | 26.2 | 16.8 | 0.0744 | 0.17 | 13.48 | 1
November | 8 | 10AM to 11AM | 59 | 45.7 | 30.9 | 26.2 | 18.23 | 0.0736 | 0.17 | 13.64 | 1
November | 8 | 11AM to 12PM | 64 | 48 | 30.9 | 26.2 | 19.45 | 0.0729 | 0.17 | 13.77 | 1
November | 8 | 12PM to 1PM | 66.9 | 48.6 | 28.9 | 23.9 | 19.79 | 0.0725 | 0.16 | 13.84 | 1
November | 8 | 1PM to 2PM | 69.1 | 49 | 27 | 21.8 | 19.98 | 0.0722 | 0.14 | 13.89 | 1
November | 8 | 2PM to 3PM | 71.1 | 49.9 | 27 | 21.8 | 20.46 | 0.0719 | 0.14 | 13.94 | 1
November | 8 | 3PM to 4PM | 71.1 | 49.6 | 26.1 | 20.9 | 20.32 | 0.0719 | 0.14 | 13.94 | 1
November | 8 | 4PM to 5PM | 70 | 49.7 | 28 | 22.9 | 20.37 | 0.0721 | 0.15 | 13.92 | 1
November | 8 | 5PM to 6PM | 66.9 | 48 | 27 | 21.8 | 19.46 | 0.0725 | 0.14 | 13.83 | 1
November | 8 | 6PM to 7PM | 62.1 | 46.4 | 28.9 | 23.9 | 18.61 | 0.0732 | 0.16 | 13.71 | 1
November | 8 | 7PM to 8PM | 61 | 45.9 | 28.9 | 23.9 | 18.35 | 0.0733 | 0.16 | 13.68 | 1
November | 8 | 8PM to 9PM | 59 | 45 | 28.9 | 23.9 | 17.87 | 0.0736 | 0.16 | 13.63 | 1
November | 8 | 9PM to 10PM | 57 | 44.4 | 30 | 25.1 | 17.59 | 0.0739 | 0.16 | 13.58 | 1
November | 8 | 10PM to 11PM | 54 | 43.3 | 30.9 | 26.2 | 17.01 | 0.0743 | 0.17 | 13.51 | 1
November | 8 | 11PM to 12AM | 52 | 42.7 | 32 | 27.5 | 16.74 | 0.0746 | 0.18 | 13.46 | 1
November | 9 | 12AM to 1AM | 50 | 42.1 | 33.1 | 28.8 | 16.45 | 0.0749 | 0.19 | 13.41 | 1
November | 9 | 1AM to 2AM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
November | 9 | 2AM to 3AM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
November | 9 | 3AM to 4AM | 45 | 38.7 | 30.9 | 26.2 | 14.84 | 0.0756 | 0.17 | 13.27 | 1
November | 9 | 4AM to 5AM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
November | 9 | 5AM to 6AM | 45 | 39.2 | 32 | 27.5 | 15.05 | 0.0756 | 0.18 | 13.27 | 1
November | 9 | 6AM to 7AM | 43 | 37.3 | 30 | 25.1 | 14.19 | 0.0759 | 0.16 | 13.22 | 1
November | 9 | 7AM to 8AM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
November | 9 | 8AM to 9AM | 48 | 41.9 | 35.1 | 31.1 | 16.34 | 0.0751 | 0.2 | 13.37 | 1
November | 9 | 9AM to 10AM | 51.1 | 44.2 | 37 | 33.7 | 17.48 | 0.0747 | 0.22 | 13.45 | 1
November | 9 | 10AM to 11AM | 55.9 | 47.3 | 39 | 36.4 | 19.08 | 0.074 | 0.24 | 13.59 | 1
November | 9 | 11AM to 12PM | 60.1 | 49.9 | 41 | 39.4 | 20.54 | 0.0734 | 0.26 | 13.71 | 1
November | 9 | 12PM to 1PM | 63 | 51.6 | 42.1 | 41.1 | 21.51 | 0.0729 | 0.27 | 13.79 | 1
November | 9 | 1PM to 2PM | 66.9 | 53.6 | 43 | 42.5 | 22.69 | 0.0724 | 0.28 | 13.9 | 1
November | 9 | 2PM to 3PM | 68 | 53.7 | 42.1 | 41.1 | 22.73 | 0.0722 | 0.27 | 13.92 | 1
November | 9 | 3PM to 4PM | 68 | 54.1 | 43 | 42.5 | 22.96 | 0.0722 | 0.28 | 13.93 | 1
November | 9 | 4PM to 5PM | 69.1 | 54.5 | 43 | 42.5 | 23.22 | 0.0721 | 0.28 | 13.96 | 1
November | 9 | 5PM to 6PM | 66 | 53.3 | 43 | 42.5 | 22.48 | 0.0725 | 0.28 | 13.88 | 1
November | 9 | 6PM to 7PM | 63 | 53.4 | 46 | 47.9 | 22.56 | 0.0729 | 0.31 | 13.81 | 1
November | 9 | 7PM to 8PM | 62.1 | 53.5 | 46.9 | 49.6 | 22.6 | 0.073 | 0.32 | 13.79 | 1
November | 9 | 8PM to 9PM | 59 | 52.2 | 46.9 | 49.6 | 21.86 | 0.0734 | 0.32 | 13.71 | 1
November | 9 | 9PM to 10PM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
November | 9 | 10PM to 11PM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
November | 9 | 11PM to 12AM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
November | 10 | 12AM to 1AM | 57 | 51.4 | 46.9 | 49.6 | 21.38 | 0.0737 | 0.32 | 13.66 | 1
November | 10 | 1AM to 2AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
November | 10 | 2AM to 3AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
November | 10 | 3AM to 4AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
November | 10 | 4AM to 5AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
November | 10 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
November | 10 | 6AM to 7AM | 52 | 49.2 | 46.9 | 49.6 | 20.15 | 0.0744 | 0.32 | 13.53 | 1
November | 10 | 7AM to 8AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
November | 10 | 8AM to 9AM | 55 | 51.1 | 48 | 51.6 | 21.22 | 0.074 | 0.34 | 13.61 | 1
November | 10 | 9AM to 10AM | 55.9 | 51.5 | 48 | 51.6 | 21.44 | 0.0739 | 0.34 | 13.64 | 1
November | 10 | 10AM to 11AM | 59 | 52.7 | 48 | 51.6 | 22.18 | 0.0734 | 0.34 | 13.72 | 1
November | 10 | 11AM to 12PM | 61 | 53.5 | 48 | 51.6 | 22.66 | 0.0731 | 0.34 | 13.77 | 1
November | 10 | 12PM to 1PM | 62.1 | 54 | 48 | 51.6 | 22.93 | 0.073 | 0.34 | 13.8 | 1
November | 10 | 1PM to 2PM | 64 | 54.2 | 46.9 | 49.6 | 23.09 | 0.0727 | 0.32 | 13.85 | 1
November | 10 | 2PM to 3PM | 66 | 54.1 | 45 | 45.9 | 23 | 0.0725 | 0.3 | 13.89 | 1
November | 10 | 3PM to 4PM | 64.9 | 52 | 41 | 39.4 | 21.72 | 0.0727 | 0.26 | 13.84 | 1
November | 10 | 4PM to 5PM | 63 | 51.2 | 41 | 39.4 | 21.24 | 0.0729 | 0.26 | 13.79 | 1
November | 10 | 5PM to 6PM | 60.1 | 50.4 | 42.1 | 41.1 | 20.81 | 0.0733 | 0.27 | 13.71 | 1
November | 10 | 6PM to 7PM | 57.9 | 49.5 | 42.1 | 41.1 | 20.28 | 0.0736 | 0.27 | 13.66 | 1
November | 10 | 7PM to 8PM | 57 | 49.5 | 43 | 42.5 | 20.29 | 0.0738 | 0.28 | 13.64 | 1
November | 10 | 8PM to 9PM | 55 | 50.1 | 46 | 47.9 | 20.64 | 0.074 | 0.31 | 13.6 | 1
November | 10 | 9PM to 10PM | 55 | 50.5 | 46.9 | 49.6 | 20.9 | 0.074 | 0.32 | 13.61 | 1
November | 10 | 10PM to 11PM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
November | 10 | 11PM to 12AM | 53.1 | 49.2 | 46 | 47.9 | 20.16 | 0.0743 | 0.31 | 13.55 | 1
November | 11 | 12AM to 1AM | 52 | 48.2 | 45 | 45.9 | 19.59 | 0.0745 | 0.3 | 13.52 | 1
November | 11 | 1AM to 2AM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
November | 11 | 2AM to 3AM | 48.9 | 46.4 | 44.1 | 44.4 | 18.61 | 0.0749 | 0.29 | 13.43 | 1
November | 11 | 3AM to 4AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
November | 11 | 4AM to 5AM | 46 | 45 | 44.1 | 44.4 | 17.91 | 0.0754 | 0.29 | 13.35 | 1
November | 11 | 5AM to 6AM | 43 | 42.5 | 42.1 | 41.1 | 16.66 | 0.0758 | 0.27 | 13.26 | 1
November | 11 | 6AM to 7AM | 44.1 | 43.1 | 42.1 | 41.1 | 16.92 | 0.0757 | 0.27 | 13.29 | 1
November | 11 | 7AM to 8AM | 43 | 42 | 41 | 39.4 | 16.4 | 0.0758 | 0.26 | 13.26 | 1
November | 11 | 8AM to 9AM | 48 | 45.4 | 43 | 42.5 | 18.11 | 0.0751 | 0.28 | 13.4 | 1
November | 11 | 9AM to 10AM | 55.9 | 49.5 | 44.1 | 44.4 | 20.31 | 0.0739 | 0.29 | 13.62 | 1
November | 11 | 10AM to 11AM | 62.1 | 51.6 | 43 | 42.5 | 21.52 | 0.0731 | 0.28 | 13.77 | 1
November | 11 | 11AM to 12PM | 66.9 | 53.3 | 42.1 | 41.1 | 22.47 | 0.0724 | 0.27 | 13.9 | 1
November | 11 | 12PM to 1PM | 70 | 52.9 | 37.9 | 34.9 | 22.25 | 0.072 | 0.23 | 13.96 | 1
November | 11 | 1PM to 2PM | 70 | 52.9 | 37.9 | 34.9 | 22.25 | 0.072 | 0.23 | 13.96 | 1
November | 11 | 2PM to 3PM | 70 | 53.3 | 39 | 36.4 | 22.49 | 0.072 | 0.24 | 13.96 | 1
November | 11 | 3PM to 4PM | 71.1 | 52.7 | 36 | 32.3 | 22.1 | 0.0719 | 0.21 | 13.98 | 1
November | 11 | 4PM to 5PM | 66.9 | 51 | 36 | 32.3 | 21.09 | 0.0724 | 0.21 | 13.87 | 1
November | 11 | 5PM to 6PM | 62.1 | 49.2 | 37 | 33.7 | 20.14 | 0.0731 | 0.22 | 13.74 | 1
November | 11 | 6PM to 7PM | 57.9 | 47 | 36 | 32.3 | 18.92 | 0.0737 | 0.21 | 13.63 | 1
November | 11 | 7PM to 8PM | 55.9 | 46.8 | 37.9 | 34.9 | 18.85 | 0.074 | 0.23 | 13.59 | 1
November | 11 | 8PM to 9PM | 54 | 46.4 | 39 | 36.4 | 18.6 | 0.0742 | 0.24 | 13.54 | 1
November | 11 | 9PM to 10PM | 52 | 45.5 | 39 | 36.4 | 18.12 | 0.0745 | 0.24 | 13.49 | 1
November | 11 | 10PM to 11PM | 48 | 43.6 | 39 | 36.4 | 17.16 | 0.0751 | 0.24 | 13.38 | 1
November | 11 | 11PM to 12AM | 46 | 42.1 | 37.9 | 34.9 | 16.45 | 0.0754 | 0.23 | 13.33 | 1
November | 12 | 12AM to 1AM | 44.1 | 40.7 | 37 | 33.7 | 15.78 | 0.0757 | 0.22 | 13.27 | 1
November | 12 | 1AM to 2AM | 44.1 | 40.7 | 37 | 33.7 | 15.78 | 0.0757 | 0.22 | 13.27 | 1
November | 12 | 2AM to 3AM | 43 | 40.2 | 37 | 33.7 | 15.52 | 0.0759 | 0.22 | 13.24 | 1
November | 12 | 3AM to 4AM | 45 | 41.2 | 37 | 33.7 | 16 | 0.0756 | 0.22 | 13.29 | 1
November | 12 | 4AM to 5AM | 46 | 40.9 | 35.1 | 31.1 | 15.86 | 0.0754 | 0.2 | 13.31 | 1
November | 12 | 5AM to 6AM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
November | 12 | 6AM to 7AM | 45 | 39.6 | 33.1 | 28.8 | 15.23 | 0.0756 | 0.19 | 13.28 | 1
November | 12 | 7AM to 8AM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
November | 12 | 8AM to 9AM | 50 | 42.5 | 34 | 29.8 | 16.62 | 0.0749 | 0.2 | 13.41 | 1
November | 12 | 9AM to 10AM | 53.1 | 44 | 34 | 29.8 | 17.36 | 0.0744 | 0.2 | 13.49 | 1
November | 12 | 10AM to 11AM | 57 | 46.2 | 35.1 | 31.1 | 18.52 | 0.0738 | 0.2 | 13.6 | 1
November | 12 | 11AM to 12PM | 62.1 | 48.8 | 36 | 32.3 | 19.92 | 0.0731 | 0.21 | 13.74 | 1
November | 12 | 12PM to 1PM | 64 | 49.7 | 36 | 32.3 | 20.4 | 0.0728 | 0.21 | 13.79 | 1
November | 12 | 1PM to 2PM | 66 | 51 | 37 | 33.7 | 21.1 | 0.0726 | 0.22 | 13.85 | 1
November | 12 | 2PM to 3PM | 68 | 51.4 | 36 | 32.3 | 21.36 | 0.0723 | 0.21 | 13.9 | 1
November | 12 | 3PM to 4PM | 66.9 | 51 | 36 | 32.3 | 21.09 | 0.0724 | 0.21 | 13.87 | 1
November | 12 | 4PM to 5PM | 64 | 50.1 | 37 | 33.7 | 20.62 | 0.0728 | 0.22 | 13.8 | 1
November | 12 | 5PM to 6PM | 59 | 47.9 | 37 | 33.7 | 19.4 | 0.0735 | 0.22 | 13.66 | 1
November | 12 | 6PM to 7PM | 57 | 47 | 37 | 33.7 | 18.92 | 0.0738 | 0.22 | 13.61 | 1
November | 12 | 7PM to 8PM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
November | 12 | 8PM to 9PM | 52 | 44.2 | 36 | 32.3 | 17.48 | 0.0746 | 0.21 | 13.47 | 1
November | 12 | 9PM to 10PM | 51.1 | 42.7 | 33.1 | 28.8 | 16.71 | 0.0747 | 0.19 | 13.44 | 1
November | 12 | 10PM to 11PM | 48 | 40.8 | 32 | 27.5 | 15.78 | 0.0752 | 0.18 | 13.36 | 1
November | 12 | 11PM to 12AM | 46.9 | 39.4 | 30 | 25.1 | 15.15 | 0.0753 | 0.16 | 13.32 | 1
November | 13 | 12AM to 1AM | 46 | 38.2 | 28 | 22.9 | 14.59 | 0.0755 | 0.15 | 13.29 | 1
November | 13 | 1AM to 2AM | 44.1 | 37.1 | 28 | 22.9 | 14.11 | 0.0758 | 0.15 | 13.24 | 1
November | 13 | 2AM to 3AM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
November | 13 | 3AM to 4AM | 42.1 | 35.7 | 27 | 21.8 | 13.46 | 0.0761 | 0.14 | 13.18 | 1
November | 13 | 4AM to 5AM | 39.9 | 34.4 | 27 | 21.8 | 12.94 | 0.0764 | 0.14 | 13.13 | 1
November | 13 | 5AM to 6AM | 39 | 33.9 | 27 | 21.8 | 12.72 | 0.0766 | 0.14 | 13.1 | 1
November | 13 | 6AM to 7AM | 37.9 | 33 | 26.1 | 20.9 | 12.32 | 0.0767 | 0.14 | 13.07 | 1
November | 13 | 7AM to 8AM | 39 | 33.6 | 26.1 | 20.9 | 12.58 | 0.0766 | 0.14 | 13.1 | 1
November | 13 | 8AM to 9AM | 39.9 | 34.1 | 26.1 | 20.9 | 12.8 | 0.0764 | 0.14 | 13.12 | 1
November | 13 | 9AM to 10AM | 44.1 | 36.4 | 26.1 | 20.9 | 13.8 | 0.0758 | 0.14 | 13.23 | 1
November | 13 | 10AM to 11AM | 48.9 | 39 | 26.1 | 20.9 | 14.97 | 0.0751 | 0.14 | 13.36 | 1
November | 13 | 11AM to 12PM | 50 | 39.6 | 26.1 | 20.9 | 15.23 | 0.0749 | 0.14 | 13.39 | 1
November | 13 | 12PM to 1PM | 54 | 41.9 | 27 | 21.8 | 16.33 | 0.0743 | 0.14 | 13.49 | 1
November | 13 | 1PM to 2PM | 55.9 | 42.9 | 27 | 21.8 | 16.81 | 0.0741 | 0.14 | 13.55 | 1
November | 13 | 2PM to 3PM | 57.9 | 44.2 | 28 | 22.9 | 17.46 | 0.0738 | 0.15 | 13.6 | 1
November | 13 | 3PM to 4PM | 57.9 | 44.2 | 28 | 22.9 | 17.46 | 0.0738 | 0.15 | 13.6 | 1
November | 13 | 4PM to 5PM | 55.9 | 43.5 | 28.9 | 23.9 | 17.14 | 0.074 | 0.16 | 13.55 | 1
November | 13 | 5PM to 6PM | 54 | 42.3 | 28 | 22.9 | 16.5 | 0.0743 | 0.15 | 13.5 | 1
November | 13 | 6PM to 7PM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
November | 13 | 7PM to 8PM | 50 | 41.3 | 30.9 | 26.2 | 16.06 | 0.0749 | 0.17 | 13.4 | 1
November | 13 | 8PM to 9PM | 48.9 | 40.8 | 30.9 | 26.2 | 15.8 | 0.075 | 0.17 | 13.37 | 1
November | 13 | 9PM to 10PM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
November | 13 | 10PM to 11PM | 45 | 39.2 | 32 | 27.5 | 15.05 | 0.0756 | 0.18 | 13.27 | 1
November | 13 | 11PM to 12AM | 43 | 38.1 | 32 | 27.5 | 14.57 | 0.0759 | 0.18 | 13.22 | 1
November | 14 | 12AM to 1AM | 43 | 38.5 | 33.1 | 28.8 | 14.76 | 0.0759 | 0.19 | 13.23 | 1
November | 14 | 1AM to 2AM | 43 | 37.7 | 30.9 | 26.2 | 14.36 | 0.0759 | 0.17 | 13.22 | 1
November | 14 | 2AM to 3AM | 42.1 | 37.2 | 30.9 | 26.2 | 14.14 | 0.0761 | 0.17 | 13.2 | 1
November | 14 | 3AM to 4AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
November | 14 | 4AM to 5AM | 39.9 | 35.2 | 28.9 | 23.9 | 13.27 | 0.0764 | 0.16 | 13.13 | 1
November | 14 | 5AM to 6AM | 39 | 33.9 | 27 | 21.8 | 12.72 | 0.0766 | 0.14 | 13.1 | 1
November | 14 | 6AM to 7AM | 37.9 | 33.3 | 27 | 21.8 | 12.46 | 0.0767 | 0.14 | 13.07 | 1
November | 14 | 7AM to 8AM | 35.1 | 32.4 | 28.9 | 23.9 | 12.09 | 0.0772 | 0.16 | 13 | 1
November | 14 | 8AM to 9AM | 48 | 40 | 30 | 25.1 | 15.41 | 0.0752 | 0.16 | 13.35 | 1
November | 14 | 9AM to 10AM | 53.1 | 39 | 18 | 14.2 | 14.93 | 0.0745 | 0.09 | 13.45 | 1
November | 14 | 10AM to 11AM | 57 | 40.4 | 15.1 | 12.3 | 15.6 | 0.074 | 0.08 | 13.54 | 1
November | 14 | 11AM to 12PM | 59 | 41.8 | 17.1 | 13.6 | 16.27 | 0.0737 | 0.09 | 13.6 | 1
November | 14 | 12PM to 1PM | 63 | 45.4 | 24.1 | 19 | 18.07 | 0.0731 | 0.12 | 13.72 | 1
November | 14 | 1PM to 2PM | 64.9 | 46.6 | 25 | 19.8 | 18.68 | 0.0728 | 0.13 | 13.78 | 1
November | 14 | 2PM to 3PM | 68 | 48.8 | 28 | 22.9 | 19.89 | 0.0724 | 0.15 | 13.87 | 1
November | 14 | 3PM to 4PM | 66.9 | 48.4 | 28 | 22.9 | 19.63 | 0.0725 | 0.15 | 13.84 | 1
November | 14 | 4PM to 5PM | 64 | 47.4 | 28.9 | 23.9 | 19.09 | 0.0729 | 0.16 | 13.77 | 1
November | 14 | 5PM to 6PM | 59 | 45 | 28.9 | 23.9 | 17.87 | 0.0736 | 0.16 | 13.63 | 1
November | 14 | 6PM to 7PM | 55 | 43.5 | 30 | 25.1 | 17.11 | 0.0742 | 0.16 | 13.53 | 1
November | 14 | 7PM to 8PM | 53.1 | 42.8 | 30.9 | 26.2 | 16.8 | 0.0744 | 0.17 | 13.48 | 1
November | 14 | 8PM to 9PM | 50 | 42.1 | 33.1 | 28.8 | 16.45 | 0.0749 | 0.19 | 13.41 | 1
November | 14 | 9PM to 10PM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
November | 14 | 10PM to 11PM | 46 | 40.1 | 33.1 | 28.8 | 15.5 | 0.0755 | 0.19 | 13.31 | 1
November | 14 | 11PM to 12AM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
November | 15 | 12AM to 1AM | 44.1 | 39.5 | 34 | 29.8 | 15.18 | 0.0757 | 0.2 | 13.26 | 1
November | 15 | 1AM to 2AM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
November | 15 | 2AM to 3AM | 45 | 40.4 | 35.1 | 31.1 | 15.6 | 0.0756 | 0.2 | 13.29 | 1
November | 15 | 3AM to 4AM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
November | 15 | 4AM to 5AM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
November | 15 | 5AM to 6AM | 41 | 37.8 | 34 | 29.8 | 14.44 | 0.0762 | 0.2 | 13.18 | 1
November | 15 | 6AM to 7AM | 39 | 36.8 | 34 | 29.8 | 13.96 | 0.0765 | 0.2 | 13.13 | 1
November | 15 | 7AM to 8AM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
November | 15 | 8AM to 9AM | 46.9 | 41.7 | 36 | 32.3 | 16.26 | 0.0753 | 0.21 | 13.34 | 1
November | 15 | 9AM to 10AM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
November | 15 | 10AM to 11AM | 63 | 49.6 | 37 | 33.7 | 20.36 | 0.073 | 0.22 | 13.77 | 1
November | 15 | 11AM to 12PM | 66 | 51 | 37 | 33.7 | 21.1 | 0.0726 | 0.22 | 13.85 | 1
November | 15 | 12PM to 1PM | 68 | 51.8 | 37 | 33.7 | 21.58 | 0.0723 | 0.22 | 13.9 | 1
November | 15 | 1PM to 2PM | 70 | 52.2 | 36 | 32.3 | 21.84 | 0.072 | 0.21 | 13.95 | 1
November | 15 | 2PM to 3PM | 71.1 | 52.7 | 36 | 32.3 | 22.1 | 0.0719 | 0.21 | 13.98 | 1
November | 15 | 3PM to 4PM | 70 | 52.2 | 36 | 32.3 | 21.84 | 0.072 | 0.21 | 13.95 | 1
November | 15 | 4PM to 5PM | 68 | 51.1 | 35.1 | 31.1 | 21.18 | 0.0723 | 0.2 | 13.89 | 1
November | 15 | 5PM to 6PM | 62.1 | 48.5 | 35.1 | 31.1 | 19.74 | 0.0731 | 0.2 | 13.74 | 1
November | 15 | 6PM to 7PM | 57.9 | 47 | 36 | 32.3 | 18.92 | 0.0737 | 0.21 | 13.63 | 1
November | 15 | 7PM to 8PM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
November | 15 | 8PM to 9PM | 54 | 45.1 | 36 | 32.3 | 17.96 | 0.0743 | 0.21 | 13.53 | 1
November | 15 | 9PM to 10PM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
November | 15 | 10PM to 11PM | 54 | 45.6 | 37 | 33.7 | 18.18 | 0.0743 | 0.22 | 13.53 | 1
November | 15 | 11PM to 12AM | 54 | 45.6 | 37 | 33.7 | 18.18 | 0.0743 | 0.22 | 13.53 | 1
November | 16 | 12AM to 1AM | 53.1 | 45.1 | 37 | 33.7 | 17.96 | 0.0744 | 0.22 | 13.51 | 1
November | 16 | 1AM to 2AM | 53.1 | 45.1 | 37 | 33.7 | 17.96 | 0.0744 | 0.22 | 13.51 | 1
November | 16 | 2AM to 3AM | 51.1 | 44.2 | 37 | 33.7 | 17.48 | 0.0747 | 0.22 | 13.45 | 1
November | 16 | 3AM to 4AM | 48.9 | 42.7 | 36 | 32.3 | 16.74 | 0.075 | 0.21 | 13.39 | 1
November | 16 | 4AM to 5AM | 48 | 42.3 | 36 | 32.3 | 16.52 | 0.0751 | 0.21 | 13.37 | 1
November | 16 | 5AM to 6AM | 50 | 43.7 | 37 | 33.7 | 17.22 | 0.0748 | 0.22 | 13.43 | 1
November | 16 | 6AM to 7AM | 50 | 44.5 | 39 | 36.4 | 17.64 | 0.0748 | 0.24 | 13.43 | 1
November | 16 | 7AM to 8AM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
November | 16 | 8AM to 9AM | 50 | 45.9 | 42.1 | 41.1 | 18.36 | 0.0748 | 0.27 | 13.45 | 1
November | 16 | 9AM to 10AM | 51.1 | 49.9 | 48.9 | 53.4 | 20.53 | 0.0746 | 0.35 | 13.52 | 1
November | 16 | 10AM to 11AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
November | 16 | 11AM to 12PM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
November | 16 | 12PM to 1PM | 55 | 53.9 | 53.1 | 62.4 | 22.89 | 0.0739 | 0.41 | 13.65 | 1
November | 16 | 1PM to 2PM | 59 | 55.4 | 53.1 | 62.4 | 23.86 | 0.0734 | 0.41 | 13.75 | 1
November | 16 | 2PM to 3PM | 61 | 56.7 | 54 | 64.5 | 24.67 | 0.0731 | 0.42 | 13.81 | 1
November | 16 | 3PM to 4PM | 62.1 | 57.1 | 54 | 64.5 | 24.93 | 0.0729 | 0.42 | 13.84 | 1
November | 16 | 4PM to 5PM | 62.1 | 56 | 52 | 59.9 | 24.22 | 0.0729 | 0.39 | 13.83 | 1
November | 16 | 5PM to 6PM | 59 | 54.3 | 51.1 | 58 | 23.17 | 0.0734 | 0.38 | 13.74 | 1
November | 16 | 6PM to 7PM | 57.9 | 53.3 | 50 | 55.6 | 22.54 | 0.0736 | 0.36 | 13.7 | 1
November | 16 | 7PM to 8PM | 57 | 50.9 | 46 | 47.9 | 21.12 | 0.0737 | 0.31 | 13.66 | 1
November | 16 | 8PM to 9PM | 55.9 | 49 | 43 | 42.5 | 20.03 | 0.0739 | 0.28 | 13.61 | 1
November | 16 | 9PM to 10PM | 53.1 | 46.3 | 39.9 | 37.8 | 18.59 | 0.0744 | 0.25 | 13.52 | 1
November | 16 | 10PM to 11PM | 53.1 | 46.3 | 39.9 | 37.8 | 18.59 | 0.0744 | 0.25 | 13.52 | 1
November | 16 | 11PM to 12AM | 54 | 47.2 | 41 | 39.4 | 19.06 | 0.0742 | 0.26 | 13.55 | 1
November | 17 | 12AM to 1AM | 53.1 | 47.3 | 42.1 | 41.1 | 19.1 | 0.0743 | 0.27 | 13.53 | 1
November | 17 | 1AM to 2AM | 50 | 46.3 | 43 | 42.5 | 18.59 | 0.0748 | 0.28 | 13.45 | 1
November | 17 | 2AM to 3AM | 48 | 45.4 | 43 | 42.5 | 18.11 | 0.0751 | 0.28 | 13.4 | 1
November | 17 | 3AM to 4AM | 46.9 | 44.9 | 43 | 42.5 | 17.85 | 0.0752 | 0.28 | 13.37 | 1
November | 17 | 4AM to 5AM | 45 | 43.5 | 42.1 | 41.1 | 17.14 | 0.0755 | 0.27 | 13.32 | 1
November | 17 | 5AM to 6AM | 46 | 44.5 | 43 | 42.5 | 17.63 | 0.0754 | 0.28 | 13.35 | 1
November | 17 | 6AM to 7AM | 45 | 43.9 | 43 | 42.5 | 17.36 | 0.0755 | 0.28 | 13.32 | 1
November | 17 | 7AM to 8AM | 45 | 44.5 | 44.1 | 44.4 | 17.65 | 0.0755 | 0.29 | 13.33 | 1
November | 17 | 8AM to 9AM | 50 | 47.9 | 46 | 47.9 | 19.41 | 0.0747 | 0.31 | 13.47 | 1
November | 17 | 9AM to 10AM | 55 | 49.5 | 45 | 45.9 | 20.34 | 0.074 | 0.3 | 13.6 | 1
November | 17 | 10AM to 11AM | 57.9 | 49.5 | 42.1 | 41.1 | 20.28 | 0.0736 | 0.27 | 13.66 | 1
November | 17 | 11AM to 12PM | 60.1 | 49.1 | 39 | 36.4 | 20.09 | 0.0734 | 0.24 | 13.7 | 1
November | 17 | 12PM to 1PM | 63 | 50 | 37.9 | 34.9 | 20.55 | 0.073 | 0.23 | 13.77 | 1
November | 17 | 1PM to 2PM | 64 | 48 | 30.9 | 26.2 | 19.45 | 0.0729 | 0.17 | 13.77 | 1
November | 17 | 2PM to 3PM | 64.9 | 49.4 | 34 | 29.8 | 20.23 | 0.0727 | 0.2 | 13.81 | 1
November | 17 | 3PM to 4PM | 64.9 | 48.8 | 32 | 27.5 | 19.88 | 0.0727 | 0.18 | 13.8 | 1
November | 17 | 4PM to 5PM | 63 | 47.5 | 30.9 | 26.2 | 19.19 | 0.073 | 0.17 | 13.74 | 1
November | 17 | 5PM to 6PM | 57.9 | 45.6 | 32 | 27.5 | 18.18 | 0.0737 | 0.18 | 13.62 | 1
November | 17 | 6PM to 7PM | 55.9 | 43.9 | 30 | 25.1 | 17.33 | 0.074 | 0.16 | 13.56 | 1
November | 17 | 7PM to 8PM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
November | 17 | 8PM to 9PM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
November | 17 | 9PM to 10PM | 48 | 40.3 | 30.9 | 26.2 | 15.58 | 0.0752 | 0.17 | 13.35 | 1
November | 17 | 10PM to 11PM | 46 | 39.3 | 30.9 | 26.2 | 15.1 | 0.0755 | 0.17 | 13.3 | 1
November | 17 | 11PM to 12AM | 44.1 | 38.2 | 30.9 | 26.2 | 14.62 | 0.0758 | 0.17 | 13.25 | 1
November | 18 | 12AM to 1AM | 41 | 37.1 | 32 | 27.5 | 14.09 | 0.0762 | 0.18 | 13.17 | 1
November | 18 | 1AM to 2AM | 41 | 36.6 | 30.9 | 26.2 | 13.88 | 0.0762 | 0.17 | 13.17 | 1
November | 18 | 2AM to 3AM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
November | 18 | 3AM to 4AM | 41 | 36.2 | 30 | 25.1 | 13.72 | 0.0762 | 0.16 | 13.16 | 1
November | 18 | 4AM to 5AM | 41 | 36.2 | 30 | 25.1 | 13.72 | 0.0762 | 0.16 | 13.16 | 1
November | 18 | 5AM to 6AM | 39.9 | 35.6 | 30 | 25.1 | 13.46 | 0.0764 | 0.16 | 13.14 | 1
November | 18 | 6AM to 7AM | 39 | 35.1 | 30 | 25.1 | 13.24 | 0.0765 | 0.16 | 13.11 | 1
November | 18 | 7AM to 8AM | 39.9 | 35.6 | 30 | 25.1 | 13.46 | 0.0764 | 0.16 | 13.14 | 1
November | 18 | 8AM to 9AM | 46 | 39.7 | 32 | 27.5 | 15.31 | 0.0755 | 0.18 | 13.3 | 1
November | 18 | 9AM to 10AM | 54 | 44.1 | 33.1 | 28.8 | 17.41 | 0.0743 | 0.19 | 13.52 | 1
November | 18 | 10AM to 11AM | 60.1 | 47.6 | 35.1 | 31.1 | 19.26 | 0.0734 | 0.2 | 13.68 | 1
November | 18 | 11AM to 12PM | 64 | 49 | 34 | 29.8 | 20.01 | 0.0729 | 0.2 | 13.78 | 1
November | 18 | 12PM to 1PM | 66.9 | 49.7 | 32 | 27.5 | 20.35 | 0.0725 | 0.18 | 13.85 | 1
November | 18 | 1PM to 2PM | 70 | 50.3 | 30 | 25.1 | 20.72 | 0.0721 | 0.16 | 13.93 | 1
November | 18 | 2PM to 3PM | 70 | 50 | 28.9 | 23.9 | 20.53 | 0.0721 | 0.16 | 13.92 | 1
November | 18 | 3PM to 4PM | 70 | 49.4 | 27 | 21.8 | 20.2 | 0.0721 | 0.14 | 13.91 | 1
November | 18 | 4PM to 5PM | 68 | 48.5 | 27 | 21.8 | 19.72 | 0.0724 | 0.14 | 13.86 | 1
November | 18 | 5PM to 6PM | 63 | 46.9 | 28.9 | 23.9 | 18.83 | 0.073 | 0.16 | 13.74 | 1
November | 18 | 6PM to 7PM | 59 | 45.4 | 30 | 25.1 | 18.07 | 0.0736 | 0.16 | 13.64 | 1
November | 18 | 7PM to 8PM | 55.9 | 44.7 | 32 | 27.5 | 17.7 | 0.074 | 0.18 | 13.56 | 1
November | 18 | 8PM to 9PM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
November | 18 | 9PM to 10PM | 52 | 42.3 | 30.9 | 26.2 | 16.53 | 0.0746 | 0.17 | 13.46 | 1
November | 18 | 10PM to 11PM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
November | 18 | 11PM to 12AM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
November | 19 | 12AM to 1AM | 55 | 43.8 | 30.9 | 26.2 | 17.27 | 0.0742 | 0.17 | 13.54 | 1
November | 19 | 1AM to 2AM | 50 | 41.3 | 30.9 | 26.2 | 16.06 | 0.0749 | 0.17 | 13.4 | 1
November | 19 | 2AM to 3AM | 48 | 40.8 | 32 | 27.5 | 15.78 | 0.0752 | 0.18 | 13.36 | 1
November | 19 | 3AM to 4AM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
November | 19 | 4AM to 5AM | 46.9 | 40.2 | 32 | 27.5 | 15.52 | 0.0753 | 0.18 | 13.33 | 1
November | 19 | 5AM to 6AM | 50 | 42.1 | 33.1 | 28.8 | 16.45 | 0.0749 | 0.19 | 13.41 | 1
November | 19 | 6AM to 7AM | 53.1 | 47.3 | 42.1 | 41.1 | 19.1 | 0.0743 | 0.27 | 13.53 | 1
November | 19 | 7AM to 8AM | 52 | 48.2 | 45 | 45.9 | 19.59 | 0.0745 | 0.3 | 13.52 | 1
November | 19 | 8AM to 9AM | 54 | 53.4 | 53.1 | 62.4 | 22.63 | 0.0741 | 0.41 | 13.62 | 1
November | 19 | 9AM to 10AM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
November | 19 | 10AM to 11AM | 57.9 | 56.7 | 55.9 | 69.4 | 24.68 | 0.0735 | 0.45 | 13.75 | 1
November | 19 | 11AM to 12PM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
November | 19 | 12PM to 1PM | 66 | 62.1 | 60.1 | 80.8 | 28.43 | 0.0723 | 0.52 | 14 | 1
November | 19 | 1PM to 2PM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
November | 19 | 2PM to 3PM | 75.9 | 65.9 | 61 | 83.5 | 31.28 | 0.0709 | 0.54 | 14.27 | 1
November | 19 | 3PM to 4PM | 75 | 65.1 | 60.1 | 80.8 | 30.64 | 0.0711 | 0.52 | 14.24 | 1
November | 19 | 4PM to 5PM | 73.9 | 64.2 | 59 | 77.7 | 29.89 | 0.0712 | 0.5 | 14.2 | 1
November | 19 | 5PM to 6PM | 73 | 63.9 | 59 | 77.7 | 29.67 | 0.0713 | 0.5 | 14.17 | 1
November | 19 | 6PM to 7PM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
November | 19 | 7PM to 8PM | 71.1 | 63.8 | 60.1 | 80.8 | 29.67 | 0.0716 | 0.52 | 14.13 | 1
November | 19 | 8PM to 9PM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
November | 19 | 9PM to 10PM | 71.1 | 64.4 | 61 | 83.5 | 30.09 | 0.0716 | 0.54 | 14.14 | 1
November | 19 | 10PM to 11PM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
November | 19 | 11PM to 12AM | 70 | 65.3 | 63 | 89.6 | 30.78 | 0.0717 | 0.58 | 14.13 | 1
November | 20 | 12AM to 1AM | 66.9 | 64.3 | 63 | 89.6 | 30.03 | 0.0721 | 0.58 | 14.05 | 1
November | 20 | 1AM to 2AM | 61 | 58.5 | 57 | 72.3 | 25.87 | 0.073 | 0.47 | 13.84 | 1
November | 20 | 2AM to 3AM | 55.9 | 50.9 | 46.9 | 49.6 | 21.12 | 0.0739 | 0.32 | 13.63 | 1
November | 20 | 3AM to 4AM | 52 | 48.2 | 45 | 45.9 | 19.59 | 0.0745 | 0.3 | 13.52 | 1
November | 20 | 4AM to 5AM | 46.9 | 42.2 | 37 | 33.7 | 16.48 | 0.0753 | 0.22 | 13.35 | 1
November | 20 | 5AM to 6AM | 43 | 40.2 | 37 | 33.7 | 15.52 | 0.0759 | 0.22 | 13.24 | 1
November | 20 | 6AM to 7AM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
November | 20 | 7AM to 8AM | 43 | 39.7 | 36 | 32.3 | 15.3 | 0.0759 | 0.21 | 13.24 | 1
November | 20 | 8AM to 9AM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
November | 20 | 9AM to 10AM | 41 | 36.2 | 30 | 25.1 | 13.72 | 0.0762 | 0.16 | 13.16 | 1
November | 20 | 10AM to 11AM | 39.9 | 35.6 | 30 | 25.1 | 13.46 | 0.0764 | 0.16 | 13.14 | 1
November | 20 | 11AM to 12PM | 39 | 34.7 | 28.9 | 23.9 | 13.05 | 0.0766 | 0.16 | 13.11 | 1
November | 20 | 12PM to 1PM | 39.9 | 35.2 | 28.9 | 23.9 | 13.27 | 0.0764 | 0.16 | 13.13 | 1
November | 20 | 1PM to 2PM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
November | 20 | 2PM to 3PM | 41 | 35.1 | 27 | 21.8 | 13.2 | 0.0763 | 0.14 | 13.15 | 1
November | 20 | 3PM to 4PM | 41 | 35.1 | 27 | 21.8 | 13.2 | 0.0763 | 0.14 | 13.15 | 1
November | 20 | 4PM to 5PM | 39.9 | 35.2 | 28.9 | 23.9 | 13.27 | 0.0764 | 0.16 | 13.13 | 1
November | 20 | 5PM to 6PM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
November | 20 | 6PM to 7PM | 39 | 33.6 | 26.1 | 20.9 | 12.58 | 0.0766 | 0.14 | 13.1 | 1
November | 20 | 7PM to 8PM | 37.9 | 33.3 | 27 | 21.8 | 12.46 | 0.0767 | 0.14 | 13.07 | 1
November | 20 | 8PM to 9PM | 37.9 | 33 | 26.1 | 20.9 | 12.32 | 0.0767 | 0.14 | 13.07 | 1
November | 20 | 9PM to 10PM | 37.9 | 33 | 26.1 | 20.9 | 12.32 | 0.0767 | 0.14 | 13.07 | 1
November | 20 | 10PM to 11PM | 37 | 32.1 | 25 | 19.8 | 11.95 | 0.0769 | 0.13 | 13.04 | 1
November | 20 | 11PM to 12AM | 37 | 32.5 | 26.1 | 20.9 | 12.11 | 0.0769 | 0.14 | 13.05 | 1
November | 21 | 12AM to 1AM | 32 | 28.3 | 23 | 18.1 | 10.46 | 0.0777 | 0.12 | 12.91 | 1
November | 21 | 1AM to 2AM | 32 | 27.9 | 21.9 | 17.1 | 10.32 | 0.0777 | 0.11 | 12.9 | 1
November | 21 | 2AM to 3AM | 30 | 26.8 | 21.9 | 17.1 | 9.84 | 0.078 | 0.11 | 12.85 | 1
November | 21 | 3AM to 4AM | 28.9 | 25.9 | 21 | 16.4 | 9.47 | 0.0782 | 0.11 | 12.82 | 1
November | 21 | 4AM to 5AM | 28 | 25.3 | 21 | 16.4 | 9.25 | 0.0783 | 0.11 | 12.8 | 1
November | 21 | 5AM to 6AM | 27 | 24.7 | 21 | 16.4 | 8.99 | 0.0785 | 0.11 | 12.77 | 1
November | 21 | 6AM to 7AM | 27 | 24.7 | 21 | 16.4 | 8.99 | 0.0785 | 0.11 | 12.77 | 1
November | 21 | 7AM to 8AM | 27 | 25 | 21.9 | 17.1 | 9.1 | 0.0785 | 0.11 | 12.77 | 1
November | 21 | 8AM to 9AM | 30.9 | 27.7 | 23 | 18.1 | 10.2 | 0.0779 | 0.12 | 12.88 | 1
November | 21 | 9AM to 10AM | 36 | 30.8 | 24.1 | 19 | 11.56 | 0.0771 | 0.12 | 13.01 | 1
November | 21 | 10AM to 11AM | 39.9 | 33.4 | 24.1 | 19 | 12.51 | 0.0764 | 0.12 | 13.12 | 1
November | 21 | 11AM to 12PM | 43 | 35.2 | 24.1 | 19 | 13.25 | 0.076 | 0.12 | 13.2 | 1
November | 21 | 12PM to 1PM | 45 | 35.9 | 23 | 18.1 | 13.58 | 0.0757 | 0.12 | 13.25 | 1
November | 21 | 1PM to 2PM | 48 | 37.9 | 24.1 | 19 | 14.47 | 0.0752 | 0.12 | 13.33 | 1
November | 21 | 2PM to 3PM | 50 | 38.7 | 23 | 18.1 | 14.8 | 0.0749 | 0.12 | 13.38 | 1
November | 21 | 3PM to 4PM | 48.9 | 37.8 | 21.9 | 17.1 | 14.4 | 0.0751 | 0.11 | 13.35 | 1
November | 21 | 4PM to 5PM | 45 | 35.9 | 23 | 18.1 | 13.58 | 0.0757 | 0.12 | 13.25 | 1
November | 21 | 5PM to 6PM | 42.1 | 34.3 | 23 | 18.1 | 12.89 | 0.0761 | 0.12 | 13.17 | 1
November | 21 | 6PM to 7PM | 39.9 | 33.1 | 23 | 18.1 | 12.37 | 0.0765 | 0.12 | 13.11 | 1
November | 21 | 7PM to 8PM | 37.9 | 31.5 | 23 | 18.1 | 11.89 | 0.0768 | 0.12 | 13.06 | 1
November | 21 | 8PM to 9PM | 37 | 31 | 23 | 18.1 | 11.67 | 0.0769 | 0.12 | 13.04 | 1
November | 21 | 9PM to 10PM | 36 | 30.8 | 24.1 | 19 | 11.56 | 0.0771 | 0.12 | 13.01 | 1
November | 21 | 10PM to 11PM | 34 | 29.8 | 24.1 | 19 | 11.08 | 0.0774 | 0.12 | 12.96 | 1
November | 21 | 11PM to 12AM | 30.9 | 27.7 | 23 | 18.1 | 10.2 | 0.0779 | 0.12 | 12.88 | 1
November | 22 | 12AM to 1AM | 30 | 27.2 | 23 | 18.1 | 9.98 | 0.078 | 0.12 | 12.85 | 1
November | 22 | 1AM to 2AM | 28 | 26 | 23 | 18.1 | 9.5 | 0.0783 | 0.12 | 12.8 | 1
November | 22 | 2AM to 3AM | 27 | 25 | 21.9 | 17.1 | 9.1 | 0.0785 | 0.11 | 12.77 | 1
November | 22 | 3AM to 4AM | 27 | 25 | 21.9 | 17.1 | 9.1 | 0.0785 | 0.11 | 12.77 | 1
November | 22 | 4AM to 5AM | 27 | 25 | 21.9 | 17.1 | 9.1 | 0.0785 | 0.11 | 12.77 | 1
November | 22 | 5AM to 6AM | 26.1 | 24.5 | 21.9 | 17.1 | 8.89 | 0.0786 | 0.11 | 12.75 | 1
November | 22 | 6AM to 7AM | 26.1 | 24.5 | 21.9 | 17.1 | 8.89 | 0.0786 | 0.11 | 12.75 | 1
November | 22 | 7AM to 8AM | 27 | 25 | 21.9 | 17.1 | 9.1 | 0.0785 | 0.11 | 12.77 | 1
November | 22 | 8AM to 9AM | 33.1 | 28.5 | 21.9 | 17.1 | 10.58 | 0.0775 | 0.11 | 12.93 | 1
November | 22 | 9AM to 10AM | 37.9 | 31.5 | 23 | 18.1 | 11.89 | 0.0768 | 0.12 | 13.06 | 1
November | 22 | 10AM to 11AM | 42.1 | 34.3 | 23 | 18.1 | 12.89 | 0.0761 | 0.12 | 13.17 | 1
November | 22 | 11AM to 12PM | 44.1 | 35.1 | 21.9 | 17.1 | 13.23 | 0.0758 | 0.11 | 13.22 | 1
November | 22 | 12PM to 1PM | 48 | 37.3 | 21.9 | 17.1 | 14.18 | 0.0752 | 0.11 | 13.32 | 1
November | 22 | 1PM to 2PM | 52 | 38.4 | 18 | 14.2 | 14.67 | 0.0747 | 0.09 | 13.42 | 1
November | 22 | 2PM to 3PM | 54 | 39.2 | 17.1 | 13.6 | 15.06 | 0.0744 | 0.09 | 13.47 | 1
November | 22 | 3PM to 4PM | 54 | 39.7 | 19 | 14.9 | 15.27 | 0.0744 | 0.1 | 13.47 | 1
November | 22 | 4PM to 5PM | 52 | 38.9 | 19.9 | 15.6 | 14.89 | 0.0747 | 0.1 | 13.42 | 1
November | 22 | 5PM to 6PM | 48 | 37 | 21 | 16.4 | 14.07 | 0.0752 | 0.11 | 13.32 | 1
November | 22 | 6PM to 7PM | 45 | 35.9 | 23 | 18.1 | 13.58 | 0.0757 | 0.12 | 13.25 | 1
November | 22 | 7PM to 8PM | 43 | 34.8 | 23 | 18.1 | 13.11 | 0.076 | 0.12 | 13.19 | 1
November | 22 | 8PM to 9PM | 42.1 | 34 | 21.9 | 17.1 | 12.75 | 0.0761 | 0.11 | 13.17 | 1
November | 22 | 9PM to 10PM | 41 | 33.7 | 23 | 18.1 | 12.63 | 0.0763 | 0.12 | 13.14 | 1
November | 22 | 10PM to 11PM | 39 | 32.2 | 21.9 | 17.1 | 12.01 | 0.0766 | 0.11 | 13.09 | 1
November | 22 | 11PM to 12AM | 37.9 | 31.9 | 24.1 | 19 | 12.04 | 0.0767 | 0.12 | 13.06 | 1
November | 23 | 12AM to 1AM | 39 | 32.9 | 24.1 | 19 | 12.3 | 0.0766 | 0.12 | 13.09 | 1
November | 23 | 1AM to 2AM | 37 | 31.4 | 24.1 | 19 | 11.82 | 0.0769 | 0.12 | 13.04 | 1
November | 23 | 2AM to 3AM | 35.1 | 30.7 | 25 | 19.8 | 11.47 | 0.0772 | 0.13 | 12.99 | 1
November | 23 | 3AM to 4AM | 36 | 31.2 | 25 | 19.8 | 11.69 | 0.0771 | 0.13 | 13.02 | 1
November | 23 | 4AM to 5AM | 37 | 32.1 | 25 | 19.8 | 11.95 | 0.0769 | 0.13 | 13.04 | 1
November | 23 | 5AM to 6AM | 33.1 | 29.6 | 25 | 19.8 | 10.99 | 0.0775 | 0.13 | 12.94 | 1
November | 23 | 6AM to 7AM | 34 | 30.1 | 25 | 19.8 | 11.21 | 0.0774 | 0.13 | 12.96 | 1
November | 23 | 7AM to 8AM | 36 | 31.5 | 26.1 | 20.9 | 11.85 | 0.077 | 0.14 | 13.02 | 1
November | 23 | 8AM to 9AM | 41 | 35.5 | 28 | 22.9 | 13.38 | 0.0763 | 0.15 | 13.16 | 1
November | 23 | 9AM to 10AM | 48.9 | 39 | 26.1 | 20.9 | 14.97 | 0.0751 | 0.14 | 13.36 | 1
November | 23 | 10AM to 11AM | 53.1 | 41.5 | 27 | 21.8 | 16.11 | 0.0745 | 0.14 | 13.47 | 1
November | 23 | 11AM to 12PM | 55 | 42.4 | 27 | 21.8 | 16.59 | 0.0742 | 0.14 | 13.52 | 1
November | 23 | 12PM to 1PM | 55.9 | 43.5 | 28.9 | 23.9 | 17.14 | 0.074 | 0.16 | 13.55 | 1
November | 23 | 1PM to 2PM | 57 | 44.1 | 28.9 | 23.9 | 17.4 | 0.0739 | 0.16 | 13.58 | 1
November | 23 | 2PM to 3PM | 57 | 44.1 | 28.9 | 23.9 | 17.4 | 0.0739 | 0.16 | 13.58 | 1
November | 23 | 3PM to 4PM | 57.9 | 44.9 | 30 | 25.1 | 17.8 | 0.0737 | 0.16 | 13.61 | 1
November | 23 | 4PM to 5PM | 57 | 44.4 | 30 | 25.1 | 17.59 | 0.0739 | 0.16 | 13.58 | 1
November | 23 | 5PM to 6PM | 57 | 44.8 | 30.9 | 26.2 | 17.75 | 0.0739 | 0.17 | 13.59 | 1
November | 23 | 6PM to 7PM | 55.9 | 43.9 | 30 | 25.1 | 17.33 | 0.074 | 0.16 | 13.56 | 1
November | 23 | 7PM to 8PM | 55 | 43.5 | 30 | 25.1 | 17.11 | 0.0742 | 0.16 | 13.53 | 1
November | 23 | 8PM to 9PM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
November | 23 | 9PM to 10PM | 52 | 43.9 | 35.1 | 31.1 | 17.3 | 0.0746 | 0.2 | 13.47 | 1
November | 23 | 10PM to 11PM | 48.9 | 44 | 39 | 36.4 | 17.38 | 0.075 | 0.24 | 13.41 | 1
November | 23 | 11PM to 12AM | 48 | 44.5 | 41 | 39.4 | 17.62 | 0.0751 | 0.26 | 13.39 | 1
November | 24 | 12AM to 1AM | 46.9 | 44.5 | 42.1 | 41.1 | 17.62 | 0.0752 | 0.27 | 13.37 | 1
November | 24 | 1AM to 2AM | 46.9 | 45.9 | 45 | 45.9 | 18.37 | 0.0752 | 0.3 | 13.38 | 1
November | 24 | 2AM to 3AM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
November | 24 | 3AM to 4AM | 48 | 47.4 | 46.9 | 49.6 | 19.19 | 0.075 | 0.32 | 13.42 | 1
November | 24 | 4AM to 5AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
November | 24 | 5AM to 6AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
November | 24 | 6AM to 7AM | 46.9 | 46.9 | 46.9 | 49.6 | 18.93 | 0.0752 | 0.32 | 13.39 | 1
November | 24 | 7AM to 8AM | 46.9 | 46.5 | 46 | 47.9 | 18.67 | 0.0752 | 0.31 | 13.39 | 1
November | 24 | 8AM to 9AM | 50 | 47.9 | 46 | 47.9 | 19.41 | 0.0747 | 0.31 | 13.47 | 1
November | 24 | 9AM to 10AM | 53.1 | 49.7 | 46.9 | 49.6 | 20.42 | 0.0743 | 0.32 | 13.56 | 1
November | 24 | 10AM to 11AM | 55.9 | 47.7 | 39.9 | 37.8 | 19.29 | 0.074 | 0.25 | 13.6 | 1
November | 24 | 11AM to 12PM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
November | 24 | 12PM to 1PM | 55 | 46.1 | 37 | 33.7 | 18.44 | 0.0741 | 0.22 | 13.56 | 1
November | 24 | 1PM to 2PM | 55.9 | 45.7 | 35.1 | 31.1 | 18.26 | 0.074 | 0.2 | 13.57 | 1
November | 24 | 2PM to 3PM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
November | 24 | 3PM to 4PM | 55 | 44.9 | 34 | 29.8 | 17.84 | 0.0741 | 0.2 | 13.55 | 1
November | 24 | 4PM to 5PM | 52 | 43.4 | 34 | 29.8 | 17.1 | 0.0746 | 0.2 | 13.47 | 1
November | 24 | 5PM to 6PM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
November | 24 | 6PM to 7PM | 46 | 40.5 | 34 | 29.8 | 15.66 | 0.0755 | 0.2 | 13.31 | 1
November | 24 | 7PM to 8PM | 43 | 38.9 | 34 | 29.8 | 14.92 | 0.0759 | 0.2 | 13.23 | 1
November | 24 | 8PM to 9PM | 41 | 37.5 | 33.1 | 28.8 | 14.28 | 0.0762 | 0.19 | 13.17 | 1
November | 24 | 9PM to 10PM | 39.9 | 36.9 | 33.1 | 28.8 | 14.02 | 0.0764 | 0.19 | 13.15 | 1
November | 24 | 10PM to 11PM | 39 | 36.4 | 33.1 | 28.8 | 13.8 | 0.0765 | 0.19 | 13.12 | 1
November | 24 | 11PM to 12AM | 37.9 | 35.8 | 33.1 | 28.8 | 13.54 | 0.0767 | 0.19 | 13.09 | 1
November | 25 | 12AM to 1AM | 37 | 34.9 | 32 | 27.5 | 13.13 | 0.0768 | 0.18 | 13.07 | 1
November | 25 | 1AM to 2AM | 37 | 34.9 | 32 | 27.5 | 13.13 | 0.0768 | 0.18 | 13.07 | 1
November | 25 | 2AM to 3AM | 37 | 34.9 | 32 | 27.5 | 13.13 | 0.0768 | 0.18 | 13.07 | 1
November | 25 | 3AM to 4AM | 36 | 34.3 | 32 | 27.5 | 12.87 | 0.077 | 0.18 | 13.04 | 1
November | 25 | 4AM to 5AM | 35.1 | 33.8 | 32 | 27.5 | 12.65 | 0.0771 | 0.18 | 13.01 | 1
November | 25 | 5AM to 6AM | 33.1 | 32.1 | 30.9 | 26.2 | 11.97 | 0.0775 | 0.17 | 12.96 | 1
November | 25 | 6AM to 7AM | 34 | 32.7 | 30.9 | 26.2 | 12.18 | 0.0773 | 0.17 | 12.98 | 1
November | 25 | 7AM to 8AM | 34 | 32.7 | 30.9 | 26.2 | 12.18 | 0.0773 | 0.17 | 12.98 | 1
November | 25 | 8AM to 9AM | 39.9 | 36.5 | 32 | 27.5 | 13.83 | 0.0764 | 0.18 | 13.14 | 1
November | 25 | 9AM to 10AM | 45 | 39.6 | 33.1 | 28.8 | 15.23 | 0.0756 | 0.19 | 13.28 | 1
November | 25 | 10AM to 11AM | 51.1 | 42.7 | 33.1 | 28.8 | 16.71 | 0.0747 | 0.19 | 13.44 | 1
November | 25 | 11AM to 12PM | 54 | 44.4 | 34 | 29.8 | 17.58 | 0.0743 | 0.2 | 13.52 | 1
November | 25 | 12PM to 1PM | 57 | 45.9 | 34 | 29.8 | 18.32 | 0.0738 | 0.2 | 13.6 | 1
November | 25 | 1PM to 2PM | 61 | 47.4 | 33.1 | 28.8 | 19.11 | 0.0733 | 0.19 | 13.7 | 1
November | 25 | 2PM to 3PM | 63 | 48.3 | 33.1 | 28.8 | 19.59 | 0.073 | 0.19 | 13.75 | 1
November | 25 | 3PM to 4PM | 63 | 48.3 | 33.1 | 28.8 | 19.59 | 0.073 | 0.19 | 13.75 | 1
November | 25 | 4PM to 5PM | 60.1 | 47.3 | 34 | 29.8 | 19.06 | 0.0734 | 0.2 | 13.68 | 1
November | 25 | 5PM to 6PM | 57 | 45.9 | 34 | 29.8 | 18.32 | 0.0738 | 0.2 | 13.6 | 1
November | 25 | 6PM to 7PM | 55 | 45.3 | 35.1 | 31.1 | 18.04 | 0.0741 | 0.2 | 13.55 | 1
November | 25 | 7PM to 8PM | 51.1 | 43.4 | 35.1 | 31.1 | 17.08 | 0.0747 | 0.2 | 13.45 | 1
November | 25 | 8PM to 9PM | 51.1 | 43.4 | 35.1 | 31.1 | 17.08 | 0.0747 | 0.2 | 13.45 | 1
November | 25 | 9PM to 10PM | 48 | 41.9 | 35.1 | 31.1 | 16.34 | 0.0751 | 0.2 | 13.37 | 1
November | 25 | 10PM to 11PM | 46.9 | 41.4 | 35.1 | 31.1 | 16.08 | 0.0753 | 0.2 | 13.34 | 1
November | 25 | 11PM to 12AM | 48 | 41.9 | 35.1 | 31.1 | 16.34 | 0.0751 | 0.2 | 13.37 | 1
November | 26 | 12AM to 1AM | 45 | 40.4 | 35.1 | 31.1 | 15.6 | 0.0756 | 0.2 | 13.29 | 1
November | 26 | 1AM to 2AM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
November | 26 | 2AM to 3AM | 43 | 39.3 | 35.1 | 31.1 | 15.12 | 0.0759 | 0.2 | 13.23 | 1
November | 26 | 3AM to 4AM | 39.9 | 37.3 | 34 | 29.8 | 14.18 | 0.0764 | 0.2 | 13.15 | 1
November | 26 | 4AM to 5AM | 37.9 | 36.2 | 34 | 29.8 | 13.7 | 0.0767 | 0.2 | 13.1 | 1
November | 26 | 5AM to 6AM | 37.9 | 36.2 | 34 | 29.8 | 13.7 | 0.0767 | 0.2 | 13.1 | 1
November | 26 | 6AM to 7AM | 37 | 35.7 | 34 | 29.8 | 13.48 | 0.0768 | 0.2 | 13.07 | 1
November | 26 | 7AM to 8AM | 37.9 | 36.2 | 34 | 29.8 | 13.7 | 0.0767 | 0.2 | 13.1 | 1
November | 26 | 8AM to 9AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
November | 26 | 9AM to 10AM | 46.9 | 43.4 | 39.9 | 37.8 | 17.11 | 0.0753 | 0.25 | 13.36 | 1
November | 26 | 10AM to 11AM | 54 | 48.6 | 44.1 | 44.4 | 19.83 | 0.0742 | 0.29 | 13.56 | 1
November | 26 | 11AM to 12PM | 60.1 | 51.3 | 44.1 | 44.4 | 21.32 | 0.0733 | 0.29 | 13.73 | 1
November | 26 | 12PM to 1PM | 63 | 52 | 43 | 42.5 | 21.73 | 0.0729 | 0.28 | 13.8 | 1
November | 26 | 1PM to 2PM | 66.9 | 53.6 | 43 | 42.5 | 22.69 | 0.0724 | 0.28 | 13.9 | 1
November | 26 | 2PM to 3PM | 68 | 52.9 | 39.9 | 37.8 | 22.21 | 0.0723 | 0.25 | 13.91 | 1
November | 26 | 3PM to 4PM | 68 | 52.9 | 39.9 | 37.8 | 22.21 | 0.0723 | 0.25 | 13.91 | 1
November | 26 | 4PM to 5PM | 66 | 52.5 | 41 | 39.4 | 21.98 | 0.0725 | 0.26 | 13.87 | 1
November | 26 | 5PM to 6PM | 63 | 51.6 | 42.1 | 41.1 | 21.51 | 0.0729 | 0.27 | 13.79 | 1
November | 26 | 6PM to 7PM | 62.1 | 51.6 | 43 | 42.5 | 21.52 | 0.0731 | 0.28 | 13.77 | 1
November | 26 | 7PM to 8PM | 57.9 | 49.9 | 43 | 42.5 | 20.51 | 0.0736 | 0.28 | 13.66 | 1
November | 26 | 8PM to 9PM | 57 | 50 | 44.1 | 44.4 | 20.57 | 0.0738 | 0.29 | 13.64 | 1
November | 26 | 9PM to 10PM | 57 | 50.4 | 45 | 45.9 | 20.82 | 0.0737 | 0.3 | 13.65 | 1
November | 26 | 10PM to 11PM | 57.9 | 50.8 | 45 | 45.9 | 21.04 | 0.0736 | 0.3 | 13.67 | 1
November | 26 | 11PM to 12AM | 57.9 | 50.8 | 45 | 45.9 | 21.04 | 0.0736 | 0.3 | 13.67 | 1
November | 27 | 12AM to 1AM | 57 | 50.4 | 45 | 45.9 | 20.82 | 0.0737 | 0.3 | 13.65 | 1
November | 27 | 1AM to 2AM | 55 | 50.1 | 46 | 47.9 | 20.64 | 0.074 | 0.31 | 13.6 | 1
November | 27 | 2AM to 3AM | 57 | 54 | 52 | 59.9 | 22.99 | 0.0737 | 0.39 | 13.69 | 1
November | 27 | 3AM to 4AM | 57.9 | 55.5 | 54 | 64.5 | 23.92 | 0.0735 | 0.42 | 13.73 | 1
November | 27 | 4AM to 5AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
November | 27 | 5AM to 6AM | 63 | 60.4 | 59 | 77.7 | 27.2 | 0.0727 | 0.5 | 13.91 | 1
November | 27 | 6AM to 7AM | 64 | 60.8 | 59 | 77.7 | 27.46 | 0.0726 | 0.5 | 13.93 | 1
November | 27 | 7AM to 8AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
November | 27 | 8AM to 9AM | 64 | 61.5 | 60.1 | 80.8 | 27.95 | 0.0725 | 0.52 | 13.94 | 1
November | 27 | 9AM to 10AM | 64.9 | 61.8 | 60.1 | 80.8 | 28.17 | 0.0724 | 0.52 | 13.97 | 1
November | 27 | 10AM to 11AM | 66.9 | 62.5 | 60.1 | 80.8 | 28.65 | 0.0721 | 0.52 | 14.02 | 1
November | 27 | 11AM to 12PM | 70 | 63.5 | 60.1 | 80.8 | 29.4 | 0.0717 | 0.52 | 14.1 | 1
November | 27 | 12PM to 1PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
November | 27 | 1PM to 2PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
November | 27 | 2PM to 3PM | 72 | 63.5 | 59 | 77.7 | 29.4 | 0.0715 | 0.5 | 14.14 | 1
November | 27 | 3PM to 4PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
November | 27 | 4PM to 5PM | 72 | 64.7 | 61 | 83.5 | 30.31 | 0.0714 | 0.54 | 14.16 | 1
November | 27 | 5PM to 6PM | 71.1 | 65 | 62.1 | 86.8 | 30.6 | 0.0715 | 0.56 | 14.15 | 1
November | 27 | 6PM to 7PM | 70 | 64.7 | 62.1 | 86.8 | 30.34 | 0.0717 | 0.56 | 14.12 | 1
November | 27 | 7PM to 8PM | 69.1 | 64.4 | 62.1 | 86.8 | 30.12 | 0.0718 | 0.56 | 14.1 | 1
November | 27 | 8PM to 9PM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
November | 27 | 9PM to 10PM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
November | 27 | 10PM to 11PM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
November | 27 | 11PM to 12AM | 66 | 64 | 63 | 89.6 | 29.81 | 0.0722 | 0.58 | 14.02 | 1
November | 28 | 12AM to 1AM | 64.9 | 63.6 | 63 | 89.6 | 29.54 | 0.0724 | 0.58 | 14 | 1
November | 28 | 1AM to 2AM | 62.1 | 59.4 | 57.9 | 74.7 | 26.51 | 0.0729 | 0.48 | 13.87 | 1
November | 28 | 2AM to 3AM | 57.9 | 55 | 53.1 | 62.4 | 23.59 | 0.0735 | 0.41 | 13.72 | 1
November | 28 | 3AM to 4AM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
November | 28 | 4AM to 5AM | 54 | 51.1 | 48.9 | 53.4 | 21.23 | 0.0741 | 0.35 | 13.59 | 1
November | 28 | 5AM to 6AM | 53.1 | 50.7 | 48.9 | 53.4 | 21.02 | 0.0743 | 0.35 | 13.57 | 1
November | 28 | 6AM to 7AM | 51.1 | 49.4 | 48 | 51.6 | 20.26 | 0.0746 | 0.34 | 13.51 | 1
November | 28 | 7AM to 8AM | 51.1 | 48.8 | 46.9 | 49.6 | 19.93 | 0.0746 | 0.32 | 13.5 | 1
November | 28 | 8AM to 9AM | 50 | 47.9 | 46 | 47.9 | 19.41 | 0.0747 | 0.31 | 13.47 | 1
November | 28 | 9AM to 10AM | 53.1 | 47.3 | 42.1 | 41.1 | 19.1 | 0.0743 | 0.27 | 13.53 | 1
November | 28 | 10AM to 11AM | 55.9 | 44.7 | 32 | 27.5 | 17.7 | 0.074 | 0.18 | 13.56 | 1
November | 28 | 11AM to 12PM | 57 | 43.4 | 27 | 21.8 | 17.07 | 0.0739 | 0.14 | 13.57 | 1
November | 28 | 12PM to 1PM | 60.1 | 44.3 | 25 | 19.8 | 17.51 | 0.0735 | 0.13 | 13.65 | 1
November | 28 | 1PM to 2PM | 63 | 44.9 | 21.9 | 17.1 | 17.78 | 0.0731 | 0.11 | 13.72 | 1
November | 28 | 2PM to 3PM | 62.1 | 44.2 | 21 | 16.4 | 17.45 | 0.0732 | 0.11 | 13.69 | 1
November | 28 | 3PM to 4PM | 62.1 | 44.2 | 21 | 16.4 | 17.45 | 0.0732 | 0.11 | 13.69 | 1
November | 28 | 4PM to 5PM | 59 | 42.7 | 21 | 16.4 | 16.71 | 0.0736 | 0.11 | 13.61 | 1
November | 28 | 5PM to 6PM | 55 | 40.7 | 21 | 16.4 | 15.76 | 0.0742 | 0.11 | 13.51 | 1
November | 28 | 6PM to 7PM | 53.1 | 40.2 | 23 | 18.1 | 15.54 | 0.0745 | 0.12 | 13.46 | 1
November | 28 | 7PM to 8PM | 51.1 | 39.8 | 25 | 19.8 | 15.33 | 0.0748 | 0.13 | 13.41 | 1
November | 28 | 8PM to 9PM | 48.9 | 39 | 26.1 | 20.9 | 14.97 | 0.0751 | 0.14 | 13.36 | 1
November | 28 | 9PM to 10PM | 46.9 | 38.3 | 27 | 21.8 | 14.63 | 0.0754 | 0.14 | 13.31 | 1
November | 28 | 10PM to 11PM | 46 | 38.2 | 28 | 22.9 | 14.59 | 0.0755 | 0.15 | 13.29 | 1
November | 28 | 11PM to 12AM | 45 | 37.6 | 28 | 22.9 | 14.33 | 0.0757 | 0.15 | 13.26 | 1
November | 29 | 12AM to 1AM | 44.1 | 37.1 | 28 | 22.9 | 14.11 | 0.0758 | 0.15 | 13.24 | 1
November | 29 | 1AM to 2AM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
November | 29 | 2AM to 3AM | 43 | 36.1 | 27 | 21.8 | 13.68 | 0.076 | 0.14 | 13.21 | 1
November | 29 | 3AM to 4AM | 41 | 35.5 | 28 | 22.9 | 13.38 | 0.0763 | 0.15 | 13.16 | 1
November | 29 | 4AM to 5AM | 41 | 35.5 | 28 | 22.9 | 13.38 | 0.0763 | 0.15 | 13.16 | 1
November | 29 | 5AM to 6AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
November | 29 | 6AM to 7AM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
November | 29 | 7AM to 8AM | 43 | 37.3 | 30 | 25.1 | 14.19 | 0.0759 | 0.16 | 13.22 | 1
November | 29 | 8AM to 9AM | 46 | 38.9 | 30 | 25.1 | 14.93 | 0.0755 | 0.16 | 13.3 | 1
November | 29 | 9AM to 10AM | 48.9 | 40.8 | 30.9 | 26.2 | 15.8 | 0.075 | 0.17 | 13.37 | 1
November | 29 | 10AM to 11AM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
November | 29 | 11AM to 12PM | 54 | 43.7 | 32 | 27.5 | 17.22 | 0.0743 | 0.18 | 13.51 | 1
November | 29 | 12PM to 1PM | 55.9 | 44.2 | 30.9 | 26.2 | 17.49 | 0.074 | 0.17 | 13.56 | 1
November | 29 | 1PM to 2PM | 57 | 44.4 | 30 | 25.1 | 17.59 | 0.0739 | 0.16 | 13.58 | 1
November | 29 | 2PM to 3PM | 57 | 44.4 | 30 | 25.1 | 17.59 | 0.0739 | 0.16 | 13.58 | 1
November | 29 | 3PM to 4PM | 55.9 | 44.2 | 30.9 | 26.2 | 17.49 | 0.074 | 0.17 | 13.56 | 1
November | 29 | 4PM to 5PM | 55.9 | 44.7 | 32 | 27.5 | 17.7 | 0.074 | 0.18 | 13.56 | 1
November | 29 | 5PM to 6PM | 55 | 44.6 | 33.1 | 28.8 | 17.67 | 0.0741 | 0.19 | 13.54 | 1
November | 29 | 6PM to 7PM | 55 | 44.2 | 32 | 27.5 | 17.48 | 0.0741 | 0.18 | 13.54 | 1
November | 29 | 7PM to 8PM | 55 | 44.6 | 33.1 | 28.8 | 17.67 | 0.0741 | 0.19 | 13.54 | 1
November | 29 | 8PM to 9PM | 53.1 | 44 | 34 | 29.8 | 17.36 | 0.0744 | 0.2 | 13.49 | 1
November | 29 | 9PM to 10PM | 53.1 | 44.4 | 35.1 | 31.1 | 17.56 | 0.0744 | 0.2 | 13.5 | 1
November | 29 | 10PM to 11PM | 53.1 | 44.4 | 35.1 | 31.1 | 17.56 | 0.0744 | 0.2 | 13.5 | 1
November | 29 | 11PM to 12AM | 48 | 45.4 | 43 | 42.5 | 18.11 | 0.0751 | 0.28 | 13.4 | 1
November | 30 | 12AM to 1AM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
November | 30 | 1AM to 2AM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
November | 30 | 2AM to 3AM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
November | 30 | 3AM to 4AM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
November | 30 | 4AM to 5AM | 46 | 44.5 | 43 | 42.5 | 17.63 | 0.0754 | 0.28 | 13.35 | 1
November | 30 | 5AM to 6AM | 46.9 | 44.5 | 42.1 | 41.1 | 17.62 | 0.0752 | 0.27 | 13.37 | 1
November | 30 | 6AM to 7AM | 43 | 41.5 | 39.9 | 37.8 | 16.15 | 0.0759 | 0.25 | 13.25 | 1
November | 30 | 7AM to 8AM | 43 | 42.5 | 42.1 | 41.1 | 16.66 | 0.0758 | 0.27 | 13.26 | 1
November | 30 | 8AM to 9AM | 42.1 | 41.5 | 41 | 39.4 | 16.18 | 0.076 | 0.26 | 13.23 | 1
November | 30 | 9AM to 10AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
November | 30 | 10AM to 11AM | 43 | 43 | 43 | 42.5 | 16.88 | 0.0758 | 0.28 | 13.27 | 1
November | 30 | 11AM to 12PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
November | 30 | 12PM to 1PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
November | 30 | 1PM to 2PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
November | 30 | 2PM to 3PM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
November | 30 | 3PM to 4PM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
November | 30 | 4PM to 5PM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
November | 30 | 5PM to 6PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
November | 30 | 6PM to 7PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
November | 30 | 7PM to 8PM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
November | 30 | 8PM to 9PM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
November | 30 | 9PM to 10PM | 39.9 | 39.3 | 38.7 | 35.9 | 15.12 | 0.0763 | 0.24 | 13.17 | 1
November | 30 | 10PM to 11PM | 37.8 | 36.6 | 35.2 | 31.4 | 13.9 | 0.0767 | 0.21 | 13.1 | 1
November | 30 | 11PM to 12AM | 35.6 | 34.1 | 32 | 27.5 | 12.78 | 0.0771 | 0.18 | 13.03 | 1
December | 1 | 12AM to 1AM | 33.4 | 31.1 | 28.4 | 23.3 | 11.61 | 0.0774 | 0.15 | 12.96 | 1
December | 1 | 1AM to 2AM | 31.5 | 28.7 | 25 | 19.8 | 10.6 | 0.0778 | 0.13 | 12.9 | 1
December | 1 | 2AM to 3AM | 29.3 | 26.2 | 21.6 | 16.9 | 9.62 | 0.0781 | 0.11 | 12.83 | 1
December | 1 | 3AM to 4AM | 27 | 23.7 | 18 | 14.2 | 8.65 | 0.0785 | 0.09 | 12.76 | 1
December | 1 | 4AM to 5AM | 27 | 24 | 19 | 14.9 | 8.76 | 0.0785 | 0.1 | 12.76 | 1
December | 1 | 5AM to 6AM | 25 | 23.1 | 19.9 | 15.6 | 8.39 | 0.0788 | 0.1 | 12.71 | 1
December | 1 | 6AM to 7AM | 25 | 23.1 | 19.9 | 15.6 | 8.39 | 0.0788 | 0.1 | 12.71 | 1
December | 1 | 7AM to 8AM | 26.1 | 23.8 | 19.9 | 15.6 | 8.65 | 0.0786 | 0.1 | 12.74 | 1
December | 1 | 8AM to 9AM | 30.9 | 27 | 21 | 16.4 | 9.95 | 0.0779 | 0.11 | 12.87 | 1
December | 1 | 9AM to 10AM | 35.1 | 30 | 23 | 18.1 | 11.2 | 0.0772 | 0.12 | 12.99 | 1
December | 1 | 10AM to 11AM | 39.9 | 33.4 | 24.1 | 19 | 12.51 | 0.0764 | 0.12 | 13.12 | 1
December | 1 | 11AM to 12PM | 44.1 | 35.1 | 21.9 | 17.1 | 13.23 | 0.0758 | 0.11 | 13.22 | 1
December | 1 | 12PM to 1PM | 46 | 36 | 21 | 16.4 | 13.59 | 0.0755 | 0.11 | 13.27 | 1
December | 1 | 1PM to 2PM | 50 | 38.1 | 21 | 16.4 | 14.55 | 0.075 | 0.11 | 13.37 | 1
December | 1 | 2PM to 3PM | 51.1 | 37.7 | 17.1 | 13.6 | 14.36 | 0.0748 | 0.09 | 13.39 | 1
December | 1 | 3PM to 4PM | 52 | 37.5 | 14 | 11.7 | 14.29 | 0.0747 | 0.08 | 13.41 | 1
December | 1 | 4PM to 5PM | 50 | 36.7 | 15.1 | 12.3 | 13.91 | 0.075 | 0.08 | 13.36 | 1
December | 1 | 5PM to 6PM | 46.9 | 34.8 | 14 | 11.7 | 13.07 | 0.0754 | 0.08 | 13.28 | 1
December | 1 | 6PM to 7PM | 42.1 | 32.4 | 16 | 12.9 | 12.09 | 0.0762 | 0.08 | 13.15 | 1
December | 1 | 7PM to 8PM | 41 | 31.6 | 18 | 14.2 | 12.03 | 0.0763 | 0.09 | 13.13 | 1
December | 1 | 8PM to 9PM | 39.9 | 31.1 | 18 | 14.2 | 11.77 | 0.0765 | 0.09 | 13.1 | 1
December | 1 | 9PM to 10PM | 39 | 30.9 | 19 | 14.9 | 11.67 | 0.0766 | 0.1 | 13.08 | 1
December | 1 | 10PM to 11PM | 37.9 | 30.6 | 19.9 | 15.6 | 11.51 | 0.0768 | 0.1 | 13.05 | 1
December | 1 | 11PM to 12AM | 37 | 30.1 | 19.9 | 15.6 | 11.29 | 0.0769 | 0.1 | 13.03 | 1
December | 2 | 12AM to 1AM | 37.9 | 30.6 | 19.9 | 15.6 | 11.51 | 0.0768 | 0.1 | 13.05 | 1
December | 2 | 1AM to 2AM | 37 | 30.1 | 19.9 | 15.6 | 11.29 | 0.0769 | 0.1 | 13.03 | 1
December | 2 | 2AM to 3AM | 36 | 29.5 | 19.9 | 15.6 | 11.03 | 0.0771 | 0.1 | 13 | 1
December | 2 | 3AM to 4AM | 34 | 28.7 | 21 | 16.4 | 10.68 | 0.0774 | 0.11 | 12.95 | 1
December | 2 | 4AM to 5AM | 32 | 28.3 | 23 | 18.1 | 10.46 | 0.0777 | 0.12 | 12.91 | 1
December | 2 | 5AM to 6AM | 30 | 26.1 | 19.9 | 15.6 | 9.6 | 0.078 | 0.1 | 12.85 | 1
December | 2 | 6AM to 7AM | 28 | 24.1 | 17.1 | 13.6 | 8.81 | 0.0783 | 0.09 | 12.79 | 1
December | 2 | 7AM to 8AM | 27 | 23.1 | 16 | 12.9 | 8.45 | 0.0785 | 0.08 | 12.76 | 1
December | 2 | 8AM to 9AM | 30 | 25 | 16 | 12.9 | 9.18 | 0.078 | 0.08 | 12.84 | 1
December | 2 | 9AM to 10AM | 33.1 | 26.5 | 15.1 | 12.3 | 9.83 | 0.0776 | 0.08 | 12.92 | 1
December | 2 | 10AM to 11AM | 35.1 | 27.4 | 14 | 11.7 | 10.21 | 0.0772 | 0.08 | 12.97 | 1
December | 2 | 11AM to 12PM | 37.9 | 29 | 14 | 11.7 | 10.91 | 0.0768 | 0.08 | 13.04 | 1
December | 2 | 12PM to 1PM | 39.9 | 30.1 | 14 | 11.7 | 11.38 | 0.0765 | 0.08 | 13.09 | 1
December | 2 | 1PM to 2PM | 41 | 30.7 | 14 | 11.7 | 11.64 | 0.0763 | 0.08 | 13.12 | 1
December | 2 | 2PM to 3PM | 43 | 31.7 | 14 | 11.7 | 12.12 | 0.076 | 0.08 | 13.17 | 1
December | 2 | 3PM to 4PM | 43 | 31.7 | 14 | 11.7 | 12.12 | 0.076 | 0.08 | 13.17 | 1
December | 2 | 4PM to 5PM | 39.9 | 29.9 | 12.9 | 11.1 | 11.29 | 0.0765 | 0.07 | 13.09 | 1
December | 2 | 5PM to 6PM | 36 | 27.2 | 10.9 | 10 | 10.18 | 0.0771 | 0.07 | 12.99 | 1
December | 2 | 6PM to 7PM | 34 | 26.1 | 10.9 | 10 | 9.7 | 0.0774 | 0.07 | 12.93 | 1
December | 2 | 7PM to 8PM | 32 | 24.9 | 10.9 | 10 | 9.22 | 0.0777 | 0.07 | 12.88 | 1
December | 2 | 8PM to 9PM | 30.9 | 24.5 | 12 | 10.6 | 9.05 | 0.0779 | 0.07 | 12.86 | 1
December | 2 | 9PM to 10PM | 30 | 24.2 | 12.9 | 11.1 | 8.91 | 0.078 | 0.07 | 12.83 | 1
December | 2 | 10PM to 11PM | 30 | 24.2 | 12.9 | 11.1 | 8.91 | 0.078 | 0.07 | 12.83 | 1
December | 2 | 11PM to 12AM | 32 | 24.9 | 10.9 | 10 | 9.22 | 0.0777 | 0.07 | 12.88 | 1
December | 3 | 12AM to 1AM | 32 | 25.2 | 12 | 10.6 | 9.31 | 0.0777 | 0.07 | 12.88 | 1
December | 3 | 1AM to 2AM | 30 | 24 | 12 | 10.6 | 8.83 | 0.078 | 0.07 | 12.83 | 1
December | 3 | 2AM to 3AM | 28.9 | 23.3 | 12 | 10.6 | 8.57 | 0.0782 | 0.07 | 12.8 | 1
December | 3 | 3AM to 4AM | 27 | 22.1 | 12 | 10.6 | 8.09 | 0.0785 | 0.07 | 12.75 | 1
December | 3 | 4AM to 5AM | 26.1 | 21.5 | 12 | 10.6 | 7.88 | 0.0787 | 0.07 | 12.73 | 1
December | 3 | 5AM to 6AM | 26.1 | 21.5 | 12 | 10.6 | 7.88 | 0.0787 | 0.07 | 12.73 | 1
December | 3 | 6AM to 7AM | 26.1 | 21.5 | 12 | 10.6 | 7.88 | 0.0787 | 0.07 | 12.73 | 1
December | 3 | 7AM to 8AM | 25 | 20.6 | 10.9 | 10 | 7.53 | 0.0789 | 0.07 | 12.7 | 1
December | 3 | 8AM to 9AM | 30 | 23.5 | 10 | 9.6 | 8.68 | 0.0781 | 0.06 | 12.83 | 1
December | 3 | 9AM to 10AM | 32 | 24.7 | 10 | 9.6 | 9.15 | 0.0777 | 0.06 | 12.88 | 1
December | 3 | 10AM to 11AM | 35.1 | 26.7 | 10.9 | 10 | 9.96 | 0.0773 | 0.07 | 12.96 | 1
December | 3 | 11AM to 12PM | 37.9 | 28.6 | 12 | 10.6 | 10.74 | 0.0768 | 0.07 | 13.04 | 1
December | 3 | 12PM to 1PM | 41 | 30.3 | 12 | 10.6 | 11.47 | 0.0763 | 0.07 | 13.12 | 1
December | 3 | 1PM to 2PM | 43 | 31.1 | 10.9 | 10 | 11.86 | 0.076 | 0.07 | 13.17 | 1
December | 3 | 2PM to 3PM | 43 | 30.9 | 10 | 9.6 | 11.8 | 0.076 | 0.06 | 13.17 | 1
December | 3 | 3PM to 4PM | 44.1 | 32.3 | 10 | 9.6 | 12.06 | 0.0759 | 0.06 | 13.2 | 1
December | 3 | 4PM to 5PM | 42.1 | 30.4 | 10 | 9.6 | 11.58 | 0.0762 | 0.06 | 13.15 | 1
December | 3 | 5PM to 6PM | 39.9 | 29.3 | 10 | 9.6 | 11.06 | 0.0765 | 0.06 | 13.09 | 1
December | 3 | 6PM to 7PM | 37.9 | 28.2 | 10 | 9.6 | 10.58 | 0.0768 | 0.06 | 13.04 | 1
December | 3 | 7PM to 8PM | 37 | 27.7 | 10 | 9.6 | 10.37 | 0.077 | 0.06 | 13.01 | 1
December | 3 | 8PM to 9PM | 37 | 27.8 | 10.9 | 10 | 10.44 | 0.0769 | 0.07 | 13.01 | 1
December | 3 | 9PM to 10PM | 35.1 | 26.7 | 10.9 | 10 | 9.96 | 0.0773 | 0.07 | 12.96 | 1
December | 3 | 10PM to 11PM | 35.1 | 26.9 | 12 | 10.6 | 10.04 | 0.0773 | 0.07 | 12.96 | 1
December | 3 | 11PM to 12AM | 35.1 | 26.9 | 12 | 10.6 | 10.04 | 0.0773 | 0.07 | 12.96 | 1
December | 4 | 12AM to 1AM | 33.1 | 26 | 12.9 | 11.1 | 9.64 | 0.0776 | 0.07 | 12.91 | 1
December | 4 | 1AM to 2AM | 28.9 | 24.1 | 15.1 | 12.3 | 8.84 | 0.0782 | 0.08 | 12.81 | 1
December | 4 | 2AM to 3AM | 27 | 23.4 | 17.1 | 13.6 | 8.55 | 0.0785 | 0.09 | 12.76 | 1
December | 4 | 3AM to 4AM | 28 | 23.8 | 16 | 12.9 | 8.71 | 0.0783 | 0.08 | 12.79 | 1
December | 4 | 4AM to 5AM | 27 | 23.1 | 16 | 12.9 | 8.45 | 0.0785 | 0.08 | 12.76 | 1
December | 4 | 5AM to 6AM | 27 | 23.1 | 16 | 12.9 | 8.45 | 0.0785 | 0.08 | 12.76 | 1
December | 4 | 6AM to 7AM | 26.1 | 22.6 | 16 | 12.9 | 8.23 | 0.0787 | 0.08 | 12.73 | 1
December | 4 | 7AM to 8AM | 26.1 | 22.6 | 16 | 12.9 | 8.23 | 0.0787 | 0.08 | 12.73 | 1
December | 4 | 8AM to 9AM | 32 | 26.4 | 17.1 | 13.6 | 9.77 | 0.0777 | 0.09 | 12.89 | 1
December | 4 | 9AM to 10AM | 39 | 30.1 | 16 | 12.9 | 11.35 | 0.0766 | 0.08 | 13.07 | 1
December | 4 | 10AM to 11AM | 44.1 | 33.6 | 16 | 12.9 | 12.56 | 0.0759 | 0.08 | 13.21 | 1
December | 4 | 11AM to 12PM | 50 | 36.9 | 16 | 12.9 | 13.99 | 0.075 | 0.08 | 13.36 | 1
December | 4 | 12PM to 1PM | 52 | 37.8 | 15.1 | 12.3 | 14.38 | 0.0747 | 0.08 | 13.41 | 1
December | 4 | 1PM to 2PM | 54 | 38.6 | 14 | 11.7 | 14.76 | 0.0744 | 0.08 | 13.46 | 1
December | 4 | 2PM to 3PM | 55 | 39.2 | 14 | 11.7 | 15.02 | 0.0742 | 0.08 | 13.49 | 1
December | 4 | 3PM to 4PM | 55.9 | 39.6 | 14 | 11.7 | 15.24 | 0.0741 | 0.08 | 13.51 | 1
December | 4 | 4PM to 5PM | 54 | 38.8 | 15.1 | 12.3 | 14.86 | 0.0744 | 0.08 | 13.46 | 1
December | 4 | 5PM to 6PM | 51.1 | 37.7 | 17.1 | 13.6 | 14.36 | 0.0748 | 0.09 | 13.39 | 1
December | 4 | 6PM to 7PM | 46.9 | 34.5 | 12.9 | 11.1 | 12.98 | 0.0754 | 0.07 | 13.28 | 1
December | 4 | 7PM to 8PM | 44.1 | 34.3 | 19 | 14.9 | 12.88 | 0.0758 | 0.1 | 13.21 | 1
December | 4 | 8PM to 9PM | 41 | 33.1 | 21 | 16.4 | 12.38 | 0.0763 | 0.11 | 13.14 | 1
December | 4 | 9PM to 10PM | 41 | 33.1 | 21 | 16.4 | 12.38 | 0.0763 | 0.11 | 13.14 | 1
December | 4 | 10PM to 11PM | 39.9 | 32.5 | 21 | 16.4 | 12.12 | 0.0765 | 0.11 | 13.11 | 1
December | 4 | 11PM to 12AM | 39.9 | 31.6 | 19.9 | 15.6 | 11.99 | 0.0765 | 0.1 | 13.11 | 1
December | 5 | 12AM to 1AM | 37.9 | 30.9 | 21 | 16.4 | 11.64 | 0.0768 | 0.11 | 13.06 | 1
December | 5 | 1AM to 2AM | 37 | 30.1 | 19.9 | 15.6 | 11.29 | 0.0769 | 0.1 | 13.03 | 1
December | 5 | 2AM to 3AM | 36 | 29.5 | 19.9 | 15.6 | 11.03 | 0.0771 | 0.1 | 13 | 1
December | 5 | 3AM to 4AM | 36 | 29.5 | 19.9 | 15.6 | 11.03 | 0.0771 | 0.1 | 13 | 1
December | 5 | 4AM to 5AM | 35.1 | 29 | 19.9 | 15.6 | 10.82 | 0.0772 | 0.1 | 12.98 | 1
December | 5 | 5AM to 6AM | 35.1 | 29 | 19.9 | 15.6 | 10.82 | 0.0772 | 0.1 | 12.98 | 1
December | 5 | 6AM to 7AM | 34 | 28.4 | 19.9 | 15.6 | 10.56 | 0.0774 | 0.1 | 12.95 | 1
December | 5 | 7AM to 8AM | 33.1 | 27.9 | 19.9 | 15.6 | 10.34 | 0.0775 | 0.1 | 12.93 | 1
December | 5 | 8AM to 9AM | 42.1 | 34.3 | 23 | 18.1 | 12.89 | 0.0761 | 0.12 | 13.17 | 1
December | 5 | 9AM to 10AM | 46.9 | 37.6 | 25 | 19.8 | 14.34 | 0.0754 | 0.13 | 13.3 | 1
December | 5 | 10AM to 11AM | 52 | 40 | 24.1 | 19 | 15.42 | 0.0746 | 0.12 | 13.43 | 1
December | 5 | 11AM to 12PM | 55 | 41.6 | 24.1 | 19 | 16.16 | 0.0742 | 0.12 | 13.51 | 1
December | 5 | 12PM to 1PM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
December | 5 | 1PM to 2PM | 62.1 | 45 | 24.1 | 19 | 17.85 | 0.0732 | 0.12 | 13.7 | 1
December | 5 | 2PM to 3PM | 63 | 44.4 | 19.9 | 15.6 | 17.54 | 0.0731 | 0.1 | 13.71 | 1
December | 5 | 3PM to 4PM | 61 | 43.2 | 19 | 14.9 | 16.96 | 0.0734 | 0.1 | 13.66 | 1
December | 5 | 4PM to 5PM | 57.9 | 42.2 | 21 | 16.4 | 16.45 | 0.0738 | 0.11 | 13.58 | 1
December | 5 | 5PM to 6PM | 55 | 41 | 21.9 | 17.1 | 15.87 | 0.0742 | 0.11 | 13.51 | 1
December | 5 | 6PM to 7PM | 53.1 | 39.7 | 21 | 16.4 | 15.28 | 0.0745 | 0.11 | 13.45 | 1
December | 5 | 7PM to 8PM | 53.1 | 39.9 | 21.9 | 17.1 | 15.4 | 0.0745 | 0.11 | 13.46 | 1
December | 5 | 8PM to 9PM | 52 | 39.4 | 21.9 | 17.1 | 15.13 | 0.0747 | 0.11 | 13.43 | 1
December | 5 | 9PM to 10PM | 50 | 39 | 24.1 | 19 | 14.95 | 0.0749 | 0.12 | 13.38 | 1
December | 5 | 10PM to 11PM | 48.9 | 39 | 26.1 | 20.9 | 14.97 | 0.0751 | 0.14 | 13.36 | 1
December | 5 | 11PM to 12AM | 50 | 39.9 | 27 | 21.8 | 15.37 | 0.0749 | 0.14 | 13.39 | 1
December | 6 | 12AM to 1AM | 51.1 | 40.2 | 26.1 | 20.9 | 15.49 | 0.0748 | 0.14 | 13.42 | 1
December | 6 | 1AM to 2AM | 50 | 40.6 | 28.9 | 23.9 | 15.7 | 0.0749 | 0.16 | 13.4 | 1
December | 6 | 2AM to 3AM | 48 | 40.3 | 30.9 | 26.2 | 15.58 | 0.0752 | 0.17 | 13.35 | 1
December | 6 | 3AM to 4AM | 48 | 42.7 | 37 | 33.7 | 16.74 | 0.0751 | 0.22 | 13.37 | 1
December | 6 | 4AM to 5AM | 46.9 | 44.5 | 42.1 | 41.1 | 17.62 | 0.0752 | 0.27 | 13.37 | 1
December | 6 | 5AM to 6AM | 46.9 | 44.5 | 42.1 | 41.1 | 17.62 | 0.0752 | 0.27 | 13.37 | 1
December | 6 | 6AM to 7AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
December | 6 | 7AM to 8AM | 48 | 48 | 48 | 51.6 | 19.51 | 0.075 | 0.34 | 13.43 | 1
December | 6 | 8AM to 9AM | 50 | 50 | 50 | 55.6 | 20.62 | 0.0747 | 0.36 | 13.49 | 1
December | 6 | 9AM to 10AM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
December | 6 | 10AM to 11AM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
December | 6 | 11AM to 12PM | 54 | 52.8 | 52 | 59.9 | 22.25 | 0.0741 | 0.39 | 13.61 | 1
December | 6 | 12PM to 1PM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
December | 6 | 1PM to 2PM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
December | 6 | 2PM to 3PM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
December | 6 | 3PM to 4PM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
December | 6 | 4PM to 5PM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
December | 6 | 5PM to 6PM | 55.9 | 55.9 | 55.9 | 69.4 | 24.2 | 0.0738 | 0.45 | 13.69 | 1
December | 6 | 6PM to 7PM | 57 | 57 | 57 | 72.3 | 24.9 | 0.0736 | 0.47 | 13.73 | 1
December | 6 | 7PM to 8PM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
December | 6 | 8PM to 9PM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
December | 6 | 9PM to 10PM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
December | 6 | 10PM to 11PM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
December | 6 | 11PM to 12AM | 52 | 50.8 | 50 | 55.6 | 21.1 | 0.0744 | 0.36 | 13.55 | 1
December | 7 | 12AM to 1AM | 48.9 | 47.4 | 46 | 47.9 | 19.15 | 0.0749 | 0.31 | 13.44 | 1
December | 7 | 1AM to 2AM | 46 | 44.5 | 43 | 42.5 | 17.63 | 0.0754 | 0.28 | 13.35 | 1
December | 7 | 2AM to 3AM | 44.1 | 43.1 | 42.1 | 41.1 | 16.92 | 0.0757 | 0.27 | 13.29 | 1
December | 7 | 3AM to 4AM | 42.1 | 41.5 | 41 | 39.4 | 16.18 | 0.076 | 0.26 | 13.23 | 1
December | 7 | 4AM to 5AM | 41 | 40.5 | 39.9 | 37.8 | 15.67 | 0.0762 | 0.25 | 13.2 | 1
December | 7 | 5AM to 6AM | 39 | 38.5 | 37.9 | 34.9 | 14.75 | 0.0765 | 0.23 | 13.14 | 1
December | 7 | 6AM to 7AM | 37 | 37 | 37 | 33.7 | 14.08 | 0.0768 | 0.22 | 13.08 | 1
December | 7 | 7AM to 8AM | 35.1 | 34.6 | 34 | 29.8 | 13 | 0.0771 | 0.2 | 13.02 | 1
December | 7 | 8AM to 9AM | 37 | 36.2 | 35.1 | 31.1 | 13.69 | 0.0768 | 0.2 | 13.08 | 1
December | 7 | 9AM to 10AM | 44.1 | 40.7 | 37 | 33.7 | 15.78 | 0.0757 | 0.22 | 13.27 | 1
December | 7 | 10AM to 11AM | 48 | 41.1 | 33.1 | 28.8 | 15.97 | 0.0752 | 0.19 | 13.36 | 1
December | 7 | 11AM to 12PM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
December | 7 | 12PM to 1PM | 55 | 42.2 | 26.1 | 20.9 | 16.45 | 0.0742 | 0.14 | 13.52 | 1
December | 7 | 1PM to 2PM | 57 | 42.6 | 24.1 | 19 | 16.64 | 0.0739 | 0.12 | 13.57 | 1
December | 7 | 2PM to 3PM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
December | 7 | 3PM to 4PM | 59 | 43.8 | 25 | 19.8 | 17.24 | 0.0736 | 0.13 | 13.62 | 1
December | 7 | 4PM to 5PM | 57.9 | 43.6 | 26.1 | 20.9 | 17.15 | 0.0738 | 0.14 | 13.6 | 1
December | 7 | 5PM to 6PM | 54 | 41.9 | 27 | 21.8 | 16.33 | 0.0743 | 0.14 | 13.49 | 1
December | 7 | 6PM to 7PM | 52 | 40.6 | 26.1 | 20.9 | 15.71 | 0.0746 | 0.14 | 13.44 | 1
December | 7 | 7PM to 8PM | 50 | 39.9 | 27 | 21.8 | 15.37 | 0.0749 | 0.14 | 13.39 | 1
December | 7 | 8PM to 9PM | 46.9 | 39 | 28.9 | 23.9 | 14.96 | 0.0754 | 0.16 | 13.32 | 1
December | 7 | 9PM to 10PM | 46 | 38.5 | 28.9 | 23.9 | 14.74 | 0.0755 | 0.16 | 13.29 | 1
December | 7 | 10PM to 11PM | 44.1 | 37.9 | 30 | 25.1 | 14.46 | 0.0758 | 0.16 | 13.24 | 1
December | 7 | 11PM to 12AM | 43 | 37.3 | 30 | 25.1 | 14.19 | 0.0759 | 0.16 | 13.22 | 1
December | 8 | 12AM to 1AM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
December | 8 | 1AM to 2AM | 42.1 | 36.8 | 30 | 25.1 | 13.98 | 0.0761 | 0.16 | 13.19 | 1
December | 8 | 2AM to 3AM | 43 | 36.9 | 28.9 | 23.9 | 14.01 | 0.0759 | 0.16 | 13.21 | 1
December | 8 | 3AM to 4AM | 43 | 36.9 | 28.9 | 23.9 | 14.01 | 0.0759 | 0.16 | 13.21 | 1
December | 8 | 4AM to 5AM | 41 | 35.8 | 28.9 | 23.9 | 13.53 | 0.0762 | 0.16 | 13.16 | 1
December | 8 | 5AM to 6AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
December | 8 | 6AM to 7AM | 41 | 35.8 | 28.9 | 23.9 | 13.53 | 0.0762 | 0.16 | 13.16 | 1
December | 8 | 7AM to 8AM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
December | 8 | 8AM to 9AM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
December | 8 | 9AM to 10AM | 46.9 | 38.7 | 28 | 22.9 | 14.81 | 0.0754 | 0.15 | 13.31 | 1
December | 8 | 10AM to 11AM | 50 | 40.6 | 28.9 | 23.9 | 15.7 | 0.0749 | 0.16 | 13.4 | 1
December | 8 | 11AM to 12PM | 53.1 | 41.5 | 27 | 21.8 | 16.11 | 0.0745 | 0.14 | 13.47 | 1
December | 8 | 12PM to 1PM | 53.1 | 41.2 | 26.1 | 20.9 | 15.97 | 0.0745 | 0.14 | 13.47 | 1
December | 8 | 1PM to 2PM | 55 | 41.6 | 24.1 | 19 | 16.16 | 0.0742 | 0.12 | 13.51 | 1
December | 8 | 2PM to 3PM | 55 | 41.3 | 23 | 18.1 | 16.01 | 0.0742 | 0.12 | 13.51 | 1
December | 8 | 3PM to 4PM | 55 | 41.3 | 23 | 18.1 | 16.01 | 0.0742 | 0.12 | 13.51 | 1
December | 8 | 4PM to 5PM | 52 | 40 | 24.1 | 19 | 15.42 | 0.0746 | 0.12 | 13.43 | 1
December | 8 | 5PM to 6PM | 46.9 | 36.7 | 21.9 | 17.1 | 13.92 | 0.0754 | 0.11 | 13.3 | 1
December | 8 | 6PM to 7PM | 45 | 35.1 | 19.9 | 15.6 | 13.2 | 0.0757 | 0.1 | 13.24 | 1
December | 8 | 7PM to 8PM | 43 | 33.9 | 19.9 | 15.6 | 12.72 | 0.076 | 0.1 | 13.19 | 1
December | 8 | 8PM to 9PM | 42.1 | 33.4 | 19.9 | 15.6 | 12.51 | 0.0761 | 0.1 | 13.16 | 1
December | 8 | 9PM to 10PM | 39.9 | 31.6 | 19.9 | 15.6 | 11.99 | 0.0765 | 0.1 | 13.11 | 1
December | 8 | 10PM to 11PM | 37.9 | 30.6 | 19.9 | 15.6 | 11.51 | 0.0768 | 0.1 | 13.05 | 1
December | 8 | 11PM to 12AM | 36 | 29.5 | 19.9 | 15.6 | 11.03 | 0.0771 | 0.1 | 13 | 1
December | 9 | 12AM to 1AM | 35.1 | 29 | 19.9 | 15.6 | 10.82 | 0.0772 | 0.1 | 12.98 | 1
December | 9 | 1AM to 2AM | 34 | 28.4 | 19.9 | 15.6 | 10.56 | 0.0774 | 0.1 | 12.95 | 1
December | 9 | 2AM to 3AM | 33.1 | 27.9 | 19.9 | 15.6 | 10.34 | 0.0775 | 0.1 | 12.93 | 1
December | 9 | 3AM to 4AM | 33.1 | 27.9 | 19.9 | 15.6 | 10.34 | 0.0775 | 0.1 | 12.93 | 1
December | 9 | 4AM to 5AM | 33.1 | 28.2 | 21 | 16.4 | 10.47 | 0.0775 | 0.11 | 12.93 | 1
December | 9 | 5AM to 6AM | 36 | 29.8 | 21 | 16.4 | 11.16 | 0.0771 | 0.11 | 13.01 | 1
December | 9 | 6AM to 7AM | 36 | 29.5 | 19.9 | 15.6 | 11.03 | 0.0771 | 0.1 | 13 | 1
December | 9 | 7AM to 8AM | 35.1 | 29 | 19.9 | 15.6 | 10.82 | 0.0772 | 0.1 | 12.98 | 1
December | 9 | 8AM to 9AM | 37.9 | 30.3 | 19 | 14.9 | 11.41 | 0.0768 | 0.1 | 13.05 | 1
December | 9 | 9AM to 10AM | 42.1 | 33.2 | 19 | 14.9 | 12.41 | 0.0761 | 0.1 | 13.16 | 1
December | 9 | 10AM to 11AM | 45 | 34.8 | 19 | 14.9 | 13.1 | 0.0757 | 0.1 | 13.24 | 1
December | 9 | 11AM to 12PM | 48.9 | 37 | 19 | 14.9 | 14.05 | 0.0751 | 0.1 | 13.34 | 1
December | 9 | 12PM to 1PM | 51.1 | 37.9 | 18 | 14.2 | 14.46 | 0.0748 | 0.09 | 13.39 | 1
December | 9 | 1PM to 2PM | 54 | 39.9 | 19.9 | 15.6 | 15.37 | 0.0744 | 0.1 | 13.47 | 1
December | 9 | 2PM to 3PM | 55.9 | 41.7 | 23 | 18.1 | 16.23 | 0.0741 | 0.12 | 13.53 | 1
December | 9 | 3PM to 4PM | 57.9 | 43 | 24.1 | 19 | 16.86 | 0.0738 | 0.12 | 13.59 | 1
December | 9 | 4PM to 5PM | 55 | 41.8 | 25 | 19.8 | 16.29 | 0.0742 | 0.13 | 13.52 | 1
December | 9 | 5PM to 6PM | 53.1 | 41.2 | 26.1 | 20.9 | 15.97 | 0.0745 | 0.14 | 13.47 | 1
December | 9 | 6PM to 7PM | 51.1 | 40.4 | 27 | 21.8 | 15.63 | 0.0748 | 0.14 | 13.42 | 1
December | 9 | 7PM to 8PM | 50 | 39.9 | 27 | 21.8 | 15.37 | 0.0749 | 0.14 | 13.39 | 1
December | 9 | 8PM to 9PM | 46.9 | 38.3 | 27 | 21.8 | 14.63 | 0.0754 | 0.14 | 13.31 | 1
December | 9 | 9PM to 10PM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
December | 9 | 10PM to 11PM | 44.1 | 36.7 | 27 | 21.8 | 13.94 | 0.0758 | 0.14 | 13.23 | 1
December | 9 | 11PM to 12AM | 43 | 36.1 | 27 | 21.8 | 13.68 | 0.076 | 0.14 | 13.21 | 1
December | 10 | 12AM to 1AM | 42.1 | 35.7 | 27 | 21.8 | 13.46 | 0.0761 | 0.14 | 13.18 | 1
December | 10 | 1AM to 2AM | 39.9 | 34.4 | 27 | 21.8 | 12.94 | 0.0764 | 0.14 | 13.13 | 1
December | 10 | 2AM to 3AM | 39 | 33.9 | 27 | 21.8 | 12.72 | 0.0766 | 0.14 | 13.1 | 1
December | 10 | 3AM to 4AM | 37.9 | 33.3 | 27 | 21.8 | 12.46 | 0.0767 | 0.14 | 13.07 | 1
December | 10 | 4AM to 5AM | 36 | 31.9 | 27 | 21.8 | 11.98 | 0.077 | 0.14 | 13.02 | 1
December | 10 | 5AM to 6AM | 37 | 32.8 | 27 | 21.8 | 12.25 | 0.0769 | 0.14 | 13.05 | 1
December | 10 | 6AM to 7AM | 36 | 31.9 | 27 | 21.8 | 11.98 | 0.077 | 0.14 | 13.02 | 1
December | 10 | 7AM to 8AM | 35.1 | 31.4 | 27 | 21.8 | 11.77 | 0.0772 | 0.14 | 13 | 1
December | 10 | 8AM to 9AM | 46 | 37.5 | 26.1 | 20.9 | 14.28 | 0.0755 | 0.14 | 13.28 | 1
December | 10 | 9AM to 10AM | 52 | 41.3 | 28 | 22.9 | 16.03 | 0.0746 | 0.15 | 13.45 | 1
December | 10 | 10AM to 11AM | 54 | 42.6 | 28.9 | 23.9 | 16.66 | 0.0743 | 0.16 | 13.5 | 1
December | 10 | 11AM to 12PM | 55.9 | 43.9 | 30 | 25.1 | 17.33 | 0.074 | 0.16 | 13.56 | 1
December | 10 | 12PM to 1PM | 60.1 | 45.5 | 28.9 | 23.9 | 18.13 | 0.0734 | 0.16 | 13.66 | 1
December | 10 | 1PM to 2PM | 62.1 | 45.8 | 27 | 21.8 | 18.28 | 0.0732 | 0.14 | 13.71 | 1
December | 10 | 2PM to 3PM | 64.9 | 47.2 | 27 | 21.8 | 18.98 | 0.0728 | 0.14 | 13.78 | 1
December | 10 | 3PM to 4PM | 66 | 48.6 | 30 | 25.1 | 19.76 | 0.0726 | 0.16 | 13.82 | 1
December | 10 | 4PM to 5PM | 63 | 47.2 | 30 | 25.1 | 19.02 | 0.073 | 0.16 | 13.74 | 1
December | 10 | 5PM to 6PM | 62.1 | 46.4 | 28.9 | 23.9 | 18.61 | 0.0732 | 0.16 | 13.71 | 1
December | 10 | 6PM to 7PM | 59 | 45 | 28.9 | 23.9 | 17.87 | 0.0736 | 0.16 | 13.63 | 1
December | 10 | 7PM to 8PM | 55.9 | 43.9 | 30 | 25.1 | 17.33 | 0.074 | 0.16 | 13.56 | 1
December | 10 | 8PM to 9PM | 54 | 43.3 | 30.9 | 26.2 | 17.01 | 0.0743 | 0.17 | 13.51 | 1
December | 10 | 9PM to 10PM | 51.1 | 42.7 | 33.1 | 28.8 | 16.71 | 0.0747 | 0.19 | 13.44 | 1
December | 10 | 10PM to 11PM | 48.9 | 42.7 | 36 | 32.3 | 16.74 | 0.075 | 0.21 | 13.39 | 1
December | 10 | 11PM to 12AM | 48.9 | 45.4 | 42.1 | 41.1 | 18.1 | 0.075 | 0.27 | 13.42 | 1
December | 11 | 12AM to 1AM | 46.9 | 43.4 | 39.9 | 37.8 | 17.11 | 0.0753 | 0.25 | 13.36 | 1
December | 11 | 1AM to 2AM | 46 | 44 | 42.1 | 41.1 | 17.4 | 0.0754 | 0.27 | 13.34 | 1
December | 11 | 2AM to 3AM | 46 | 44.5 | 43 | 42.5 | 17.63 | 0.0754 | 0.28 | 13.35 | 1
December | 11 | 3AM to 4AM | 45 | 43.5 | 42.1 | 41.1 | 17.14 | 0.0755 | 0.27 | 13.32 | 1
December | 11 | 4AM to 5AM | 44.1 | 42.5 | 41 | 39.4 | 16.66 | 0.0757 | 0.26 | 13.29 | 1
December | 11 | 5AM to 6AM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
December | 11 | 6AM to 7AM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
December | 11 | 7AM to 8AM | 43 | 42 | 41 | 39.4 | 16.4 | 0.0758 | 0.26 | 13.26 | 1
December | 11 | 8AM to 9AM | 46 | 45 | 44.1 | 44.4 | 17.91 | 0.0754 | 0.29 | 13.35 | 1
December | 11 | 9AM to 10AM | 53.1 | 49.2 | 46 | 47.9 | 20.16 | 0.0743 | 0.31 | 13.55 | 1
December | 11 | 10AM to 11AM | 59 | 53.8 | 50 | 55.6 | 22.81 | 0.0734 | 0.36 | 13.73 | 1
December | 11 | 11AM to 12PM | 64 | 57.4 | 53.1 | 62.4 | 25.09 | 0.0727 | 0.41 | 13.89 | 1
December | 11 | 12PM to 1PM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
December | 11 | 1PM to 2PM | 70 | 60.6 | 55 | 67.2 | 27.28 | 0.0718 | 0.44 | 14.06 | 1
December | 11 | 2PM to 3PM | 70 | 58 | 50 | 55.6 | 25.48 | 0.0719 | 0.36 | 14.02 | 1
December | 11 | 3PM to 4PM | 70 | 60.6 | 55 | 67.2 | 27.28 | 0.0718 | 0.44 | 14.06 | 1
December | 11 | 4PM to 5PM | 69.1 | 60.3 | 55 | 67.2 | 27.06 | 0.0719 | 0.44 | 14.03 | 1
December | 11 | 5PM to 6PM | 66 | 59.2 | 55 | 67.2 | 26.31 | 0.0724 | 0.44 | 13.95 | 1
December | 11 | 6PM to 7PM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
December | 11 | 7PM to 8PM | 63 | 58.1 | 55 | 67.2 | 25.56 | 0.0728 | 0.44 | 13.87 | 1
December | 11 | 8PM to 9PM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
December | 11 | 9PM to 10PM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
December | 11 | 10PM to 11PM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
December | 11 | 11PM to 12AM | 60.1 | 57 | 55 | 67.2 | 24.86 | 0.0732 | 0.44 | 13.8 | 1
December | 12 | 12AM to 1AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
December | 12 | 1AM to 2AM | 57.9 | 56.2 | 55 | 67.2 | 24.33 | 0.0735 | 0.44 | 13.74 | 1
December | 12 | 2AM to 3AM | 57 | 55.8 | 55 | 67.2 | 24.11 | 0.0736 | 0.44 | 13.71 | 1
December | 12 | 3AM to 4AM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
December | 12 | 4AM to 5AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
December | 12 | 5AM to 6AM | 55 | 55 | 55 | 67.2 | 23.63 | 0.0739 | 0.44 | 13.66 | 1
December | 12 | 6AM to 7AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
December | 12 | 7AM to 8AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
December | 12 | 8AM to 9AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
December | 12 | 9AM to 10AM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
December | 12 | 10AM to 11AM | 64.9 | 59.9 | 57 | 72.3 | 26.84 | 0.0725 | 0.47 | 13.94 | 1
December | 12 | 11AM to 12PM | 69.1 | 61.4 | 57 | 72.3 | 27.85 | 0.0719 | 0.47 | 14.05 | 1
December | 12 | 12PM to 1PM | 70 | 61.7 | 57 | 72.3 | 28.07 | 0.0718 | 0.47 | 14.07 | 1
December | 12 | 1PM to 2PM | 73 | 62.7 | 57 | 72.3 | 28.82 | 0.0714 | 0.47 | 14.16 | 1
December | 12 | 2PM to 3PM | 73 | 61.1 | 54 | 64.5 | 27.61 | 0.0714 | 0.42 | 14.13 | 1
December | 12 | 3PM to 4PM | 72 | 60.7 | 54 | 64.5 | 27.35 | 0.0716 | 0.42 | 14.1 | 1
December | 12 | 4PM to 5PM | 71.1 | 61 | 55 | 67.2 | 27.54 | 0.0717 | 0.44 | 14.09 | 1
December | 12 | 5PM to 6PM | 68 | 59.9 | 55 | 67.2 | 26.79 | 0.0721 | 0.44 | 14.01 | 1
December | 12 | 6PM to 7PM | 66.9 | 59.5 | 55 | 67.2 | 26.53 | 0.0722 | 0.44 | 13.98 | 1
December | 12 | 7PM to 8PM | 66.9 | 58.9 | 54 | 64.5 | 26.12 | 0.0722 | 0.42 | 13.97 | 1
December | 12 | 8PM to 9PM | 64.9 | 58.2 | 54 | 64.5 | 25.64 | 0.0725 | 0.42 | 13.92 | 1
December | 12 | 9PM to 10PM | 64.9 | 58.2 | 54 | 64.5 | 25.64 | 0.0725 | 0.42 | 13.92 | 1
December | 12 | 10PM to 11PM | 64.9 | 58.8 | 55 | 67.2 | 26.05 | 0.0725 | 0.44 | 13.93 | 1
December | 12 | 11PM to 12AM | 64 | 58.5 | 55 | 67.2 | 25.83 | 0.0726 | 0.44 | 13.9 | 1
December | 13 | 12AM to 1AM | 62.1 | 57.7 | 55 | 67.2 | 25.34 | 0.0729 | 0.44 | 13.85 | 1
December | 13 | 1AM to 2AM | 61 | 57.3 | 55 | 67.2 | 25.08 | 0.0731 | 0.44 | 13.82 | 1
December | 13 | 2AM to 3AM | 62.1 | 58.3 | 55.9 | 69.4 | 25.7 | 0.0729 | 0.45 | 13.86 | 1
December | 13 | 3AM to 4AM | 63 | 59.2 | 57 | 72.3 | 26.35 | 0.0727 | 0.47 | 13.89 | 1
December | 13 | 4AM to 5AM | 63 | 59.8 | 57.9 | 74.7 | 26.73 | 0.0727 | 0.48 | 13.9 | 1
December | 13 | 5AM to 6AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
December | 13 | 6AM to 7AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
December | 13 | 7AM to 8AM | 62.1 | 60.1 | 59 | 77.7 | 26.98 | 0.0728 | 0.5 | 13.88 | 1
December | 13 | 8AM to 9AM | 63 | 61.1 | 60.1 | 80.8 | 27.68 | 0.0727 | 0.52 | 13.92 | 1
December | 13 | 9AM to 10AM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
December | 13 | 10AM to 11AM | 66.9 | 63.7 | 62.1 | 86.8 | 29.59 | 0.0721 | 0.56 | 14.04 | 1
December | 13 | 11AM to 12PM | 68 | 63.4 | 61 | 83.5 | 29.33 | 0.072 | 0.54 | 14.06 | 1
December | 13 | 12PM to 1PM | 69.1 | 63.2 | 60.1 | 80.8 | 29.18 | 0.0719 | 0.52 | 14.08 | 1
December | 13 | 1PM to 2PM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
December | 13 | 2PM to 3PM | 64.9 | 62.3 | 61 | 83.5 | 28.58 | 0.0724 | 0.54 | 13.98 | 1
December | 13 | 3PM to 4PM | 63 | 62.4 | 62.1 | 86.8 | 28.61 | 0.0727 | 0.56 | 13.93 | 1
December | 13 | 4PM to 5PM | 62.1 | 62.1 | 62.1 | 86.8 | 28.39 | 0.0728 | 0.56 | 13.91 | 1
December | 13 | 5PM to 6PM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
December | 13 | 6PM to 7PM | 61 | 61 | 61 | 83.5 | 27.61 | 0.073 | 0.54 | 13.87 | 1
December | 13 | 7PM to 8PM | 61 | 60.4 | 60.1 | 80.8 | 27.2 | 0.073 | 0.52 | 13.86 | 1
December | 13 | 8PM to 9PM | 57 | 56.4 | 55.9 | 69.4 | 24.46 | 0.0736 | 0.45 | 13.72 | 1
December | 13 | 9PM to 10PM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
December | 13 | 10PM to 11PM | 55 | 54.4 | 54 | 64.5 | 23.22 | 0.0739 | 0.42 | 13.65 | 1
December | 13 | 11PM to 12AM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
December | 14 | 12AM to 1AM | 52 | 50.3 | 48.9 | 53.4 | 20.75 | 0.0744 | 0.35 | 13.54 | 1
December | 14 | 1AM to 2AM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
December | 14 | 2AM to 3AM | 46.9 | 45.9 | 45 | 45.9 | 18.37 | 0.0752 | 0.3 | 13.38 | 1
December | 14 | 3AM to 4AM | 46 | 45 | 44.1 | 44.4 | 17.91 | 0.0754 | 0.29 | 13.35 | 1
December | 14 | 4AM to 5AM | 45 | 43.9 | 43 | 42.5 | 17.36 | 0.0755 | 0.28 | 13.32 | 1
December | 14 | 5AM to 6AM | 44.1 | 41.6 | 39 | 36.4 | 16.2 | 0.0757 | 0.24 | 13.28 | 1
December | 14 | 6AM to 7AM | 43 | 40.6 | 37.9 | 34.9 | 15.71 | 0.0759 | 0.23 | 13.25 | 1
December | 14 | 7AM to 8AM | 42.1 | 40.1 | 37.9 | 34.9 | 15.49 | 0.076 | 0.23 | 13.22 | 1
December | 14 | 8AM to 9AM | 43 | 40.6 | 37.9 | 34.9 | 15.71 | 0.0759 | 0.23 | 13.25 | 1
December | 14 | 9AM to 10AM | 44.1 | 41.1 | 37.9 | 34.9 | 15.97 | 0.0757 | 0.23 | 13.27 | 1
December | 14 | 10AM to 11AM | 51.1 | 45 | 39 | 36.4 | 17.91 | 0.0747 | 0.24 | 13.46 | 1
December | 14 | 11AM to 12PM | 54 | 46.8 | 39.9 | 37.8 | 18.81 | 0.0742 | 0.25 | 13.54 | 1
December | 14 | 12PM to 1PM | 57 | 49.5 | 43 | 42.5 | 20.29 | 0.0738 | 0.28 | 13.64 | 1
December | 14 | 1PM to 2PM | 57.9 | 49.9 | 43 | 42.5 | 20.51 | 0.0736 | 0.28 | 13.66 | 1
December | 14 | 2PM to 3PM | 59 | 50.8 | 44.1 | 44.4 | 21.05 | 0.0735 | 0.29 | 13.7 | 1
December | 14 | 3PM to 4PM | 59 | 51.2 | 45 | 45.9 | 21.3 | 0.0735 | 0.3 | 13.7 | 1
December | 14 | 4PM to 5PM | 57 | 50.4 | 45 | 45.9 | 20.82 | 0.0737 | 0.3 | 13.65 | 1
December | 14 | 5PM to 6PM | 57 | 50.4 | 45 | 45.9 | 20.82 | 0.0737 | 0.3 | 13.65 | 1
December | 14 | 6PM to 7PM | 51.1 | 46.4 | 42.1 | 41.1 | 18.62 | 0.0746 | 0.27 | 13.48 | 1
December | 14 | 7PM to 8PM | 48 | 44 | 39.9 | 37.8 | 17.37 | 0.0751 | 0.25 | 13.39 | 1
December | 14 | 8PM to 9PM | 45 | 42.1 | 39 | 36.4 | 16.42 | 0.0756 | 0.24 | 13.3 | 1
December | 14 | 9PM to 10PM | 50 | 42.5 | 34 | 29.8 | 16.62 | 0.0749 | 0.2 | 13.41 | 1
December | 14 | 10PM to 11PM | 48.9 | 41.6 | 33.1 | 28.8 | 16.19 | 0.075 | 0.19 | 13.38 | 1
December | 14 | 11PM to 12AM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
December | 15 | 12AM to 1AM | 44.1 | 38.2 | 30.9 | 26.2 | 14.62 | 0.0758 | 0.17 | 13.25 | 1
December | 15 | 1AM to 2AM | 44.1 | 38.2 | 30.9 | 26.2 | 14.62 | 0.0758 | 0.17 | 13.25 | 1
December | 15 | 2AM to 3AM | 41 | 35.8 | 28.9 | 23.9 | 13.53 | 0.0762 | 0.16 | 13.16 | 1
December | 15 | 3AM to 4AM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
December | 15 | 4AM to 5AM | 39.9 | 34.9 | 28 | 22.9 | 13.11 | 0.0764 | 0.15 | 13.13 | 1
December | 15 | 5AM to 6AM | 39 | 33.9 | 27 | 21.8 | 12.72 | 0.0766 | 0.14 | 13.1 | 1
December | 15 | 6AM to 7AM | 37.9 | 33.3 | 27 | 21.8 | 12.46 | 0.0767 | 0.14 | 13.07 | 1
December | 15 | 7AM to 8AM | 37 | 33.2 | 28 | 22.9 | 12.42 | 0.0769 | 0.15 | 13.05 | 1
December | 15 | 8AM to 9AM | 37.9 | 34.5 | 30 | 25.1 | 12.98 | 0.0767 | 0.16 | 13.08 | 1
December | 15 | 9AM to 10AM | 43 | 37.7 | 30.9 | 26.2 | 14.36 | 0.0759 | 0.17 | 13.22 | 1
December | 15 | 10AM to 11AM | 46.9 | 39.4 | 30 | 25.1 | 15.15 | 0.0753 | 0.16 | 13.32 | 1
December | 15 | 11AM to 12PM | 48.9 | 40 | 28.9 | 23.9 | 15.44 | 0.0751 | 0.16 | 13.37 | 1
December | 15 | 12PM to 1PM | 50 | 40.6 | 28.9 | 23.9 | 15.7 | 0.0749 | 0.16 | 13.4 | 1
December | 15 | 1PM to 2PM | 51.1 | 40.2 | 26.1 | 20.9 | 15.49 | 0.0748 | 0.14 | 13.42 | 1
December | 15 | 2PM to 3PM | 50 | 39.2 | 25 | 19.8 | 15.07 | 0.0749 | 0.13 | 13.38 | 1
December | 15 | 3PM to 4PM | 48.9 | 39 | 26.1 | 20.9 | 14.97 | 0.0751 | 0.14 | 13.36 | 1
December | 15 | 4PM to 5PM | 50 | 39.6 | 26.1 | 20.9 | 15.23 | 0.0749 | 0.14 | 13.39 | 1
December | 15 | 5PM to 6PM | 48 | 38.6 | 26.1 | 20.9 | 14.76 | 0.0752 | 0.14 | 13.34 | 1
December | 15 | 6PM to 7PM | 46 | 37.8 | 27 | 21.8 | 14.42 | 0.0755 | 0.14 | 13.29 | 1
December | 15 | 7PM to 8PM | 45 | 37.2 | 27 | 21.8 | 14.16 | 0.0757 | 0.14 | 13.26 | 1
December | 15 | 8PM to 9PM | 45 | 38.4 | 30 | 25.1 | 14.67 | 0.0756 | 0.16 | 13.27 | 1
December | 15 | 9PM to 10PM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
December | 15 | 10PM to 11PM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 15 | 11PM to 12AM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 16 | 12AM to 1AM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 16 | 1AM to 2AM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 16 | 2AM to 3AM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 16 | 3AM to 4AM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 16 | 4AM to 5AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
December | 16 | 5AM to 6AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
December | 16 | 6AM to 7AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
December | 16 | 7AM to 8AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
December | 16 | 8AM to 9AM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 16 | 9AM to 10AM | 43 | 40.6 | 37.9 | 34.9 | 15.71 | 0.0759 | 0.23 | 13.25 | 1
December | 16 | 10AM to 11AM | 46 | 42.6 | 39 | 36.4 | 16.68 | 0.0754 | 0.24 | 13.33 | 1
December | 16 | 11AM to 12PM | 51.1 | 45.4 | 39.9 | 37.8 | 18.11 | 0.0747 | 0.25 | 13.47 | 1
December | 16 | 12PM to 1PM | 53.1 | 46.8 | 41 | 39.4 | 18.84 | 0.0744 | 0.26 | 13.52 | 1
December | 16 | 1PM to 2PM | 57.9 | 50.4 | 44.1 | 44.4 | 20.79 | 0.0736 | 0.29 | 13.67 | 1
December | 16 | 2PM to 3PM | 57.9 | 50.8 | 45 | 45.9 | 21.04 | 0.0736 | 0.3 | 13.67 | 1
December | 16 | 3PM to 4PM | 55.9 | 50.5 | 46 | 47.9 | 20.86 | 0.0739 | 0.31 | 13.63 | 1
December | 16 | 4PM to 5PM | 52 | 48.2 | 45 | 45.9 | 19.59 | 0.0745 | 0.3 | 13.52 | 1
December | 16 | 5PM to 6PM | 51.1 | 47.8 | 45 | 45.9 | 19.37 | 0.0746 | 0.3 | 13.49 | 1
December | 16 | 6PM to 7PM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
December | 16 | 7PM to 8PM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
December | 16 | 8PM to 9PM | 46 | 45 | 44.1 | 44.4 | 17.91 | 0.0754 | 0.29 | 13.35 | 1
December | 16 | 9PM to 10PM | 45 | 44.5 | 44.1 | 44.4 | 17.65 | 0.0755 | 0.29 | 13.33 | 1
December | 16 | 10PM to 11PM | 45 | 43 | 41 | 39.4 | 16.88 | 0.0756 | 0.26 | 13.31 | 1
December | 16 | 11PM to 12AM | 44.1 | 41.1 | 37.9 | 34.9 | 15.97 | 0.0757 | 0.23 | 13.27 | 1
December | 17 | 12AM to 1AM | 41 | 37.8 | 34 | 29.8 | 14.44 | 0.0762 | 0.2 | 13.18 | 1
December | 17 | 1AM to 2AM | 39 | 36 | 32 | 27.5 | 13.61 | 0.0765 | 0.18 | 13.12 | 1
December | 17 | 2AM to 3AM | 35.1 | 32.1 | 28 | 22.9 | 11.94 | 0.0772 | 0.15 | 13 | 1
December | 17 | 3AM to 4AM | 33.1 | 30 | 26.1 | 20.9 | 11.15 | 0.0775 | 0.14 | 12.94 | 1
December | 17 | 4AM to 5AM | 32 | 29 | 25 | 19.8 | 10.73 | 0.0777 | 0.13 | 12.91 | 1
December | 17 | 5AM to 6AM | 30 | 26.5 | 21 | 16.4 | 9.73 | 0.078 | 0.11 | 12.85 | 1
December | 17 | 6AM to 7AM | 28.9 | 25.2 | 19 | 14.9 | 9.24 | 0.0782 | 0.1 | 12.82 | 1
December | 17 | 7AM to 8AM | 28 | 24.3 | 18 | 14.2 | 8.91 | 0.0783 | 0.09 | 12.79 | 1
December | 17 | 8AM to 9AM | 28.9 | 24.6 | 17.1 | 13.6 | 9.03 | 0.0782 | 0.09 | 12.81 | 1
December | 17 | 9AM to 10AM | 30.9 | 25.5 | 16 | 12.9 | 9.4 | 0.0779 | 0.08 | 12.86 | 1
December | 17 | 10AM to 11AM | 34 | 27.3 | 16 | 12.9 | 10.14 | 0.0774 | 0.08 | 12.94 | 1
December | 17 | 11AM to 12PM | 35.1 | 27.9 | 16 | 12.9 | 10.4 | 0.0772 | 0.08 | 12.97 | 1
December | 17 | 12PM to 1PM | 37.9 | 29.5 | 16 | 12.9 | 11.09 | 0.0768 | 0.08 | 13.05 | 1
December | 17 | 1PM to 2PM | 39 | 29.9 | 15.1 | 12.3 | 11.26 | 0.0766 | 0.08 | 13.07 | 1
December | 17 | 2PM to 3PM | 39.9 | 29.9 | 12.9 | 11.1 | 11.29 | 0.0765 | 0.07 | 13.09 | 1
December | 17 | 3PM to 4PM | 39.9 | 29.7 | 12 | 10.6 | 11.21 | 0.0765 | 0.07 | 13.09 | 1
December | 17 | 4PM to 5PM | 37.9 | 28.3 | 10.9 | 10 | 10.65 | 0.0768 | 0.07 | 13.04 | 1
December | 17 | 5PM to 6PM | 34 | 26.1 | 10.9 | 10 | 9.7 | 0.0774 | 0.07 | 12.93 | 1
December | 17 | 6PM to 7PM | 32 | 24.7 | 10 | 9.6 | 9.15 | 0.0777 | 0.06 | 12.88 | 1
December | 17 | 7PM to 8PM | 30 | 23.5 | 10 | 9.6 | 8.68 | 0.0781 | 0.06 | 12.83 | 1
December | 17 | 8PM to 9PM | 30 | 23.5 | 10 | 9.6 | 8.68 | 0.0781 | 0.06 | 12.83 | 1
December | 17 | 9PM to 10PM | 28.9 | 22.9 | 10 | 9.6 | 8.42 | 0.0782 | 0.06 | 12.8 | 1
December | 17 | 10PM to 11PM | 28.9 | 22.9 | 10 | 9.6 | 8.42 | 0.0782 | 0.06 | 12.8 | 1
December | 17 | 11PM to 12AM | 28 | 22.5 | 10.9 | 10 | 8.27 | 0.0784 | 0.07 | 12.78 | 1
December | 18 | 12AM to 1AM | 26.1 | 21.1 | 10 | 9.6 | 7.73 | 0.0787 | 0.06 | 12.73 | 1
December | 18 | 1AM to 2AM | 25 | 20.4 | 10 | 9.6 | 7.47 | 0.0789 | 0.06 | 12.7 | 1
December | 18 | 2AM to 3AM | 25 | 20.4 | 10 | 9.6 | 7.47 | 0.0789 | 0.06 | 12.7 | 1
December | 18 | 3AM to 4AM | 25 | 20.4 | 10 | 9.6 | 7.47 | 0.0789 | 0.06 | 12.7 | 1
December | 18 | 4AM to 5AM | 23 | 19.3 | 10.9 | 10 | 7.06 | 0.0792 | 0.07 | 12.65 | 1
December | 18 | 5AM to 6AM | 23 | 19.6 | 12 | 10.6 | 7.14 | 0.0792 | 0.07 | 12.65 | 1
December | 18 | 6AM to 7AM | 23 | 19.3 | 10.9 | 10 | 7.06 | 0.0792 | 0.07 | 12.65 | 1
December | 18 | 7AM to 8AM | 21.9 | 18.6 | 10.9 | 10 | 6.8 | 0.0794 | 0.07 | 12.62 | 1
December | 18 | 8AM to 9AM | 28 | 23 | 12.9 | 11.1 | 8.43 | 0.0784 | 0.07 | 12.78 | 1
December | 18 | 9AM to 10AM | 33.1 | 26.3 | 14 | 11.7 | 9.74 | 0.0776 | 0.08 | 12.92 | 1
December | 18 | 10AM to 11AM | 37.9 | 29.3 | 15.1 | 12.3 | 11 | 0.0768 | 0.08 | 13.04 | 1
December | 18 | 11AM to 12PM | 39.9 | 29.9 | 12.9 | 11.1 | 11.29 | 0.0765 | 0.07 | 13.09 | 1
December | 18 | 12PM to 1PM | 44.1 | 32.9 | 12.9 | 11.1 | 12.29 | 0.0759 | 0.07 | 13.2 | 1
December | 18 | 1PM to 2PM | 46 | 33.9 | 12 | 10.6 | 12.69 | 0.0756 | 0.07 | 13.25 | 1
December | 18 | 2PM to 3PM | 50 | 36.1 | 12 | 10.6 | 13.64 | 0.075 | 0.07 | 13.36 | 1
December | 18 | 3PM to 4PM | 50 | 36.1 | 12 | 10.6 | 13.64 | 0.075 | 0.07 | 13.36 | 1
December | 18 | 4PM to 5PM | 50 | 35.9 | 10.9 | 10 | 13.55 | 0.075 | 0.07 | 13.35 | 1
December | 18 | 5PM to 6PM | 46 | 33.5 | 10 | 9.6 | 12.53 | 0.0756 | 0.06 | 13.25 | 1
December | 18 | 6PM to 7PM | 44.1 | 32.9 | 12.9 | 11.1 | 12.29 | 0.0759 | 0.07 | 13.2 | 1
December | 18 | 7PM to 8PM | 42.1 | 31 | 12.9 | 11.1 | 11.81 | 0.0762 | 0.07 | 13.15 | 1
December | 18 | 8PM to 9PM | 39.9 | 30.1 | 14 | 11.7 | 11.38 | 0.0765 | 0.08 | 13.09 | 1
December | 18 | 9PM to 10PM | 37.9 | 29.3 | 15.1 | 12.3 | 11 | 0.0768 | 0.08 | 13.04 | 1
December | 18 | 10PM to 11PM | 36 | 28.4 | 16 | 12.9 | 10.61 | 0.0771 | 0.08 | 12.99 | 1
December | 18 | 11PM to 12AM | 36 | 28.4 | 16 | 12.9 | 10.61 | 0.0771 | 0.08 | 12.99 | 1
December | 19 | 12AM to 1AM | 35.1 | 27.9 | 16 | 12.9 | 10.4 | 0.0772 | 0.08 | 12.97 | 1
December | 19 | 1AM to 2AM | 34 | 27.3 | 16 | 12.9 | 10.14 | 0.0774 | 0.08 | 12.94 | 1
December | 19 | 2AM to 3AM | 33.1 | 26.5 | 15.1 | 12.3 | 9.83 | 0.0776 | 0.08 | 12.92 | 1
December | 19 | 3AM to 4AM | 32 | 26.1 | 16 | 12.9 | 9.66 | 0.0777 | 0.08 | 12.89 | 1
December | 19 | 4AM to 5AM | 32 | 26.1 | 16 | 12.9 | 9.66 | 0.0777 | 0.08 | 12.89 | 1
December | 19 | 5AM to 6AM | 32 | 26.1 | 16 | 12.9 | 9.66 | 0.0777 | 0.08 | 12.89 | 1
December | 19 | 6AM to 7AM | 32 | 26.1 | 16 | 12.9 | 9.66 | 0.0777 | 0.08 | 12.89 | 1
December | 19 | 7AM to 8AM | 30.9 | 25.5 | 16 | 12.9 | 9.4 | 0.0779 | 0.08 | 12.86 | 1
December | 19 | 8AM to 9AM | 36 | 28.7 | 17.1 | 13.6 | 10.72 | 0.0771 | 0.09 | 13 | 1
December | 19 | 9AM to 10AM | 39.9 | 30.8 | 17.1 | 13.6 | 11.67 | 0.0765 | 0.09 | 13.1 | 1
December | 19 | 10AM to 11AM | 45 | 34.8 | 19 | 14.9 | 13.1 | 0.0757 | 0.1 | 13.24 | 1
December | 19 | 11AM to 12PM | 50 | 37.3 | 18 | 14.2 | 14.2 | 0.075 | 0.09 | 13.37 | 1
December | 19 | 12PM to 1PM | 53.1 | 38.8 | 17.1 | 13.6 | 14.84 | 0.0745 | 0.09 | 13.44 | 1
December | 19 | 1PM to 2PM | 57 | 40.6 | 16 | 12.9 | 15.68 | 0.074 | 0.08 | 13.55 | 1
December | 19 | 2PM to 3PM | 57 | 40.2 | 14 | 11.7 | 15.5 | 0.074 | 0.08 | 13.54 | 1
December | 19 | 3PM to 4PM | 57.9 | 40.9 | 15.1 | 12.3 | 15.81 | 0.0738 | 0.08 | 13.57 | 1
December | 19 | 4PM to 5PM | 57 | 40.8 | 17.1 | 13.6 | 15.79 | 0.074 | 0.09 | 13.55 | 1
December | 19 | 5PM to 6PM | 54 | 39.4 | 18 | 14.2 | 15.15 | 0.0744 | 0.09 | 13.47 | 1
December | 19 | 6PM to 7PM | 48.9 | 37.8 | 21.9 | 17.1 | 14.4 | 0.0751 | 0.11 | 13.35 | 1
December | 19 | 7PM to 8PM | 46.9 | 37.3 | 24.1 | 19 | 14.21 | 0.0754 | 0.12 | 13.3 | 1
December | 19 | 8PM to 9PM | 43 | 35.5 | 25 | 19.8 | 13.38 | 0.076 | 0.13 | 13.2 | 1
December | 19 | 9PM to 10PM | 42.1 | 35 | 25 | 19.8 | 13.16 | 0.0761 | 0.13 | 13.18 | 1
December | 19 | 10PM to 11PM | 42.1 | 35 | 25 | 19.8 | 13.16 | 0.0761 | 0.13 | 13.18 | 1
December | 19 | 11PM to 12AM | 42.1 | 35.3 | 26.1 | 20.9 | 13.32 | 0.0761 | 0.14 | 13.18 | 1
December | 20 | 12AM to 1AM | 39.9 | 34.1 | 26.1 | 20.9 | 12.8 | 0.0764 | 0.14 | 13.12 | 1
December | 20 | 1AM to 2AM | 39 | 33.6 | 26.1 | 20.9 | 12.58 | 0.0766 | 0.14 | 13.1 | 1
December | 20 | 2AM to 3AM | 39 | 33.6 | 26.1 | 20.9 | 12.58 | 0.0766 | 0.14 | 13.1 | 1
December | 20 | 3AM to 4AM | 37.9 | 33 | 26.1 | 20.9 | 12.32 | 0.0767 | 0.14 | 13.07 | 1
December | 20 | 4AM to 5AM | 37 | 32.5 | 26.1 | 20.9 | 12.11 | 0.0769 | 0.14 | 13.05 | 1
December | 20 | 5AM to 6AM | 37 | 32.5 | 26.1 | 20.9 | 12.11 | 0.0769 | 0.14 | 13.05 | 1
December | 20 | 6AM to 7AM | 37 | 32.5 | 26.1 | 20.9 | 12.11 | 0.0769 | 0.14 | 13.05 | 1
December | 20 | 7AM to 8AM | 37.9 | 33 | 26.1 | 20.9 | 12.32 | 0.0767 | 0.14 | 13.07 | 1
December | 20 | 8AM to 9AM | 44.1 | 37.1 | 28 | 22.9 | 14.11 | 0.0758 | 0.15 | 13.24 | 1
December | 20 | 9AM to 10AM | 50 | 40.6 | 28.9 | 23.9 | 15.7 | 0.0749 | 0.16 | 13.4 | 1
December | 20 | 10AM to 11AM | 52 | 40.6 | 26.1 | 20.9 | 15.71 | 0.0746 | 0.14 | 13.44 | 1
December | 20 | 11AM to 12PM | 52 | 40.3 | 25 | 19.8 | 15.55 | 0.0746 | 0.13 | 13.44 | 1
December | 20 | 12PM to 1PM | 57 | 42.8 | 25 | 19.8 | 16.77 | 0.0739 | 0.13 | 13.57 | 1
December | 20 | 1PM to 2PM | 57.9 | 43 | 24.1 | 19 | 16.86 | 0.0738 | 0.12 | 13.59 | 1
December | 20 | 2PM to 3PM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
December | 20 | 3PM to 4PM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
December | 20 | 4PM to 5PM | 57 | 42.8 | 25 | 19.8 | 16.77 | 0.0739 | 0.13 | 13.57 | 1
December | 20 | 5PM to 6PM | 53.1 | 40.8 | 25 | 19.8 | 15.81 | 0.0745 | 0.13 | 13.46 | 1
December | 20 | 6PM to 7PM | 51.1 | 39.8 | 25 | 19.8 | 15.33 | 0.0748 | 0.13 | 13.41 | 1
December | 20 | 7PM to 8PM | 51.1 | 39.8 | 25 | 19.8 | 15.33 | 0.0748 | 0.13 | 13.41 | 1
December | 20 | 8PM to 9PM | 48.9 | 38.7 | 25 | 19.8 | 14.81 | 0.0751 | 0.13 | 13.36 | 1
December | 20 | 9PM to 10PM | 46.9 | 37.6 | 25 | 19.8 | 14.34 | 0.0754 | 0.13 | 13.3 | 1
December | 20 | 10PM to 11PM | 45 | 36.9 | 26.1 | 20.9 | 14.02 | 0.0757 | 0.14 | 13.25 | 1
December | 20 | 11PM to 12AM | 44.1 | 36.4 | 26.1 | 20.9 | 13.8 | 0.0758 | 0.14 | 13.23 | 1
December | 21 | 12AM to 1AM | 42.1 | 35.3 | 26.1 | 20.9 | 13.32 | 0.0761 | 0.14 | 13.18 | 1
December | 21 | 1AM to 2AM | 41 | 34.7 | 26.1 | 20.9 | 13.06 | 0.0763 | 0.14 | 13.15 | 1
December | 21 | 2AM to 3AM | 39 | 33.6 | 26.1 | 20.9 | 12.58 | 0.0766 | 0.14 | 13.1 | 1
December | 21 | 3AM to 4AM | 37 | 32.5 | 26.1 | 20.9 | 12.11 | 0.0769 | 0.14 | 13.05 | 1
December | 21 | 4AM to 5AM | 35.1 | 32.1 | 28 | 22.9 | 11.94 | 0.0772 | 0.15 | 13 | 1
December | 21 | 5AM to 6AM | 34 | 31.7 | 28.9 | 23.9 | 11.83 | 0.0773 | 0.16 | 12.98 | 1
December | 21 | 6AM to 7AM | 35.1 | 32.9 | 30 | 25.1 | 12.28 | 0.0772 | 0.16 | 13.01 | 1
December | 21 | 7AM to 8AM | 35.1 | 33.3 | 30.9 | 26.2 | 12.45 | 0.0771 | 0.17 | 13.01 | 1
December | 21 | 8AM to 9AM | 36 | 33.8 | 30.9 | 26.2 | 12.66 | 0.077 | 0.17 | 13.03 | 1
December | 21 | 9AM to 10AM | 37 | 34.9 | 32 | 27.5 | 13.13 | 0.0768 | 0.18 | 13.07 | 1
December | 21 | 10AM to 11AM | 39.9 | 36.5 | 32 | 27.5 | 13.83 | 0.0764 | 0.18 | 13.14 | 1
December | 21 | 11AM to 12PM | 41 | 37.1 | 32 | 27.5 | 14.09 | 0.0762 | 0.18 | 13.17 | 1
December | 21 | 12PM to 1PM | 42.1 | 37.6 | 32 | 27.5 | 14.35 | 0.0761 | 0.18 | 13.2 | 1
December | 21 | 1PM to 2PM | 43 | 38.5 | 33.1 | 28.8 | 14.76 | 0.0759 | 0.19 | 13.23 | 1
December | 21 | 2PM to 3PM | 44.1 | 39.5 | 34 | 29.8 | 15.18 | 0.0757 | 0.2 | 13.26 | 1
December | 21 | 3PM to 4PM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
December | 21 | 4PM to 5PM | 44.1 | 39.5 | 34 | 29.8 | 15.18 | 0.0757 | 0.2 | 13.26 | 1
December | 21 | 5PM to 6PM | 43 | 38.9 | 34 | 29.8 | 14.92 | 0.0759 | 0.2 | 13.23 | 1
December | 21 | 6PM to 7PM | 42.1 | 38.4 | 34 | 29.8 | 14.7 | 0.076 | 0.2 | 13.21 | 1
December | 21 | 7PM to 8PM | 42.1 | 38.4 | 34 | 29.8 | 14.7 | 0.076 | 0.2 | 13.21 | 1
December | 21 | 8PM to 9PM | 42.1 | 38.4 | 34 | 29.8 | 14.7 | 0.076 | 0.2 | 13.21 | 1
December | 21 | 9PM to 10PM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
December | 21 | 10PM to 11PM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
December | 21 | 11PM to 12AM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
December | 22 | 12AM to 1AM | 42.1 | 39.2 | 36 | 32.3 | 15.08 | 0.076 | 0.21 | 13.21 | 1
December | 22 | 1AM to 2AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
December | 22 | 2AM to 3AM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
December | 22 | 3AM to 4AM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
December | 22 | 4AM to 5AM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
December | 22 | 5AM to 6AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
December | 22 | 6AM to 7AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
December | 22 | 7AM to 8AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
December | 22 | 8AM to 9AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
December | 22 | 9AM to 10AM | 43 | 40.2 | 37 | 33.7 | 15.52 | 0.0759 | 0.22 | 13.24 | 1
December | 22 | 10AM to 11AM | 44.1 | 40.7 | 37 | 33.7 | 15.78 | 0.0757 | 0.22 | 13.27 | 1
December | 22 | 11AM to 12PM | 46 | 42.1 | 37.9 | 34.9 | 16.45 | 0.0754 | 0.23 | 13.33 | 1
December | 22 | 12PM to 1PM | 48 | 43.1 | 37.9 | 34.9 | 16.93 | 0.0751 | 0.23 | 13.38 | 1
December | 22 | 1PM to 2PM | 48.9 | 44.9 | 41 | 39.4 | 17.84 | 0.075 | 0.26 | 13.42 | 1
December | 22 | 2PM to 3PM | 50 | 45.4 | 41 | 39.4 | 18.1 | 0.0748 | 0.26 | 13.44 | 1
December | 22 | 3PM to 4PM | 50 | 45.4 | 41 | 39.4 | 18.1 | 0.0748 | 0.26 | 13.44 | 1
December | 22 | 4PM to 5PM | 52 | 47.2 | 43 | 42.5 | 19.07 | 0.0745 | 0.28 | 13.51 | 1
December | 22 | 5PM to 6PM | 50 | 46.9 | 44.1 | 44.4 | 18.87 | 0.0748 | 0.29 | 13.46 | 1
December | 22 | 6PM to 7PM | 50 | 47.3 | 45 | 45.9 | 19.11 | 0.0748 | 0.3 | 13.46 | 1
December | 22 | 7PM to 8PM | 48.9 | 46.8 | 45 | 45.9 | 18.85 | 0.0749 | 0.3 | 13.44 | 1
December | 22 | 8PM to 9PM | 48 | 45.9 | 44.1 | 44.4 | 18.39 | 0.0751 | 0.29 | 13.41 | 1
December | 22 | 9PM to 10PM | 46.9 | 45.4 | 44.1 | 44.4 | 18.13 | 0.0752 | 0.29 | 13.38 | 1
December | 22 | 10PM to 11PM | 46.9 | 45.4 | 44.1 | 44.4 | 18.13 | 0.0752 | 0.29 | 13.38 | 1
December | 22 | 11PM to 12AM | 46 | 45 | 44.1 | 44.4 | 17.91 | 0.0754 | 0.29 | 13.35 | 1
December | 23 | 12AM to 1AM | 46 | 45 | 44.1 | 44.4 | 17.91 | 0.0754 | 0.29 | 13.35 | 1
December | 23 | 1AM to 2AM | 46 | 45.5 | 45 | 45.9 | 18.15 | 0.0753 | 0.3 | 13.36 | 1
December | 23 | 2AM to 3AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 23 | 3AM to 4AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 23 | 4AM to 5AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 23 | 5AM to 6AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 23 | 6AM to 7AM | 46.9 | 46.9 | 46.9 | 49.6 | 18.93 | 0.0752 | 0.32 | 13.39 | 1
December | 23 | 7AM to 8AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 23 | 8AM to 9AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 23 | 9AM to 10AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 23 | 10AM to 11AM | 46.9 | 46.9 | 46.9 | 49.6 | 18.93 | 0.0752 | 0.32 | 13.39 | 1
December | 23 | 11AM to 12PM | 48.9 | 48.4 | 48 | 51.6 | 19.73 | 0.0749 | 0.34 | 13.45 | 1
December | 23 | 12PM to 1PM | 50 | 49.4 | 48.9 | 53.4 | 20.27 | 0.0747 | 0.35 | 13.49 | 1
December | 23 | 1PM to 2PM | 53.1 | 50.7 | 48.9 | 53.4 | 21.02 | 0.0743 | 0.35 | 13.57 | 1
December | 23 | 2PM to 3PM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
December | 23 | 3PM to 4PM | 54 | 50.6 | 48 | 51.6 | 20.96 | 0.0741 | 0.34 | 13.59 | 1
December | 23 | 4PM to 5PM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
December | 23 | 5PM to 6PM | 54 | 51.7 | 50 | 55.6 | 21.58 | 0.0741 | 0.36 | 13.6 | 1
December | 23 | 6PM to 7PM | 52 | 50.8 | 50 | 55.6 | 21.1 | 0.0744 | 0.36 | 13.55 | 1
December | 23 | 7PM to 8PM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
December | 23 | 8PM to 9PM | 51.1 | 50.5 | 50 | 55.6 | 20.88 | 0.0745 | 0.36 | 13.52 | 1
December | 23 | 9PM to 10PM | 52 | 50.8 | 50 | 55.6 | 21.1 | 0.0744 | 0.36 | 13.55 | 1
December | 23 | 10PM to 11PM | 52 | 50.8 | 50 | 55.6 | 21.1 | 0.0744 | 0.36 | 13.55 | 1
December | 23 | 11PM to 12AM | 52 | 50.8 | 50 | 55.6 | 21.1 | 0.0744 | 0.36 | 13.55 | 1
December | 24 | 12AM to 1AM | 52 | 51.5 | 51.1 | 58 | 21.45 | 0.0744 | 0.38 | 13.55 | 1
December | 24 | 1AM to 2AM | 53.1 | 52.4 | 52 | 59.9 | 22.03 | 0.0742 | 0.39 | 13.59 | 1
December | 24 | 2AM to 3AM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
December | 24 | 3AM to 4AM | 53.1 | 53.1 | 53.1 | 62.4 | 22.41 | 0.0742 | 0.41 | 13.6 | 1
December | 24 | 4AM to 5AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
December | 24 | 5AM to 6AM | 54 | 54 | 54 | 64.5 | 22.96 | 0.0741 | 0.42 | 13.63 | 1
December | 24 | 6AM to 7AM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
December | 24 | 7AM to 8AM | 55.9 | 55.4 | 55 | 67.2 | 23.85 | 0.0738 | 0.44 | 13.69 | 1
December | 24 | 8AM to 9AM | 59 | 57.1 | 55.9 | 69.4 | 24.95 | 0.0733 | 0.45 | 13.77 | 1
December | 24 | 9AM to 10AM | 62.1 | 58.9 | 57 | 72.3 | 26.13 | 0.0729 | 0.47 | 13.86 | 1
December | 24 | 10AM to 11AM | 59 | 58.3 | 57.9 | 74.7 | 25.76 | 0.0733 | 0.48 | 13.79 | 1
December | 24 | 11AM to 12PM | 55.9 | 54.2 | 53.1 | 62.4 | 23.11 | 0.0738 | 0.41 | 13.67 | 1
December | 24 | 12PM to 1PM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
December | 24 | 1PM to 2PM | 55 | 53.9 | 53.1 | 62.4 | 22.89 | 0.0739 | 0.41 | 13.65 | 1
December | 24 | 2PM to 3PM | 54 | 53.4 | 53.1 | 62.4 | 22.63 | 0.0741 | 0.41 | 13.62 | 1
December | 24 | 3PM to 4PM | 55 | 53.9 | 53.1 | 62.4 | 22.89 | 0.0739 | 0.41 | 13.65 | 1
December | 24 | 4PM to 5PM | 55 | 53.2 | 52 | 59.9 | 22.51 | 0.0739 | 0.39 | 13.64 | 1
December | 24 | 5PM to 6PM | 53.1 | 51.3 | 50 | 55.6 | 21.36 | 0.0743 | 0.36 | 13.57 | 1
December | 24 | 6PM to 7PM | 52 | 48.2 | 45 | 45.9 | 19.59 | 0.0745 | 0.3 | 13.52 | 1
December | 24 | 7PM to 8PM | 51.1 | 45.9 | 41 | 39.4 | 18.36 | 0.0746 | 0.26 | 13.47 | 1
December | 24 | 8PM to 9PM | 50 | 45.9 | 42.1 | 41.1 | 18.36 | 0.0748 | 0.27 | 13.45 | 1
December | 24 | 9PM to 10PM | 50 | 46.3 | 43 | 42.5 | 18.59 | 0.0748 | 0.28 | 13.45 | 1
December | 24 | 10PM to 11PM | 48 | 44.5 | 41 | 39.4 | 17.62 | 0.0751 | 0.26 | 13.39 | 1
December | 24 | 11PM to 12AM | 46.9 | 43.9 | 41 | 39.4 | 17.36 | 0.0753 | 0.26 | 13.36 | 1
December | 25 | 12AM to 1AM | 46 | 43.5 | 41 | 39.4 | 17.14 | 0.0754 | 0.26 | 13.34 | 1
December | 25 | 1AM to 2AM | 46 | 43.5 | 41 | 39.4 | 17.14 | 0.0754 | 0.26 | 13.34 | 1
December | 25 | 2AM to 3AM | 46 | 42.6 | 39 | 36.4 | 16.68 | 0.0754 | 0.24 | 13.33 | 1
December | 25 | 3AM to 4AM | 46 | 41.7 | 37 | 33.7 | 16.26 | 0.0754 | 0.22 | 13.32 | 1
December | 25 | 4AM to 5AM | 46 | 42.1 | 37.9 | 34.9 | 16.45 | 0.0754 | 0.23 | 13.33 | 1
December | 25 | 5AM to 6AM | 44.1 | 41.6 | 39 | 36.4 | 16.2 | 0.0757 | 0.24 | 13.28 | 1
December | 25 | 6AM to 7AM | 43 | 41.1 | 39 | 36.4 | 15.94 | 0.0759 | 0.24 | 13.25 | 1
December | 25 | 7AM to 8AM | 42.1 | 39.7 | 37 | 33.7 | 15.3 | 0.076 | 0.22 | 13.22 | 1
December | 25 | 8AM to 9AM | 41 | 38.7 | 36 | 32.3 | 14.82 | 0.0762 | 0.21 | 13.18 | 1
December | 25 | 9AM to 10AM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 25 | 10AM to 11AM | 42.1 | 39.7 | 37 | 33.7 | 15.3 | 0.076 | 0.22 | 13.22 | 1
December | 25 | 11AM to 12PM | 41 | 39.1 | 37 | 33.7 | 15.04 | 0.0762 | 0.22 | 13.19 | 1
December | 25 | 12PM to 1PM | 39.9 | 38.6 | 37 | 33.7 | 14.78 | 0.0763 | 0.22 | 13.16 | 1
December | 25 | 1PM to 2PM | 43 | 39.3 | 35.1 | 31.1 | 15.12 | 0.0759 | 0.2 | 13.23 | 1
December | 25 | 2PM to 3PM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
December | 25 | 3PM to 4PM | 43 | 39.3 | 35.1 | 31.1 | 15.12 | 0.0759 | 0.2 | 13.23 | 1
December | 25 | 4PM to 5PM | 42.1 | 38.9 | 35.1 | 31.1 | 14.91 | 0.076 | 0.2 | 13.21 | 1
December | 25 | 5PM to 6PM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
December | 25 | 6PM to 7PM | 41 | 37.8 | 34 | 29.8 | 14.44 | 0.0762 | 0.2 | 13.18 | 1
December | 25 | 7PM to 8PM | 41 | 37.8 | 34 | 29.8 | 14.44 | 0.0762 | 0.2 | 13.18 | 1
December | 25 | 8PM to 9PM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
December | 25 | 9PM to 10PM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
December | 25 | 10PM to 11PM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
December | 25 | 11PM to 12AM | 39.9 | 37.7 | 35.1 | 31.1 | 14.38 | 0.0764 | 0.2 | 13.15 | 1
December | 26 | 12AM to 1AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
December | 26 | 1AM to 2AM | 39.9 | 38.1 | 36 | 32.3 | 14.56 | 0.0764 | 0.21 | 13.16 | 1
December | 26 | 2AM to 3AM | 39 | 37.2 | 35.1 | 31.1 | 14.17 | 0.0765 | 0.2 | 13.13 | 1
December | 26 | 3AM to 4AM | 39 | 37.2 | 35.1 | 31.1 | 14.17 | 0.0765 | 0.2 | 13.13 | 1
December | 26 | 4AM to 5AM | 39 | 37.2 | 35.1 | 31.1 | 14.17 | 0.0765 | 0.2 | 13.13 | 1
December | 26 | 5AM to 6AM | 37.9 | 36.2 | 34 | 29.8 | 13.7 | 0.0767 | 0.2 | 13.1 | 1
December | 26 | 6AM to 7AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
December | 26 | 7AM to 8AM | 37.9 | 36.6 | 35.1 | 31.1 | 13.9 | 0.0767 | 0.2 | 13.1 | 1
December | 26 | 8AM to 9AM | 37.9 | 36.2 | 34 | 29.8 | 13.7 | 0.0767 | 0.2 | 13.1 | 1
December | 26 | 9AM to 10AM | 41 | 38.3 | 35.1 | 31.1 | 14.64 | 0.0762 | 0.2 | 13.18 | 1
December | 26 | 10AM to 11AM | 44.1 | 39.9 | 35.1 | 31.1 | 15.39 | 0.0757 | 0.2 | 13.26 | 1
December | 26 | 11AM to 12PM | 46.9 | 41.4 | 35.1 | 31.1 | 16.08 | 0.0753 | 0.2 | 13.34 | 1
December | 26 | 12PM to 1PM | 48.9 | 42.4 | 35.1 | 31.1 | 16.56 | 0.075 | 0.2 | 13.39 | 1
December | 26 | 1PM to 2PM | 53.1 | 44.4 | 35.1 | 31.1 | 17.56 | 0.0744 | 0.2 | 13.5 | 1
December | 26 | 2PM to 3PM | 54 | 44.8 | 35.1 | 31.1 | 17.78 | 0.0743 | 0.2 | 13.52 | 1
December | 26 | 3PM to 4PM | 54 | 44.8 | 35.1 | 31.1 | 17.78 | 0.0743 | 0.2 | 13.52 | 1
December | 26 | 4PM to 5PM | 50 | 42.5 | 34 | 29.8 | 16.62 | 0.0749 | 0.2 | 13.41 | 1
December | 26 | 5PM to 6PM | 46.9 | 40.9 | 34 | 29.8 | 15.88 | 0.0753 | 0.2 | 13.33 | 1
December | 26 | 6PM to 7PM | 44.1 | 39.5 | 34 | 29.8 | 15.18 | 0.0757 | 0.2 | 13.26 | 1
December | 26 | 7PM to 8PM | 42.1 | 38.4 | 34 | 29.8 | 14.7 | 0.076 | 0.2 | 13.21 | 1
December | 26 | 8PM to 9PM | 39.9 | 37.3 | 34 | 29.8 | 14.18 | 0.0764 | 0.2 | 13.15 | 1
December | 26 | 9PM to 10PM | 39 | 36.8 | 34 | 29.8 | 13.96 | 0.0765 | 0.2 | 13.13 | 1
December | 26 | 10PM to 11PM | 37.9 | 35.8 | 33.1 | 28.8 | 13.54 | 0.0767 | 0.19 | 13.09 | 1
December | 26 | 11PM to 12AM | 37.9 | 35.8 | 33.1 | 28.8 | 13.54 | 0.0767 | 0.19 | 13.09 | 1
December | 27 | 12AM to 1AM | 37 | 35.3 | 33.1 | 28.8 | 13.32 | 0.0768 | 0.19 | 13.07 | 1
December | 27 | 1AM to 2AM | 37 | 35.3 | 33.1 | 28.8 | 13.32 | 0.0768 | 0.19 | 13.07 | 1
December | 27 | 2AM to 3AM | 36 | 34.7 | 33.1 | 28.8 | 13.06 | 0.077 | 0.19 | 13.04 | 1
December | 27 | 3AM to 4AM | 36 | 34.7 | 33.1 | 28.8 | 13.06 | 0.077 | 0.19 | 13.04 | 1
December | 27 | 4AM to 5AM | 36 | 34.3 | 32 | 27.5 | 12.87 | 0.077 | 0.18 | 13.04 | 1
December | 27 | 5AM to 6AM | 36 | 34.3 | 32 | 27.5 | 12.87 | 0.077 | 0.18 | 13.04 | 1
December | 27 | 6AM to 7AM | 35.1 | 33.3 | 30.9 | 26.2 | 12.45 | 0.0771 | 0.17 | 13.01 | 1
December | 27 | 7AM to 8AM | 36 | 33.4 | 30 | 25.1 | 12.5 | 0.077 | 0.16 | 13.03 | 1
December | 27 | 8AM to 9AM | 37.9 | 34.5 | 30 | 25.1 | 12.98 | 0.0767 | 0.16 | 13.08 | 1
December | 27 | 9AM to 10AM | 43 | 37.7 | 30.9 | 26.2 | 14.36 | 0.0759 | 0.17 | 13.22 | 1
December | 27 | 10AM to 11AM | 48.9 | 40.8 | 30.9 | 26.2 | 15.8 | 0.075 | 0.17 | 13.37 | 1
December | 27 | 11AM to 12PM | 55 | 43.1 | 28.9 | 23.9 | 16.92 | 0.0742 | 0.16 | 13.53 | 1
December | 27 | 12PM to 1PM | 59 | 45 | 28.9 | 23.9 | 17.87 | 0.0736 | 0.16 | 13.63 | 1
December | 27 | 1PM to 2PM | 62.1 | 46.2 | 28 | 22.9 | 18.46 | 0.0732 | 0.15 | 13.71 | 1
December | 27 | 2PM to 3PM | 64.9 | 47.5 | 28 | 22.9 | 19.16 | 0.0728 | 0.15 | 13.79 | 1
December | 27 | 3PM to 4PM | 62.1 | 46.8 | 30 | 25.1 | 18.8 | 0.0732 | 0.16 | 13.72 | 1
December | 27 | 4PM to 5PM | 59 | 45.4 | 30 | 25.1 | 18.07 | 0.0736 | 0.16 | 13.64 | 1
December | 27 | 5PM to 6PM | 55.9 | 43.9 | 30 | 25.1 | 17.33 | 0.074 | 0.16 | 13.56 | 1
December | 27 | 6PM to 7PM | 53.1 | 42.8 | 30.9 | 26.2 | 16.8 | 0.0744 | 0.17 | 13.48 | 1
December | 27 | 7PM to 8PM | 51.1 | 42.3 | 32 | 27.5 | 16.52 | 0.0747 | 0.18 | 13.44 | 1
December | 27 | 8PM to 9PM | 48.9 | 41.6 | 33.1 | 28.8 | 16.19 | 0.075 | 0.19 | 13.38 | 1
December | 27 | 9PM to 10PM | 46.9 | 40.6 | 33.1 | 28.8 | 15.71 | 0.0753 | 0.19 | 13.33 | 1
December | 27 | 10PM to 11PM | 46 | 40.1 | 33.1 | 28.8 | 15.5 | 0.0755 | 0.19 | 13.31 | 1
December | 27 | 11PM to 12AM | 45 | 39.9 | 34 | 29.8 | 15.4 | 0.0756 | 0.2 | 13.28 | 1
December | 28 | 12AM to 1AM | 42.1 | 38.4 | 34 | 29.8 | 14.7 | 0.076 | 0.2 | 13.21 | 1
December | 28 | 1AM to 2AM | 41 | 37.8 | 34 | 29.8 | 14.44 | 0.0762 | 0.2 | 13.18 | 1
December | 28 | 2AM to 3AM | 39 | 36.8 | 34 | 29.8 | 13.96 | 0.0765 | 0.2 | 13.13 | 1
December | 28 | 3AM to 4AM | 37.9 | 36.2 | 34 | 29.8 | 13.7 | 0.0767 | 0.2 | 13.1 | 1
December | 28 | 4AM to 5AM | 37 | 35.7 | 34 | 29.8 | 13.48 | 0.0768 | 0.2 | 13.07 | 1
December | 28 | 5AM to 6AM | 37 | 35.7 | 34 | 29.8 | 13.48 | 0.0768 | 0.2 | 13.07 | 1
December | 28 | 6AM to 7AM | 36 | 35.1 | 34 | 29.8 | 13.22 | 0.077 | 0.2 | 13.04 | 1
December | 28 | 7AM to 8AM | 37 | 35.7 | 34 | 29.8 | 13.48 | 0.0768 | 0.2 | 13.07 | 1
December | 28 | 8AM to 9AM | 43 | 38.9 | 34 | 29.8 | 14.92 | 0.0759 | 0.2 | 13.23 | 1
December | 28 | 9AM to 10AM | 44.1 | 39.1 | 33.1 | 28.8 | 15.02 | 0.0758 | 0.19 | 13.25 | 1
December | 28 | 10AM to 11AM | 48 | 41.1 | 33.1 | 28.8 | 15.97 | 0.0752 | 0.19 | 13.36 | 1
December | 28 | 11AM to 12PM | 50 | 41.3 | 30.9 | 26.2 | 16.06 | 0.0749 | 0.17 | 13.4 | 1
December | 28 | 12PM to 1PM | 52 | 42.3 | 30.9 | 26.2 | 16.53 | 0.0746 | 0.17 | 13.46 | 1
December | 28 | 1PM to 2PM | 55 | 43.8 | 30.9 | 26.2 | 17.27 | 0.0742 | 0.17 | 13.54 | 1
December | 28 | 2PM to 3PM | 55.9 | 44.2 | 30.9 | 26.2 | 17.49 | 0.074 | 0.17 | 13.56 | 1
December | 28 | 3PM to 4PM | 55 | 43.8 | 30.9 | 26.2 | 17.27 | 0.0742 | 0.17 | 13.54 | 1
December | 28 | 4PM to 5PM | 54 | 43 | 30 | 25.1 | 16.85 | 0.0743 | 0.16 | 13.5 | 1
December | 28 | 5PM to 6PM | 52 | 41.6 | 28.9 | 23.9 | 16.18 | 0.0746 | 0.16 | 13.45 | 1
December | 28 | 6PM to 7PM | 50 | 41 | 30 | 25.1 | 15.89 | 0.0749 | 0.16 | 13.4 | 1
December | 28 | 7PM to 8PM | 48 | 40 | 30 | 25.1 | 15.41 | 0.0752 | 0.16 | 13.35 | 1
December | 28 | 8PM to 9PM | 46.9 | 39.4 | 30 | 25.1 | 15.15 | 0.0753 | 0.16 | 13.32 | 1
December | 28 | 9PM to 10PM | 46 | 38.9 | 30 | 25.1 | 14.93 | 0.0755 | 0.16 | 13.3 | 1
December | 28 | 10PM to 11PM | 46 | 38.9 | 30 | 25.1 | 14.93 | 0.0755 | 0.16 | 13.3 | 1
December | 28 | 11PM to 12AM | 46 | 38.5 | 28.9 | 23.9 | 14.74 | 0.0755 | 0.16 | 13.29 | 1
December | 29 | 12AM to 1AM | 44.1 | 37.5 | 28.9 | 23.9 | 14.27 | 0.0758 | 0.16 | 13.24 | 1
December | 29 | 1AM to 2AM | 43 | 36.9 | 28.9 | 23.9 | 14.01 | 0.0759 | 0.16 | 13.21 | 1
December | 29 | 2AM to 3AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
December | 29 | 3AM to 4AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
December | 29 | 4AM to 5AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
December | 29 | 5AM to 6AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
December | 29 | 6AM to 7AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
December | 29 | 7AM to 8AM | 42.1 | 36.4 | 28.9 | 23.9 | 13.79 | 0.0761 | 0.16 | 13.19 | 1
December | 29 | 8AM to 9AM | 43 | 36.9 | 28.9 | 23.9 | 14.01 | 0.0759 | 0.16 | 13.21 | 1
December | 29 | 9AM to 10AM | 45 | 37.9 | 28.9 | 23.9 | 14.48 | 0.0757 | 0.16 | 13.26 | 1
December | 29 | 10AM to 11AM | 48 | 40 | 30 | 25.1 | 15.41 | 0.0752 | 0.16 | 13.35 | 1
December | 29 | 11AM to 12PM | 54 | 41.3 | 25 | 19.8 | 16.03 | 0.0744 | 0.13 | 13.49 | 1
December | 29 | 12PM to 1PM | 55.9 | 42 | 24.1 | 19 | 16.38 | 0.0741 | 0.12 | 13.54 | 1
December | 29 | 1PM to 2PM | 57.9 | 42.7 | 23 | 18.1 | 16.71 | 0.0738 | 0.12 | 13.59 | 1
December | 29 | 2PM to 3PM | 59 | 43.5 | 24.1 | 19 | 17.12 | 0.0736 | 0.12 | 13.62 | 1
December | 29 | 3PM to 4PM | 57.9 | 44.2 | 28 | 22.9 | 17.46 | 0.0738 | 0.15 | 13.6 | 1
December | 29 | 4PM to 5PM | 57 | 44.1 | 28.9 | 23.9 | 17.4 | 0.0739 | 0.16 | 13.58 | 1
December | 29 | 5PM to 6PM | 55.9 | 43.5 | 28.9 | 23.9 | 17.14 | 0.074 | 0.16 | 13.55 | 1
December | 29 | 6PM to 7PM | 55.9 | 43.5 | 28.9 | 23.9 | 17.14 | 0.074 | 0.16 | 13.55 | 1
December | 29 | 7PM to 8PM | 57.9 | 44.5 | 28.9 | 23.9 | 17.61 | 0.0738 | 0.16 | 13.6 | 1
December | 29 | 8PM to 9PM | 57.9 | 44.5 | 28.9 | 23.9 | 17.61 | 0.0738 | 0.16 | 13.6 | 1
December | 29 | 9PM to 10PM | 54 | 43 | 30 | 25.1 | 16.85 | 0.0743 | 0.16 | 13.5 | 1
December | 29 | 10PM to 11PM | 52 | 42.3 | 30.9 | 26.2 | 16.53 | 0.0746 | 0.17 | 13.46 | 1
December | 29 | 11PM to 12AM | 53.1 | 42.5 | 30 | 25.1 | 16.63 | 0.0744 | 0.16 | 13.48 | 1
December | 30 | 12AM to 1AM | 51.1 | 41.9 | 30.9 | 26.2 | 16.32 | 0.0747 | 0.17 | 13.43 | 1
December | 30 | 1AM to 2AM | 48.9 | 43.2 | 37 | 33.7 | 16.96 | 0.075 | 0.22 | 13.4 | 1
December | 30 | 2AM to 3AM | 45 | 42.5 | 39.9 | 37.8 | 16.63 | 0.0756 | 0.25 | 13.31 | 1
December | 30 | 3AM to 4AM | 43 | 43 | 43 | 42.5 | 16.88 | 0.0758 | 0.28 | 13.27 | 1
December | 30 | 4AM to 5AM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
December | 30 | 5AM to 6AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
December | 30 | 6AM to 7AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 30 | 7AM to 8AM | 46 | 46 | 46 | 47.9 | 18.45 | 0.0753 | 0.31 | 13.36 | 1
December | 30 | 8AM to 9AM | 46.9 | 46.5 | 46 | 47.9 | 18.67 | 0.0752 | 0.31 | 13.39 | 1
December | 30 | 9AM to 10AM | 48 | 47.4 | 46.9 | 49.6 | 19.19 | 0.075 | 0.32 | 13.42 | 1
December | 30 | 10AM to 11AM | 48.9 | 48.4 | 48 | 51.6 | 19.73 | 0.0749 | 0.34 | 13.45 | 1
December | 30 | 11AM to 12PM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
December | 30 | 12PM to 1PM | 50 | 48.9 | 48 | 51.6 | 19.99 | 0.0747 | 0.34 | 13.48 | 1
December | 30 | 1PM to 2PM | 48.9 | 47.8 | 46.9 | 49.6 | 19.41 | 0.0749 | 0.32 | 13.45 | 1
December | 30 | 2PM to 3PM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
December | 30 | 3PM to 4PM | 48 | 47 | 46 | 47.9 | 18.93 | 0.075 | 0.31 | 13.42 | 1
December | 30 | 4PM to 5PM | 46.9 | 45.9 | 45 | 45.9 | 18.37 | 0.0752 | 0.3 | 13.38 | 1
December | 30 | 5PM to 6PM | 46.9 | 45.9 | 45 | 45.9 | 18.37 | 0.0752 | 0.3 | 13.38 | 1
December | 30 | 6PM to 7PM | 46 | 45.5 | 45 | 45.9 | 18.15 | 0.0753 | 0.3 | 13.36 | 1
December | 30 | 7PM to 8PM | 46 | 45.5 | 45 | 45.9 | 18.15 | 0.0753 | 0.3 | 13.36 | 1
December | 30 | 8PM to 9PM | 46 | 45.5 | 45 | 45.9 | 18.15 | 0.0753 | 0.3 | 13.36 | 1
December | 30 | 9PM to 10PM | 46 | 45.5 | 45 | 45.9 | 18.15 | 0.0753 | 0.3 | 13.36 | 1
December | 30 | 10PM to 11PM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
December | 30 | 11PM to 12AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
December | 31 | 12AM to 1AM | 45 | 45 | 45 | 45.9 | 17.89 | 0.0755 | 0.3 | 13.33 | 1
December | 31 | 1AM to 2AM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
December | 31 | 2AM to 3AM | 44.1 | 44.1 | 44.1 | 44.4 | 17.43 | 0.0757 | 0.29 | 13.3 | 1
December | 31 | 3AM to 4AM | 43 | 43 | 43 | 42.5 | 16.88 | 0.0758 | 0.28 | 13.27 | 1
December | 31 | 4AM to 5AM | 43 | 43 | 43 | 42.5 | 16.88 | 0.0758 | 0.28 | 13.27 | 1
December | 31 | 5AM to 6AM | 43 | 43 | 43 | 42.5 | 16.88 | 0.0758 | 0.28 | 13.27 | 1
December | 31 | 6AM to 7AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
December | 31 | 7AM to 8AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
December | 31 | 8AM to 9AM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
December | 31 | 9AM to 10AM | 43 | 42.5 | 42.1 | 41.1 | 16.66 | 0.0758 | 0.27 | 13.26 | 1
December | 31 | 10AM to 11AM | 43 | 42.5 | 42.1 | 41.1 | 16.66 | 0.0758 | 0.27 | 13.26 | 1
December | 31 | 11AM to 12PM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
December | 31 | 12PM to 1PM | 42.1 | 42.1 | 42.1 | 41.1 | 16.44 | 0.076 | 0.27 | 13.24 | 1
December | 31 | 1PM to 2PM | 43 | 42 | 41 | 39.4 | 16.4 | 0.0758 | 0.26 | 13.26 | 1
December | 31 | 2PM to 3PM | 43 | 42 | 41 | 39.4 | 16.4 | 0.0758 | 0.26 | 13.26 | 1
December | 31 | 3PM to 4PM | 42.1 | 41.5 | 41 | 39.4 | 16.18 | 0.076 | 0.26 | 13.23 | 1
December | 31 | 4PM to 5PM | 42.1 | 41 | 39.9 | 37.8 | 15.93 | 0.076 | 0.25 | 13.23 | 1
December | 31 | 5PM to 6PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
December | 31 | 6PM to 7PM | 42.1 | 40.6 | 39 | 36.4 | 15.72 | 0.076 | 0.24 | 13.23 | 1
December | 31 | 7PM to 8PM | 41 | 40 | 39 | 36.4 | 15.46 | 0.0762 | 0.24 | 13.2 | 1
December | 31 | 8PM to 9PM | 41 | 39.6 | 37.9 | 34.9 | 15.23 | 0.0762 | 0.23 | 13.19 | 1
December | 31 | 9PM to 10PM | 41 | 39.6 | 37.9 | 34.9 | 15.23 | 0.0762 | 0.23 | 13.19 | 1
December | 31 | 10PM to 11PM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1
December | 31 | 11PM to 12AM | 39.9 | 39 | 37.9 | 34.9 | 14.97 | 0.0763 | 0.23 | 13.16 | 1

## Akton Atlanta Design Day
Project Name
Date | 2021-07-11
Altitude (ft) | 580.7087
Barometric Pressure (in. Hg) | 29.2987
Atmospheric Pressure (psia) | 14.3902
Point Name | Airflow | Condition | Airflow UOM | Dry Bulb (°F) | Wet Bulb (°F) | Relative Humidity (%) | Humidity Ratio (gr/lb) | Humidity Ratio (lb/lb) | Specific Volume (cu.ft./lb) | Enthalpy (Btu/lb) | Dew Point (°F) | Density (lb/cu.ft.) | Vapor Pressure (in. Hg) | Absolute Humidity (gr/cu.ft.)
CC LAT | 1000 | Standard | cfm | 51 | 50.8 | 98.7055 | 56.1306 | 0.0080187 | 13.312 | 20.9317 | 50.64 | 0.075722 | 0.37136 | 4.2165
Fan Heat | 1000 | Standard | cfm | 52.5 | 51.1268 | 91.4454 | 54.95 | 0.00785 | 13.3475 | 21.1142 | 50.08 | 0.075508 | 0.36371 | 4.1169
Duct Temp. Rise | 1000 | Standard | cfm | 53.5 | 51.5526 | 88.1469 | 54.95 | 0.00785 | 13.3736 | 21.3576 | 50.08 | 0.075361 | 0.36371 | 4.1088
Space Condition
| 1000 | Standard | cfm | 72 | 59.9821 | 50 | 59.8708 | 0.008553 | 13.8711 | 26.6305 | 52.37 | 0.072709 | 0.39589 | 4.3162
Atlanta 0.4% Cooling | 1000 | Standard | cfm | 93.8 | 74.3 | 40.6854 | 99.4853 | 0.014212 | 14.5693 | 38.1854 | 66.32 | 0.069613 | 0.65172 | 6.8284
Return Air Condition | 1000 | Standard | cfm | 73 | 60.3362 | 48.323 | 59.85 | 0.00855 | 13.8972 | 26.871 | 52.36 | 0.072572 | 0.39574 | 4.3066
Mixed Air | 1000 | Standard | cfm | 78.2401 | 64.2539 | 47.1918 | 69.7588 | 0.0099655 | 14.0653 | 29.6996 | 56.49 | 0.071805 | 0.46013 | 4.9596
Point Name | Process Name | Total Energy (tons) | Total Energy (Btu/hr) | Sensible Energy (Btu/hr) | Latent Energy (Btu/hr) | Sensible Heat Ratio | Moisture Difference (lb/hr) | Moisture Difference (gal/hr) | Start Point Name | Second Point Name
CC LAT | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CC LAT
Fan Heat | Connect States | 0.068417 | 821 | 1643 | -822 | 2.0012 | -0.75898 | -0.090939 | CC LAT
Duct Temp. Rise | Connect States | 0.09125 | 1095 | 1095 | 0 | 1 | 0 | 0 | Fan Heat
Space Condition
| Connect States | 1.9772 | 23727 | 20296 | 3431 | 0.8554 | 3.1634 | 0.37903 | Duct Temp. Rise
Atlanta 0.4% Cooling | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Return Air Condition | Connect States | 0.090167 | 1082 | 1097 | -15 | 1.0139 | -0.013402 | -0.0016058 | Space Condition
Mixed Air | Air Mixing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Nashville 0.4% Cooling Design | Return Air Condition

## Akton Atlanta Econ Change Over
Project Name
Date | 2021-07-11
Altitude (ft) | 1010.4987
Barometric Pressure (in. Hg) | 28.8447
Atmospheric Pressure (psia) | 14.1672
Point Name | Airflow | Condition | Airflow UOM | Dry Bulb (°F) | Wet Bulb (°F) | Relative Humidity (%) | Humidity Ratio (gr/lb) | Humidity Ratio (lb/lb) | Specific Volume (cu.ft./lb) | Enthalpy (Btu/lb) | Dew Point (°F) | Density (lb/cu.ft.) | Vapor Pressure (in. Hg) | Absolute Humidity (gr/cu.ft.)
Marriott Space | 1000 | Standard | cfm | 72 | 59.9136 | 50 | 60.8263 | 0.0086895 | 14.0925 | 26.7814 | 52.37 | 0.071576 | 0.39589 | 4.3162
0.4% Cooling Design | 1000 | Standard | cfm | 93.8 | 74.3 | 40.8873 | 101.6009 | 0.014514 | 14.8056 | 38.5203 | 66.47 | 0.068522 | 0.65511 | 6.8623
.0.4% Evap Design | 1000 | Standard | cfm | 88.2 | 79.8433 | 70.0527 | 147.6288 | 0.02109 | 14.807 | 44.3742 | 77.2 | 0.06896 | 0.94209 | 9.9702
99.6% Heating Design | 1000 | Standard | cfm | 20.7 | 16.829 | 50 | 8.0712 | 0.001153 | 12.5809 | 6.206 | 6.66 | 0.079577 | 0.053133 | 0.64154
Bin DB and MCWB | 1000 | Standard | cfm | 102 | 77.7 | 34.4703 | 110.1059 | 0.015729 | 15.0536 | 41.8853 | 68.74 | 0.067474 | 0.70843 | 7.3143
97 Bin | 1000 | Standard | cfm | 97 | 75.5 | 37.8855 | 103.9137 | 0.014845 | 14.8989 | 39.6737 | 67.1 | 0.068115 | 0.66955 | 6.9746
92 Bin | 1000 | Standard | cfm | 92 | 74.4 | 44.7124 | 105.1567 | 0.015022 | 14.7692 | 38.6364 | 67.44 | 0.068725 | 0.67745 | 7.12
87 Bin | 1000 | Standard | cfm | 87 | 72.6 | 50.9657 | 102.356 | 0.014622 | 14.6262 | 36.9631 | 66.68 | 0.06937 | 0.65989 | 6.9981
82 Bin | 1000 | Standard | cfm | 82 | 70.5 | 57.5036 | 98.2656 | 0.014038 | 14.4791 | 35.0894 | 65.53 | 0.070034 | 0.63408 | 6.7867
77 Bin | 1000 | Standard | cfm | 77 | 68.5 | 65.7247 | 95.2668 | 0.01361 | 14.3359 | 33.389 | 64.66 | 0.070705 | 0.61515 | 6.6454
72 Bin | 1000 | Standard | cfm | 72 | 66.2 | 74.436 | 91.1759 | 0.013025 | 14.1893 | 31.5201 | 63.43 | 0.071394 | 0.58922 | 6.4257
67 Bin | 1000 | Standard | cfm | 67 | 61.2 | 72.6739 | 74.7463 | 0.010678 | 14.0039 | 27.7311 | 57.94 | 0.072171 | 0.48483 | 5.3375
62 Bin | 1000 | Standard | cfm | 62 | 56.1 | 70.1268 | 60.3667 | 0.0086238 | 13.826 | 24.2713 | 52.16 | 0.072951 | 0.39284 | 4.3662
57 Bin | 1000 | Standard | cfm | 57 | 51.2 | 68.156 | 48.9496 | 0.0069928 | 13.6581 | 21.2804 | 46.62 | 0.073728 | 0.31946 | 3.5839
52 Bin | 1000 | Standard | cfm | 52 | 46.6 | 67.5175 | 40.3235 | 0.0057605 | 13.4995 | 18.7289 | 41.59 | 0.074503 | 0.26359 | 2.987
47 Bin | 1000 | Standard | cfm | 47 | 42.1 | 67.4194 | 33.3598 | 0.0047657 | 13.3465 | 16.4399 | 36.78 | 0.075283 | 0.21844 | 2.4995
42 Bin | 1000 | Standard | cfm | 42 | 37.7 | 68.1006 | 27.8105 | 0.0039729 | 13.1981 | 14.3734 | 32.25 | 0.07607 | 0.18232 | 2.1072
37 Bin | 1000 | Standard | cfm | 37 | 33.1 | 67.4824 | 22.648 | 0.0032354 | 13.0512 | 12.37 | 27.79 | 0.076869 | 0.14861 | 1.7353
32 Bin | 1000 | Standard | cfm | 32 | 28.5 | 67.6292 | 18.5783 | 0.002654 | 12.9078 | 10.5377 | 23.59 | 0.077678 | 0.12201 | 1.4393
27 Bin | 1000 | Standard | cfm | 27 | 23.7 | 64.8338 | 14.1196 | 0.0020171 | 12.7635 | 8.6484 | 17.89 | 0.078506 | 0.092836 | 1.1062
22 Bin | 1000 | Standard | cfm | 22 | 19.2 | 65.0673 | 11.1848 | 0.0015978 | 12.6239 | 6.995 | 13.15 | 0.079341 | 0.073593 | 0.886
17 Bin | 1000 | Standard | cfm | 17 | 14.9 | 68.8759 | 9.3008 | 0.0013287 | 12.4875 | 5.5038 | 9.46 | 0.080187 | 0.061218 | 0.74481
12 Bin | 1000 | Standard | cfm | 12 | 10.4 | 71.4927 | 7.5455 | 0.0010779 | 12.3515 | 4.0335 | 5.34 | 0.081049 | 0.049671 | 0.61089
7 Bin | 1000 | Standard | cfm | 7 | 5.8 | 73.9687 | 6.0698 | 0.00086711 | 12.2165 | 2.6067 | 1.14 | 0.081928 | 0.039983 | 0.49685
2 Bin | 1000 | Standard | cfm | 2 | 0.07 | 48.5944 | 3.0824 | 0.00044034 | 12.0773 | 0.95163 | -11.5 | 0.082836 | 0.020306 | 0.25522
-3 Bin | 1000 | Standard | cfm | -3 | -3.6 | 79.9564 | 3.9017 | 0.00055739 | 11.9488 | -0.12531 | -7.18 | 0.083737 | 0.025707 | 0.32654
-8 Bin | 1000 | Standard | cfm | -8 | -8 | 100 | 3.7314 | 0.00053306 | 11.8175 | -1.3523 | -8 | 0.084665 | 0.02459 | 0.31575
Economizer high limit | 1000 | Standard | cfm | 65.7 | 59.7964 | 71.7 | 70.426 | 0.010061 | 13.9558 | 26.7401 | 56.32 | 0.072376 | 0.45731 | 5.0464
Point Name | Process Name | Total Energy (tons) | Total Energy (Btu/hr) | Sensible Energy (Btu/hr) | Latent Energy (Btu/hr) | Sensible Heat Ratio | Moisture Difference (lb/hr) | Moisture Difference (gal/hr) | Start Point Name
Marriott Space | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
0.4% Cooling Design | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
.0.4% Evap Design | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
99.6% Heating Design | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Bin DB and MCWB | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
97 Bin | Connect States | -0.82942 | -9953 | -5549 | -4404 | 0.55752 | -3.9807 | -0.47696 | Bin DB and MCWB
92 Bin | Connect States | -0.389 | -4668 | -5551 | 883 | 1.1892 | 0.79908 | 0.095744 | 97 Bin
87 Bin | Connect States | -0.6275 | -7530 | -5547 | -1983 | 0.73665 | -1.8004 | -0.21573 | 92 Bin
82 Bin | Connect States | -0.70267 | -8432 | -5541 | -2891 | 0.65714 | -2.6295 | -0.31506 | 87 Bin
77 Bin | Connect States | -0.63767 | -7652 | -5536 | -2116 | 0.72347 | -1.9278 | -0.23099 | 82 Bin
72 Bin | Connect States | -0.70092 | -8411 | -5531 | -2880 | 0.65759 | -2.6299 | -0.31511 | 77 Bin
67 Bin | Connect States | -1.4209 | -17051 | -5507 | -11544 | 0.32297 | -10.5619 | -1.2655 | 72 Bin
62 Bin | Connect States | -1.2975 | -15570 | -5487 | -10083 | 0.35241 | -9.244 | -1.1076 | 67 Bin
57 Bin | Connect States | -1.1217 | -13460 | -5470 | -7990 | 0.40639 | -7.3395 | -0.87941 | 62 Bin
52 Bin | Connect States | -0.95683 | -11482 | -5458 | -6024 | 0.47535 | -5.5454 | -0.66444 | 57 Bin
47 Bin | Connect States | -0.85842 | -10301 | -5448 | -4853 | 0.52888 | -4.4766 | -0.53638 | 52 Bin
42 Bin | Connect States | -0.775 | -9300 | -5440 | -3860 | 0.58495 | -3.5674 | -0.42744 | 47 Bin
37 Bin | Connect States | -0.75133 | -9016 | -5433 | -3583 | 0.6026 | -3.3187 | -0.39764 | 42 Bin
32 Bin | Connect States | -0.68717 | -8246 | -5427 | -2819 | 0.65814 | -2.6163 | -0.31347 | 37 Bin
27 Bin | Connect States | -0.74375 | -8925 | -5421 | -3504 | 0.60739 | -2.8663 | -0.34343 | 32 Bin
22 Bin | Connect States | -0.64358 | -7723 | -5416 | -2307 | 0.70128 | -1.8866 | -0.22605 | 27 Bin
17 Bin | Connect States | -0.57458 | -6895 | -5414 | -1481 | 0.78521 | -1.2111 | -0.14512 | 22 Bin
12 Bin | Connect States | -0.56592 | -6791 | -5411 | -1380 | 0.79679 | -1.1284 | -0.13521 | 17 Bin
7 Bin | Connect States | -0.54742 | -6569 | -5409 | -1160 | 0.82341 | -0.94868 | -0.11367 | 12 Bin
2 Bin | Connect States | -0.64617 | -7754 | -5405 | -2349 | 0.69706 | -1.9205 | -0.23011 | 7 Bin
-3 Bin | Connect States | -0.39683 | -4762 | -5406 | 644 | 1.1352 | 0.52672 | 0.06311 | 2 Bin
-8 Bin | Connect States | -0.46167 | -5540 | -5406 | -134 | 0.97581 | -0.10946 | -0.013115 | -3 Bin
Economizer high limit | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Akton Portland Design Day
Project Name
Date | 2021-07-15
Altitude (ft) | 580.7087
Barometric Pressure (in. Hg) | 29.2987
Atmospheric Pressure (psia) | 14.3902
Point Name | Airflow | Condition | Airflow UOM | Dry Bulb (°F) | Wet Bulb (°F) | Relative Humidity (%) | Humidity Ratio (gr/lb) | Humidity Ratio (lb/lb) | Specific Volume (cu.ft./lb) | Enthalpy (Btu/lb) | Dew Point (°F) | Density (lb/cu.ft.) | Vapor Pressure (in. Hg) | Absolute Humidity (gr/cu.ft.)
CC LAT | 1000 | Standard | cfm | 51 | 50.8 | 98.7055 | 56.1306 | 0.0080187 | 13.312 | 20.9317 | 50.64 | 0.075722 | 0.37136 | 4.2165
Fan Heat | 1000 | Standard | cfm | 52.5 | 51.4438 | 93.4005 | 56.14 | 0.00802 | 13.3511 | 21.2985 | 50.65 | 0.075501 | 0.37149 | 4.2049
Duct Temp. Rise | 1000 | Standard | cfm | 53.5 | 51.8671 | 90.0315 | 56.14 | 0.00802 | 13.3772 | 21.542 | 50.65 | 0.075354 | 0.37149 | 4.1967
Space Condition
| 1000 | Standard | cfm | 72 | 59.9821 | 50 | 59.8708 | 0.008553 | 13.8711 | 26.6305 | 52.37 | 0.072709 | 0.39589 | 4.3162
Portland 0.4% Cooling | 1000 | Standard | cfm | 91.2 | 67.5 | 29.1699 | 65.2871 | 0.0093267 | 14.3897 | 32.1636 | 54.69 | 0.070143 | 0.43102 | 4.5371
Return Air Condition | 1000 | Standard | cfm | 73 | 60.3362 | 48.323 | 59.85 | 0.00855 | 13.8972 | 26.871 | 52.36 | 0.072572 | 0.39574 | 4.3066
Mixed Air | 1000 | Standard | cfm | 77.5548 | 62.2308 | 42.4374 | 61.2093 | 0.0087442 | 14.0203 | 28.1942 | 52.96 | 0.071949 | 0.40457 | 4.3658
Point Name | Process Name | Total Energy (tons) | Total Energy (Btu/hr) | Sensible Energy (Btu/hr) | Latent Energy (Btu/hr) | Sensible Heat Ratio | Moisture Difference (lb/hr) | Moisture Difference (gal/hr) | Start Point Name | Second Point Name
CC LAT | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CC LAT
Fan Heat | Connect States | 0.1375 | 1650 | 1644 | 6 | 0.99636 | 0.0060187 | 0.00072115 | CC LAT
Duct Temp. Rise | Connect States | 0.091333 | 1096 | 1096 | 0 | 1 | 0 | 0 | Fan Heat
Space Condition
| Connect States | 1.9081 | 22897 | 20296 | 2601 | 0.8864 | 2.3984 | 0.28737 | Duct Temp. Rise
Portland 0.4% Cooling | None | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Return Air Condition | Connect States | 0.090167 | 1082 | 1097 | -15 | 1.0139 | -0.013403 | -0.0016059 | Space Condition
Mixed Air | Air Mixing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Portland 0.4% Cooling | Return Air Condition