## Curve Image and Nameplate
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Notice: I have provided this spreadsheet for educational purposes. I am fine with you using it as a starting point for your own spreadsheet performing a similar analysis or even using it as is. But you are using it at your own risk and neither FDE nor I can not be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head.
Engineering Calculation
| Date: | 2017-04-29 10:57
| Project Name: | Pump Curve Generator
| Project Number: | None
| Engineer: | David
Notes
1 | This spreadsheet is intended to facilitate generating an electronic version of a pump or fan curve from data you generate using Plot Digitizer. The link below will take you to a page on my website that provides more information on plot digitizer and a link to the download location.
http://www.av8rdas.com/plot-digitizer.html
2 | The tool is not totally automated but should save time vs. having to create a new chart from the plot digitizer CSV files every time you digitize a new pump curve.
3 | There are instructions on the "Impeller Data" tab that explain more about how to use it. This tab is a place where you can paste in an image of the curve that you used in plot digitizer for a reference and also enter the basic pump nameplate data, which populates the labels on the actual pump curve chart.
4 | The links below serve no purpose in this tool but facilitate navigation when you insert a copy of the curve you have crated into the pump law tool spreadsheet tool I have so you can use the curve to project impeller sizes, pump speeds, and develop a bhp vs. flow or speed relationship for a specific system. For them to actually work, you will have to set edit the hyperlinks as needed once you insert the curve into the affinity law tool.
5 | Personally, I have found it useful to link to the folders where the original CSV files are located for future reference, which is what the "Links to supporting file locations" are for. You will need to edit them for you file lcations if you want that feature to work.
Click here to go to the data used to plot the digital pump curve set
Click here to go to the design condition tabs
Click here to go to the 75% load condition tabs
Click here to go to the 50% load condition tabs
Click here to go to the 25% load condition tabs
Click here to go to the 12.5% load condition tabs
Click here to go to the summary tab
Enter nameplate data below to generate lables that will automatically update on the pump curve chart
| Pump Make | Bell and Gossett
| Pump Series and/or Model | Series e-1510 5A
| Pump Speed | 3550
Pump Impeller Size
Pump Motor HP
Note that the CSV files used for this were originally generated from an older version of the curve vs. the image to the right, which is a cleaner image. But the curves appear to be identical.
Label Generator
| Pump Make | Bell and Gossett
| Pump Series and/or Model | Series e-1510 5A
| Pump Speed | 3,550 rpm
Pump Impeller Size
Pump Motor HP
Links to supporting file locations
Impeller lines CSV files
Efficiency lines CSV files
BHP lines CSV files
NPSH line CSV files

## Impeller Data
This is the tab where you paste in your raw data from the impeller lines you created using Plot Digitizer. If you fill in the pump nameplate data on the "Curve Image and Nameplate" tab, the chart lable will automatically update to reflect those values. When you digitize your curve, it is likely that you will not have exactly the same number of data pairs for each line as were created for the curve that was the basis of this template. You could just paste your data in over the data that is already here and re-select it for the chart on the "Pump Curve" full tab and there is nothing wrong with that. If if you can create your raw data so that each series (line) you digitize has the same number of data pairs as the template has for a given impeller size and paste your data in over the data that is in the template then the chart would automatically update with your data, which would save you some time compared to having to reselect your data. But that is harder than it sounds. However, the pump data tabs in the spreadsheet (the red tabs) are set up to allow you to use the procedure below as a way to allow you insert your data in a way that will minimize the amount of effort required on your part. Note that this template contains room for 8 impeller lines, 7 efficiency lines, 6 bhp lines and one net positive suction head line . If you have more lines than that, then you will need to paste the data a blank space on the appropriate tab and add them to the chart using standard Excel graphing techniques. You will also need to add the labels for them. If you have fewer lines than there are provided for in this template, then you can delete the rows with the template data and then delete the blank series from the chart along with the labels associated with them. Regardless of the number of impeller lines efficiency lines, brake horsepower lines, and NPSH lines, you will need to adjust the chart axis ranges to match the requirements of the particular fan or pump you are developing the chart for.
1 | Select a data series that you want to replace with your data.
2 | Highlight all of the rows with existing data pairs between the colored rows and delete them. For example, if you were going to replace the 10 inch impeller data in the template with new date, you would highlight and delete all of the rows between the two rows with red highlighting.
3 | Open up the .csv file for one of the impeller lines that you created in pump digitizer.
4 | Highlight all of the rows with data pairs in them and copy them.
5 | Use the "Insert Copied Rows" function to insert the rows from your CSV file between the to colored rows that were left after you deleted the data from the template. For instance if you were going to insert data to replace the data in this template that you deleted for the 10 inch impeller, you would insert your rows between the two rows with red highlighting. Depending on how your CSV files are formatted, you may need to cut and paste the inserted data one column to the right (vs. dragging the cells) after you insert the rows to get the flow and head into the righ columns.
6 | Zero the flow value associated with the dead head point from your digitized data to create a clean cut-off of the impeller line at the 0 gpm axis
7 | Insert the labe you want to use for the series where indicated.
8 | Repeat this process for all of the remaining impeller line CSV files.
9 | Frequently, when you do the digitization process in Plot Digitizer, you will be slightyly off center when you click on the curve you are digitizing to add a point. As a result, when you plot the data, the curve on the chart will have a slight "wiggle" in it at that point. You can manually "tweak" the digitizer data to elminate this and make the curve smooth. When I do this, I find it to be helpful to temporarily turn on the markers for the curve I want to "tweak" and use them to help me identify the point or points where a minor adjustment would be desirable. I then make the necessary adjustments and once the curve is smooth, turn the markers back off. I also copy and paste the original values to the right of the plotted series and highlight the ones I change to make easier to go back to the original if I need to. I personally find it easier to "tweak" the head value than the flow value to smooth the curve out for some reason.
10 | If you have more impeller lines than where provided for by the template, then add them below the data currently in the template and add them to the chart using standard Excel data plotting techniques.
11 | If you have fewer impeller lines that are provided for by the template, lable the unused lines as "Blank 1", "Blank 2" , etc. and then delete the blank series and related labels from the chart.
12 | Adjust the axis in the chart to match the range of flow and head associated with your new data set.
13 | Move the impeller line labels as necessary on the chart to line them up with your new impeller lines.
14 | Add lables for additional impeller lines that you added to the chart.
Comic | Delete labels for unused impeller lines/blank series from the chart.
16 | Perform similar steps for the Efficiency, Bhp, and NPSH tabs to replace the template data with your new data.
17 | Fine tune the appearance of the chart as desired using standard Excel formatting techniques.
18 | For some reason that is likely only known to the folks who code Excel, sometimes, when you delete one of the original series from the chart, the formatting on some of the other series changes. I have not figured out what to do about that other than reformat them.
| 7" |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 0 | 177.186 |  | 0 | 177.186
| 297.409 | 176.9 |  | 297.409 | 176.642
| 400.52 | 176.9 |  | 400.52 | 177.252
| 500.023 | 176.7 |  | 500.023 | 176.379
| 601.328 | 176.692 |  | 601.328 | 176.692
| 700.831 | 175.82 |  | 700.831 | 175.82
| 802.146 | 174.355 |  | 802.146 | 174.355
| 898.038 | 172.296 |  | 898.038 | 172.296
| 1001.17 | 169.943 |  | 1001.17 | 169.943
| 1098.87 | 166.996 |  | 1098.87 | 166.996
| 1198.39 | 163.457 |  | 1198.39 | 163.457
| 1303.35 | 158.733 |  | 1303.35 | 158.733
| 1399.26 | 153.12 |  | 1399.26 | 153.12
| 1500.62 | 145.136 |  | 1500.62 | 145.136
| 1531.39 | 141.882 |  | 1531.39 | 141.882
| 6" |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 0 | 112.592
| 200.111 | 112.922
| 361.116 | 112.949
| 431.672 | 112.368
| 505.849 | 111.491
| 601.739 | 109.729
| 699.445 | 106.782
| 802.581 | 103.54
| 900.295 | 99.4077
| 1001.63 | 94.6836
| 1101.16 | 89.9593
| 1198.88 | 84.9383
| 1305.65 | 78.141
| 1372.61 | 73.7076
| 5.5" |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 0 | 88.5927
| 202.071 | 88.3298
| 256.342 | 88.3387
| 355.845 | 87.4662
| 440.876 | 86.5913
| 513.248 | 84.8254
| 603.717 | 82.1737
| 688.762 | 78.9284
| 797.334 | 74.2055
| 898.669 | 69.4814
| 1005.43 | 64.462
| 1099.54 | 59.1441
| 1200.88 | 52.9385
| 1302.23 | 45.5478
| Blank 1 |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| Blank 2 |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| Blank 3 |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| Blank 4 |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| Blank 5 |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head

## Efficiency Data
This is the tab where you paste in your raw data from the efficiency lines you created using Plot Digitizer. If you fill in the pump nameplate data on the "Curve Image and Nameplate" tab, the chart lable will automatically update to reflect those values. The Impeller Data tab has instructions for a way that allows you to replace the data in this template with your own data so that the pump curve chart automatically updates to reflect the new data points. Note that one thing about the efficiency lines that is different is that some of them are not continuous. You can either digitize them as two seperate curves; 60% left and right for instance and plot them as two seperate curves. Or you can digitize them as one curve and insert a blank row in the series where the curve splits. If you don't do that, they you will get a straight line connecting the two points where the curve is broken. But inserting a blank row will create a break in the plotted line.
| 30% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 261.226 | 176.932
| 259.459 | 170.117
| 252.286 | 159.746
| 250.537 | 149.968
| 245.172 | 139.893
| 245.235 | 129.522
| 245.295 | 119.744
| 250.784 | 109.671
| 252.65 | 100.486
| 254.535 | 88.0421
| 40% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 375.194 | 177.247
| 371.621 | 169.839
| 368.063 | 160.061
| 366.316 | 149.987
| 362.761 | 139.616
| 362.82 | 130.134
| 362.881 | 120.06
| 361.134 | 109.986
| 366.683 | 90.1347
| 368.51 | 87.172
| 50% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 527.161 | 176.087
| 525.39 | 169.865
| 516.406 | 159.789
| 512.847 | 150.307
| 511.101 | 139.936
| 509.356 | 129.566
| 505.794 | 120.38
| 505.794 | 120.38
| 504.05 | 109.713
| 504.119 | 98.4536
| 507.819 | 85.1208
| 60% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| 700.831 | 175.82
| 699.06 | 169.597
| 691.884 | 159.818
| 682.898 | 150.039
| 677.535 | 139.667
| 673.979 | 129.593
| 674.037 | 120.111
| 674.104 | 109.148
| 674.162 | 99.6668
| 677.842 | 89.5933
| 681.524 | 79.2235
| 65% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 816.619 | 174.357
| 805.793 | 169.615
| 794.997 | 160.131
| 786.014 | 150.056
| 780.65 | 139.684
| 775.283 | 129.906
| 775.343 | 120.128
| 780.834 | 109.758
| 786.319 | 100.278
| 802.664 | 89.9101
| 826.244 | 79.8399
| 848 | 72.1398
| 70% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| 937.843 | 171.414
| 925.248 | 160.153
| 914.456 | 150.077
| 909.092 | 139.706
| 912.772 | 129.632
| 916.449 | 120.151
| 925.556 | 110.079
| 943.708 | 100.007
| 963.669 | 89.9366
| 1001.72 | 80.4614
| 1041.56 | 73.6531
| 1092.23 | 70.4022
| 1137.47 | 68.9282
| 1189.93 | 68.6405
| 1247.81 | 69.5389
| 1302.08 | 70.733
| 1401.55 | 74.305
Right
| 73% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
Right
| 1028.31 | 169.059
| 1022.94 | 159.872
| 1017.57 | 150.39
| 1023.06 | 140.021
| 1028.55 | 129.947
| 1048.5 | 121.062
| 1070.28 | 110.399
| 1101.09 | 100.626
| 1151.8 | 91.4491
| 1178.97 | 86.7128
| 1200.68 | 85.2349
| 1235.06 | 83.7591
| 1280.29 | 83.1739
| 1318.28 | 84.0691
| 1390.61 | 88.5254
Right
| 75% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 1113.35 | 166.406
| 1111.59 | 158.998
| 1113.45 | 150.702
| 1118.92 | 142.999
| 1133.46 | 132.928
| 1155.22 | 123.746
| 1178.79 | 115.75
| 1202.34 | 110.124
| 1234.94 | 103.907
| 1269.33 | 100.95
| 1307.32 | 100.364
| 1348.93 | 100.963
| 1385.09 | 103.932
| 1412.2 | 107.492
| 78% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 1252.68 | 160.799
| 1254.55 | 151.022
| 1263.64 | 143.912
| 1279.95 | 138.581
| 1308.92 | 135.327
| 1341.5 | 132.666
| 1370.45 | 131.485
| 1412.06 | 131.196
| 1451.85 | 133.276
| 1495.24 | 137.135
| 1533.2 | 141.586
| 80% |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 1404.69 | 152.824
| 1420.95 | 155.79
| Blank |  | Manually enter the lable you want this data series to have in the yellow cells to the left

## BHP Data
This is the tab where you paste in your raw data from the brake horse power lines you created using Plot Digitizer. If you fill in the pump nameplate data on the "Curve Image and Nameplate" tab, the chart lable will automatically update to reflect those values. The Impeller Data tab has instructions for a way that allows you to replace the data in this template with your own data so that the pump curve chart automatically updates to reflect the new data points.
| 25 Bhp |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 248.939 | 115.597
| 330.377 | 110.573
| 431.721 | 104.368
| 536.686 | 97.8664
| 641.652 | 91.0688
| 732.139 | 85.4541
| 831.676 | 78.9519
| 938.452 | 72.1547
| 1047.04 | 64.7651
| 1144.77 | 57.6701
| 1229.84 | 50.5729
| 1313.1 | 44.0681
| 30 Bhp |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 243.403 | 133.374
| 332.079 | 128.055
| 426.191 | 121.256
| 504.01 | 116.231
| 612.598 | 108.842
| 726.612 | 101.749
| 818.906 | 96.4313
| 929.303 | 89.0421
| 1041.52 | 80.4679
| 1137.44 | 72.78
| 1246.04 | 64.2053
| 1381.78 | 53.2646
| 40 Bhp |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 259.466 | 168.932
| 349.962 | 161.836
| 442.265 | 155.036
| 576.196 | 144.984
| 673.928 | 137.889
| 753.562 | 131.976
| 873.015 | 122.811
| 952.651 | 116.602
| 1030.48 | 110.096
| 1137.26 | 101.817
| 1240.43 | 93.5378
| 1323.69 | 87.0329
| 1403.32 | 80.8238
| 1479.34 | 74.9104
| 50 Bhp |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 651.985 | 176.108 |  | 651.985 | 176.108
| 762.404 | 165.163 |  | 762.404 | 165.163
| 867.386 | 155.699 |  | 867.386 | 155.699
| 974.18 | 145.939 |  | 974.18 | 145.939
| 1062.87 | 137.953 |  | 1062.87 | 137.953
| 1158.8 | 129.376 |  | 1158.8 | 129.376
| 1271.03 | 119 |  | 1271.03 | 118.432
| 1354.3 | 109 |  | 1354.3 | 110.445
| 1423.08 | 101.5 |  | 1423.08 | 103.346
| 1502.73 | 95.0624 |  | 1502.73 | 95.0624
| 60 Bhp |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 1030.12 | 169.355
| 1111.57 | 161.072
| 1194.84 | 152.79
| 1303.45 | 141.845
| 1388.53 | 132.97
| 1500.76 | 121.433
| 75 Bhp |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 1545.71 | 166.181
| 1674.22 | 155.239

## NPSH Data
This is the tab where you paste in your raw data from the net positive suction pressure you created using Plot Digitizer (if you created this line; not all curves will have it). If you fill in the pump nameplate data on the "Curve Image and Nameplate" tab, the chart lable will automatically update to reflect those values. Note that NPSHr curves are usually plotted on a secondary Y axis on the right of the chart, which is how the template is set up. Note that there is a white box over the upper part of the right vertical axis to hide the scale above the maximum required for the NPSR curve. If you delete teh NPSHr series because you are not using it, the chart will rescale and part of it will be hidden behind the box, so you will need to delete it. The other way to handle that (and to keep a chart from rescaling in general if you want a version of it with and with out a data series showing) is to set the transparenecy of the data series you don't want to see to 100%. That will hide the series but, since it is still there, the chart will not rescale. The Impeller Data tab has instructions for a way that allows you to replace the data in this template with your own data so that the pump curve chart automatically updates to reflect the new data points.
| NPSHr |  | Manually enter the lable you want this data series to have in the yellow cells to the left
| Flow | Head
| 298.492 | 11.7647 |  | 298.492 | 11.7647
| 405.226 | 12.3529 |  | 405.226 | 12.3529
| 499.296 | 12.6 |  | 499.296 | 12.9412
| 602.412 | 12.9412 |  | 602.412 | 12.9412
| 701.91 | 14.1176 |  | 701.91 | 14.1176
| 803.216 | 16 |  | 803.216 | 17.6471
| 899.095 | 18.2 |  | 899.095 | 18.8235
| 1002.21 | 20.5882 |  | 1002.21 | 20.5882
| 1101.71 | 23.5294 |  | 1101.71 | 23.5294
| 1203.02 | 27.0588 |  | 1203.02 | 27.0588
| 1306.13 | 32.3529 |  | 1306.13 | 32.3529
| 1403.82 | 37.6471 |  | 1403.82 | 37.6471
| 1517.79 | 49.4118 |  | 1517.79 | 49.4118