## Slide 1: Pumps (and Piping)
Design, Performance and Commissioning Issues
Pipes, Valves, and Fittings
David Sellers
Senior Engineer
Facility Dynamics Engineering
April 4, 2017

## Slide 2: Pipes, Valves and Fittings; The System Part of the Phrase “Pumping System”

## Slide 3: Pipe Materials
Pipe Comes in a Variety of Materials
  HVAC
    Black Iron
    Cast Iron
    Copper
    Brass
    Plastic
    Composite/Fiberglass
  Process
    All the above
    Stainless
    Aluminum
Selection Depends On
  Service
  Exposure
  Cost

## Slide 4: Pipe Sizes
Sizes are “Nominal”
  My or may not match the outside diameter
  May or may not match the inside diameter
  “Nominal” tends to vary with material
  Multiple wall thicknesses available for each size in most materials

## Slide 5: Pipe Joints
Most materials can be joined by a number of methods
  Threads
  Solder
  Braze
  Welding
  Flanges
  Grooved joints
    Different gaskets for different applications
    Color = Intended use
  Flare joints
  Compression joints

## Slide 6: Pipe Joints
Most materials can be joined by a number of methods
  Threads
  Solder
  Braze
  Welding
  Flanges
  Grooved joints
    Different gaskets for different applications
    Color = Intended use
  Flare joints
  Compression joints
Selection determined by
  Material
  Service
  Exposure
  Cost/labor
    Example – Typical welded joint
      Cut to length
      Bevel
      Align and gap
      Tack
      Weld
        Multiple passes (c=πd)
        Chip out flux after each pass

## Slide 7: Fitting Pressure Losses
Fitting pressure losses are also related to velocity
Commonly used tables have their roots in work that has it’s origins in the late 1800’s and early 1900’s
Recent ASHRAE research demonstrates
    Some variation from classic values
    Fittings in series interact to reduce the pressure drop compared to the sum of the losses
Losses may also be expressed as equivalent feet of pipe
A common rule of thumb is to estimate the fittings losses as adding another 50% to 100% to the actual length of pipe

## Slide 8: An Interesting Thing about Elbows
One way to think of elbow resistance is to consider it as composed of:
Resistance due to interaction with the pipe wall
Resistance due to a change in direction

## Slide 9: An Interesting Thing about Elbows

## Slide 10: An Interesting Thing about Elbows

## Slide 11: An Interesting Thing about Elbows
Pressure Drop Savings = Energy Savings
Long Radius Elbow
Short Radius Elbow

## Slide 12: 8” Short Radius Elbow For a Long Radius Elbow the Centerline Radius would be 1.5 x 8” or 12”
The centerline radius is the same dimension as the pipe diameter
8”
8”

## Slide 13: Short Radius vs. Long Radius Elbows Small differences can add up to significant numbers
Number of elbows = 26
Difference in head for the circuit with long radius versus short radius elbows
  3+ ft.w.c.
  9+% difference in pump head (A.K.A. the safety factor)
  .8+ kW
  7,100 kWh annually
  $850 annually

## Slide 14: Tees are Interesting Too
Different Flow Paths = Significantly Different Pressure Drops
  Bad thing if you are trying to minimize losses
    Branching points in distribution mains
    Areas where noise might be critical
  Good thing if you are trying to balance flow between branches
    Balancing flow to cooling tower cells
    Balancing flow to coil banks

## Slide 15: Construction Impacts Loss Too
Field Fabricated Tee
Factory Forged Tee
Smooth exit to branch
Square, rough exit to branch and run

## Slide 16: Fittings and Flanges have Pressure Ratings Pressure Class and Rated Pressure May Not be the Same

## Slide 17: Crane Technical Paper 410
Available used from $49.99 and up at various used book stores
Available new for $60 at:
http://www.flowoffluids.com/publications/crane-tp-410.aspx
Notes: http://www.flowoffluids.com/publications/crane-tp-410.aspx

## Slide 18: Service Valves
Intended to isolate things for service or repair
Open or Closed
Bubble Tight shut-off may be important
Gate Valve

## Slide 19: Service Valves
Intended to isolate things for service or repair
Open or Closed
Bubble Tight shut-off may be important
Ball Valve

## Slide 20: Service Valves
Intended to isolate things for service or repair
Open or Closed
Bubble Tight shut-off may be important
Lug Style Butterfly Valve

## Slide 21: Service Valves
Intended to isolate things for service or repair
Open or Closed
Bubble Tight shut-off may be important
Plug Valve

## Slide 22: Throttling Valves
Intended to be used to modulate flow
Can be “On-Off” but can also have intermediate positions
Most throttling valves can be used as service valves …
  Ball valve
  Butterfly valve
  Plug valve
… but not all service valves can be throttling valves
Gate valve
Plug Valve

## Slide 23: Throttling Valves
Control valves are automated throttling valves
Come in a variety of styles
  Globe
  Butterfly
  Ball
  Plug
Come in a variety of actuator types
  Pneumatic
    Piston
    Diaphragm
  Electric
    Gear motor
    Linear screw
Need to be properly sized for modulating control
  Rule of thumb – smaller than the line size
Globe Type Control Valve

## Slide 24: Throttling Valves
Control valves are automated throttling valves
Come in a variety of styles
  Globe
  Butterfly
  Ball
  Plug
Come in a variety of actuator types
  Pneumatic
    Piston
    Diaphragm
  Electric
    Gear motor
    Linear screw
Need to be properly sized for modulating control
  Rule of thumb – smaller than the line size
Wafer Style Butterfly Control Valve with Double Acting Pneumatic Actuator

## Slide 25: Throttling Valves
Balancing valves are manually adjusted characterized throttling valves
  Flow coefficient calibrated to valve position
  Pressure taps allow valve pressure drop to be measured
  Pressure drop and flow coefficient can be used to determine flow rate
Bell and Gossett “Circuit Setter” type balance valve

## Slide 26: Throttling Valves
Balancing valves are manually adjusted characterized throttling valves
  Flow coefficient calibrated to valve position
  Pressure taps allow valve pressure drop to be measured
  Pressure drop and flow coefficient can be used to determine flow rate
Data logging across a “Circuit Setter” to develop a flow profile

## Slide 27: Check Valves
Intended to prevent reverse flow
Typically found on the discharge of pumps, especially parallel pumps
Swing Type Check Valve

## Slide 28: Check Valves
Intended to prevent reverse flow
Typically found on the discharge of pumps, especially parallel pumps
Wafer Type Check Valve – Outlet

## Slide 29: Check Valves
Intended to prevent reverse flow
Typically found on the discharge of pumps, especially parallel pumps
Wafer Type Check Valve – Inlet

## Slide 30: Check Valves
Intended to prevent reverse flow
Typically found on the discharge of pumps, especially parallel pumps
Directional; if you put it in backwards, it won’t do its job
Wafer Type Check Valve – Note Directional Arrow

## Slide 31: Valves with Multiple Functions
“Triple Duty” Valves
Throttling
Isolation
Check valve

## Slide 32: Different Manufacture's Have Different Performance Data

## Slide 33: Different Manufacture's Have Different Features
Entering Side
Leaving Side
The seat that is the check valve seat is also the isolation valve seat

## Slide 34: Strainers; Details Matter
What happens if you put a reducer on the outlet or flip the cover plate so the outlet is on top vs. on the bottom?

## Slide 35: Redundant Strainers Allow Uninterrupted Service

## Slide 37: Temperature Sensors and Wells
Thermometer wells
Allow sensors to be removed and replaced with out draining the system
Introduce a thermal lag between the actual temperature change and the sensed temperature change

## Slide 38: Insertion Length is Critical

## Slide 39: Wells Introduce Lags

## Slide 42: Thermal Lags A Research Experiment by the FDE NW Research Lab
Dr. Riley Sellers; PhD CTK LBNL CTPSC *
Hobbes Sellers; Post Doc Applied Chaos Theory
See 4-20 ma Current Loop Experiments – Thermal Mass Effects for details
* Doctorate of Philosophy - Canine Treat Kinetics - Lower Buchanan National Labs, Canine Treat Preservation Systems Center

## Slide 43: Pressure Testing
Typical Specifications
  Test medium (air or water)
  Test pressure
  Test duration
  Allowable variation
    Temperature compensation
  All may be driven by code requirements, especially life safety code requirements for fire protection systems

## Slide 44: Cleaning
Step 1
    Don’t let it get dirty
May be more critical for some applications than others
    High purity vs. HVAC
    Refrigeration vs. Water
  Methodology
    Flushing
    Circulation of cleaning solution
      Velocities matter
      Solution matters
      Make-up quality matters

## Slide 45: Why a Picture of a Glass of Water in a Pump (and Piping) Class

## Slide 46: What Does the Glass of Water Have to do With This Pipe?

## Slide 47: What Does the Glass of Water Have to do With This Pipe?

## Slide 48: Hangers
Need to fully support the weight of the pipe and water
  No stress on equipment flanges
  Attachment points sufficient for the imposed loads
Need to constrain and guide movement
  Normal operation
  Seismic events
  Vibration isolation
Need to be coordinated with anchors, guides, and expansion loops
Need to be coordinated with insulation
Hanger rod supports piping weight and keeps it off of the pump flanges below

## Slide 49: Hangers
Need to fully support the weight of the pipe and water
  No stress on equipment flanges
  Attachment points sufficient for the imposed loads
Need to constrain and guide movement
  Vibration isolation
  Normal operation
  Seismic events
Need to be coordinated with anchors, guides, and expansion loops
Need to be coordinated with insulation
Spring and neoprene isolators prevent vibration from reaching building structure

## Slide 50: Hangers
Need to fully support the weight of the pipe and water
  No stress on equipment flanges
  Attachment points sufficient for the imposed loads
Need to constrain and guide movement
  Vibration isolation
  Normal operation
  Seismic events
Need to be coordinated with anchors, guides, and expansion loops
Need to be coordinated with insulation
The vertical pipe risers in this 450 foot tall high rise can expand 3-4 inches or more when subjected to the temperature change associated with standing empty on a cold day vs. being filled and coming up to operating temperature

## Slide 51: Hangers
Need to fully support the weight of the pipe and water
  No stress on equipment flanges
  Attachment points sufficient for the imposed loads
Need to constrain and guide movement
  Normal operation
  Vibration isolation
  Seismic events
Need to be coordinated with anchors, guides, and expansion loops
Need to be coordinated with insulation
Angle iron reinforces hanger rod and prevents lateral movement. Similar braces prevent longitudinal movement on long runs

## Slide 52: Hangers
Need to fully support the weight of the pipe and water
  No stress on equipment flanges
  Attachment points sufficient for the imposed loads
Need to constrain and guide movement
  Normal operation
  Seismic events
  Vibration isolation
Need to be coordinated with anchors, guides, and expansion loops
Need to be coordinated with insulation

## Slide 53: Hangers
Need to fully support the weight of the pipe and water
  No stress on equipment flanges
  Attachment points sufficient for the imposed loads
Need to constrain and guide movement
  Normal operation
  Seismic events
  Vibration isolation
Need to be coordinated with anchors, guides, and expansion loops
Need to be coordinated with insulation

## Slide 54: Hangers
Need to fully support the weight of the pipe and water
  No stress on equipment flanges
  Attachment points sufficient for the imposed loads
Need to constrain and guide movement
  Normal operation
  Seismic events
  Vibration isolation
Need to be coordinated with anchors, guides, and expansion loops
Need to be coordinated with insulation

## Slide 55: Pump Vibration Isolation
Similar Considerations to Hangers
  Isolate pump from structure
  Isolate pump from piping
  Eliminate loads on pump flanges
Springs prevent day to day vibration transmission. Seismic snubbers limit movement during a seismic event

## Slide 56: Pump Vibration Isolation
Similar Considerations to Hangers
  Isolate pump from structure
  Isolate pump from piping
  Eliminate loads on pump flanges
Flex connectors and mechanical couplings prevent vibration transmission from pumps to the building structure

## Slide 57: Gauge Manifolds Less is Better
Three valves and one gauge allow:
Strainer pressure drop,
Suction pressure, and
Discharge pressure
to be read with one gauge, thereby eliminating gauge error and saving first cost

## Slide 58: Gauge Manifolds Less is Better

## Slide 59: Small Differences can Make A Big Difference

## Slide 60: Gauge Manifolds from Hell

## Slide 61: A Great Resource for Understanding the Field Side of Piping