## Design Static Calcs
AS DESIGNED LOSS CALCULATION
OA intake system loss
Loss for louvers and moving to duct intake - | 0.05 | in.w.c. (allowance)
OA Duct from 20A to 20D and plenum on 20D)
Entry loss
Duct height - | 196.8504 | inches
Duct width - | 102.3622 | inches
Duct area - | 139.9308 | sq.ft.
Duct flow rate - | 101379.9326 | cfm (AHU8, AHU10, AHU12 on 100% OA)
Duct velocity - | 724.5003 | fpm
Velocity pressure - | 0.032724 | in.w.c.
C0 for duct entry - | 0.5 | (ASHRAE Duct Fitting Data Base)
Entry loss - | 0.016362 | in.w.c.
Plenum run
Flow rate - | 101379.9326
Duct velocity - | 724.5003 | fpm
Duct length - | 73.1627 | ft.
Circular equivalent - | 153.1514 | inches (equation 25 ASHRAE 2009 Handbook, Ch 21)
Assumed friction rate - | 0.01 | in.w.c./100 ft. (large duct at 750 fpm from friction chart)
Loss - | 0.0073163 | in.w.c.
Summary
Entry loss - | 0.016362 | in.w.c.
Plenum loss - | 0.0073163 | in.w.c.
TOTAL - | 0.023678 | in.w.c.
OA Duct run - plenum to plenum
Duct height - | 47.2441 | inches
Duct width - | 102.3622 | inches
Duct area - | 33.5834 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 1389.4357 | fpm
Velocity pressure - | 0.12036 | in.w.c.
C0 for duct entry - | 0.5 | (ASHRAE Duct Fitting Data Base)
Entry loss - | 0.060179 | in.w.c.
Duct length - | 40.5623 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base)
C0 for duct exit - | 0.97 | (ASHRAE Duct Fitting Data Base)
Entry loss - | 0.11675 | in.w.c.
AHU OA Plenum
Loss - | 0.0073163 | in.w.c. (assume no more than the intake plenum)
Duct run - plenum to OA damper
Duct height - | 37.5591 | inches
Duct width - | 129.9213 | inches
Duct area - | 33.8869 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 1376.9898 | fpm
Velocity pressure - | 0.11821 | in.w.c.
C0 for duct entry - | 0.5 | (ASHRAE Duct Fitting Data Base)
Entry loss - | 0.059105 | in.w.c.
Duct length - | 3.2808 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Entry loss - | 0.060179 | in.w.c.
Plenum to plenum OA duct - | 0.01 | in.w.c.
Exit loss - | 0.11675
AHU OA plenum - | 0.0073163
AHU OA duct entry loss - | 0.059105
AHU OA duct - | 0.01
TOTAL - | 0.26335 | in.w.c.
Design Damper Pressure Drop - 100% OA
Max plus min OA damper length - | 129.9213 | inches
Max plus min OA damper width - | 37.5591 | inches
Max plus min OA damper area - | 33.8869 | sq.ft.
Flow rate - | 46661.9754 | cfm
Velocity - | 1376.9898 | fpm
Damper pressure drop - | 0.02 | in.w.c. (From T.A. Morrison curve to the right)
Plenum height - | 129.9213 | inches
Plenum width - | 37.5591 | inches
Flow rate - | 46661.9754 | cfm
Plenum velocity - | 1376.9898 | fpm
Plenum velocity pressure - | 0.11821 | in.w.c.
C0 for damper entry - | 0 | Same size as damper
C0 for damper exit - | 0.97 | Same size as damper
Entry loss - | 0 | in.w.c.
Exit loss - | 0.11466 | in.w.c.
Total damper pressure drop - | 0.13466 | in.w.c.
Prefilter pressure drop allowance
Pressure drop allowance - | 0.89928 | in.w.c. (Nothing specific called out; use shop drawing data)
Heating coil pressure drop
Pressure drop allowance - | 0.084307 | in.w.c. (Equipment schedule)
Cooling coil pressure drop
Pressure drop allowance - | 0.88723 | in.w.c. (Equipment schedule)
Final filters pressure drop allowance
Pressure drop allowance - | 1.4975 | in.w.c. (Nothing specific called out; use shop drawing data)
Sound attenuators
Pressure drop allowance - | 0.024088 | in.w.c. (Nothing specific called out; use shop drawing data)
Discharge duct loss to vertical duct down on 20C
Entry loss
Plenum wall thickness - | 4.0157 | inches
Plenum height - | 47.2441 | inches
Plenum width - | 152.0079 | inches
Plenum area - | 49.8713 | sq.ft.
Plenum flow rate - | 46661.9754 | cfm
Plenum velocity - | 935.6469 | fpm
Duct height - | 35.4331 | inches
Duct width - | 70.8661 | inches
Duct area - | 17.4375 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2675.9502 | fpm
Velocity pressure - | 0.44643 | in.w.c.
C0 for duct entry - | 0.17 | (ASHRAE Duct Fitting Data Base)
Entry loss - | 0.075893 | in.w.c.
90° mitered elbow loss (typical of 2)
Duct height - | 35.4331 | inches
Duct width - | 70.8661 | inches
Duct area - | 17.4375 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2675.9502 | fpm
Velocity pressure - | 0.44643 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Fitting loss - | 0.049107 | in.w.c. per elbow
25° mitered offset loss
Duct height - | 35.4331 | inches
Duct width - | 70.8661 | inches
Duct area - | 17.4375 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2675.9502 | fpm
Velocity pressure - | 0.44643 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow, no vanes; 25° angle; CR3-6)
Fitting loss - | 0.049107 | in.w.c. per elbow
Fitting interaction - 90° elbow to 25° mitered offset - multiplier for 1st offset (see AMCA derived chart to the right)
Centerline distance between fittings - | 2 | ft.
Multiplier - | 1.75 | (AMCA Chart)
Modified loss first 25° offset- | 0.085937 | in.w.c. per elbow
Fitting interaction - 25° elbow to 25° mitered offset - multiplier for 2nd offset (see AMCA derived chart to the right)
Centerline distance between fittings - | 8.7697 | ft.
Multiplier - | 1.05 | (AMCA Chart)
Modified loss 2nd 25° offset- | 0.051562 | in.w.c. per elbow
Fitting interaction - 25° offset to 90° mitered elbow with vanes - multiplier for 2nd elbow (see AMCA derived chart to the right)
Centerline distance between fittings - | 2 | ft.
Multiplier - | 1.75 | (AMCA Chart)
Modified loss 2nd 90° offset- | 0.085937 | in.w.c. per elbow
Straight duct
Duct height - | 35.4331 | inches
Duct width - | 70.8661 | inches
Duct area - | 17.4375 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 2675.9502 | fpm
Velocity pressure - | 0.44643 | in.w.c.
Duct length - | 18.7697 | ft.
Loss - | 0.03 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Exit loss - | 0.075893 | in.w.c.
First 90° elbow - | 0.049107 | in.w.c.
First 25° offset - | 0.085937 | in.w.c.
Straight duct - | 0.03 | in.w.c. (includes duct between fittings and duct from turn down to Level C)
Second 25° offset - | 0.051562 | in.w.c.
Second 90° elbow - | 0.085937 | in.w.c.
Total - | 0.37844 | in.w.c.
Vertical duct through the first turn on level 20A
Straight duct
Duct height - | 35.4331 | inches
Duct width - | 70.8661 | inches
Duct area - | 17.4375 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 2675.9502 | fpm
Velocity pressure - | 0.44643 | in.w.c.
Duct length - | 32.3491 | ft.
Loss - | 0.05 | in.w.c. (ASHRAE Fitting Data Base)
90° mitered elbow loss
Duct height - | 35.4331 | inches
Duct width - | 70.8661 | inches
Duct area - | 17.4375 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2675.9502 | fpm
Velocity pressure - | 0.44643 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Fitting loss - | 0.049107 | in.w.c. per elbow
Summary
Straight duct - | 0.05 | in.w.c. (includes duct between fittings and duct from turn down to Level C)
Elbow to horizontal on level 20A - | 0.049107 | in.w.c.
Total - | 0.099107 | in.w.c.
Level 20A duct up to the FSD at the shaft
Straight duct
Duct height - | 35.4331 | inches
Duct width - | 70.8661 | inches
Duct area - | 17.4375 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 2675.9502 | fpm
Velocity pressure - | 0.44643 | in.w.c.
Duct length - | 1.6404 | ft.
Loss - | 0 | in.w.c. (ASHRAE Fitting Data Base)
90° mitered variable inlet/outlet area elbow loss |  |  |  | 90° mitered elbow loss with vanes
Duct height - | 35.4331 | inches |  | Duct height - | 35.4331 | inches
Duct width - in - | 70.8661 | inches |  | Duct width - | 70.8661 | inches
Duct area - in - | 17.4375 | sq.ft. |  | Duct area - | 17.4375 | sq.ft.
Duct width - out - | 78.7402 | inches |  | Duct flow rate - | 46661.9754 | cfm (AHU8, AHU10, AHU12 on 100% OA)
Duct area - out - | 19.375 | sq.ft. |  | Duct velocity - | 2675.9502 | fpm
Duct flow rate - | 46661.9754 | cfm |  | Velocity pressure - | 0.44643 | in.w.c.
Duct velocity - in - | 2675.9502 | fpm |  | C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Velocity pressure - in - | 0.44643 | in.w.c. |  | Fitting loss - | 0.049107 | in.w.c. per elbow
Duct velocity - out - | 2408.3552 | fpm |  | 90° mitered elbow loss no vanes
Velocity pressure - out - | 0.36161 | in.w.c. |  | Duct height - | 35.4331 | inches
C0 for fitting - | 1.42 | (ASHRAE Duct Fitting Data Base; 90° variable inlet/outlet area; Idelchik 1986 Diagram 6-4) (ASHRAE does not show turning vanes; not sure how this impacts things but at least one field experience says they could make it worse not better; i.e. pressure drop improved when we took the vanes out. That experience was for a much bigger area change though) |  | Duct width - | 70.8661 | inches
Fitting loss - | 0.51348 | in.w.c. per elbow |  | Duct area - | 17.4375 | sq.ft.
Modified loss with improvement factor for vanes - | 0.052788 | (see calculations to the right)
Fitting interaction - 90° elbow to 90° elbow (See AMCA derived chart to the right) |  |  |  | Duct flow rate - | 46661.9754 | cfm (AHU8, AHU10, AHU12 on 100% OA)
Centerline distance between fittings - | 2 | ft. |  | Duct velocity - | 2675.9502 | fpm
Multiplier - | 1.78 | (AMCA Chart) |  | Velocity pressure - | 0.44643 | in.w.c.
Modified loss - | 0.093962 | in.w.c. per elbow |  | C0 for fitting - | 1.07 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Straight duct
Duct height - | 35.4331 | inches
Duct width - | 78.7402 | inches
Duct area - | 19.375 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 2408.3552 | fpm
Velocity pressure - | 0.36161 | in.w.c.
Duct length - | 4.9213 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base)
Transition - Nozzel |  |  |  | Fitting loss - | 0 | in.w.c. per elbow
Duct height - | 35.4331 | inches |  | Duct height - | 35.4331 | inches
Duct width - in - | 78.7402 | inches |  | Duct width - | 70.8661 | inches
Duct area - in - | 19.375 | sq.ft. |  | Duct area - | 17.4375 | sq.ft.
Duct height - out - | 41.3386 | inches |  | Duct height - | 35.4331 | inches
Duct width - out - | 55.1181 | inches |  | Duct flow rate - | 46661.9754 | cfm (AHU8, AHU10, AHU12 on 100% OA)
Duct area - out - | 13.5625 | sq.ft. |  | Duct velocity - | 2675.9502 | fpm
Duct flow rate - | 46661.9754 | cfm |  | Velocity pressure - | 0.44643 | in.w.c.
Duct velocity - in - | 2408.3552 | fpm |  | C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Velocity pressure - in - | 0.36161 | in.w.c. |  | Fitting loss - | 0.049107 | in.w.c. per elbow
Duct velocity - out - | 3440.5074 | fpm |  | 90° mitered elbow loss no vanes
Velocity pressure - out - | 0.73797 | in.w.c. |  | Duct height - | 35.4331 | inches
Static change (velocity pressure conversion) - | 0.37637 | in.w.c.
90° mitered elbow loss |  |  |  | Fitting loss - | 0.47768 | in.w.c. per elbow
Duct height - | 41.3386 | inches |  | Improvement factor for vanes - | 0.1028
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2949.0064 | fpm
Velocity pressure - | 0.54218 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Fitting loss - | 0.05964 | in.w.c. per elbow
Fitting interaction -Transition to 90° elbow (See AMCA derived chart to the right) |  |  |  | Duct flow rate - | 0 | cfm (AHU8, AHU10, AHU12 on 100% OA)
Centerline distance between fittings - | 4.9213 | ft. |  | Duct velocity - | #DIV/0! | fpm
Multiplier - | 1.3 | (AMCA Chart) |  | Velocity pressure - | #DIV/0! | in.w.c.
Modified loss - | 0.077532 | in.w.c. per elbow |  | C0 for fitting - | 1.07 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Straight duct
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 2949.0064 | fpm
Velocity pressure - | 0.54218 | in.w.c.
Duct length - | 3.2808 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Straight duct - | 0 | in.w.c.
First 90° elbow - | 0.093962 | in.w.c.
Straight duct - | 0.01 | in.w.c.
Transition (conversion to VP) - | 0.37637 | in.w.c.
Second 90° elbow - | 0.077532 | in.w.c.
Straight duct - | 0.01 | in.w.c.
Total - | 0.56786 | in.w.c.
Through FSD and elbow down
FSD loss
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2949.0064 | fpm
Velocity pressure - | 0.54218 | in.w.c.
C0 for fitting - | 0.18 | (ASHRAE Duct Fitting Data Base; Parallel or Opposed Blade Airfoil Damper; CR9-4)
Fitting loss - | 0.097593 | in.w.c.
90° mitered elbow loss
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2949.0064 | fpm
Velocity pressure - | 0.54218 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; single thickness vane; 1-1/2" spacing; CR3-9)
Fitting loss - | 0.05964 | in.w.c. per elbow
Summary
FSD - | 0.097593 | in.w.c.
90° elbow - | 0.05964 | in.w.c.
Total - | 0.15723 | in.w.c.
Main shaft to Level 9 take-off
Straight duct to offset
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Flow rate - | 46661.9754 | cfm
Duct velocity - | 2949.0064 | fpm
Velocity pressure - | 0.54218 | in.w.c.
Duct length - | 196.5223 | ft.
Loss - | 0.36 | in.w.c. (ASHRAE Fitting Data Base)
45° radiused elbow loss - first elbow
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2949.0064 | fpm
Velocity pressure - | 0.54218 | in.w.c.
C0 for fitting - | 0.08 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.043375 | in.w.c. per elbow
45° radiused elbow loss - second elbow
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Duct flow rate - | 46661.9754 | cfm
Duct velocity - | 2949.0064 | fpm
Velocity pressure - | 0.54218 | in.w.c.
C0 for fitting - | 0.08 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.043375 | in.w.c. per elbow
Fitting interaction - elbows (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.056387 | in.w.c. per elbow
Summary
Straight duct - | 0.36 | in.w.c.
First 45° elbow - | 0.043375 | in.w.c.
Second 45° elbow - | 0.056387 | in.w.c.
Total - | 0.45976 | in.w.c.
Level 9 to Level 8 take-off
Flow through main past branch tap
Duct height in - | 41.3386 | inches
Duct width in - | 55.1181 | inches
Duct area in - | 15.8229 | sq.ft.
Duct flow rate in - | 46661.9754 | cfm
Duct velocity in - | 2949.0064 | fpm
Velocity pressure in - | 0.54218 | in.w.c.
Duct height out - | 41.3386 | inches
Duct width out - | 55.1181 | inches
Duct area out - | 15.8229 | sq.ft.
Duct flow rate out - | 43057.7605 | cfm
Duct velocity out - | 2721.2223 | fpm
Velocity pressure out - | 0.46166 | in.w.c.
Branch height - | 35.4331 | inches
Branch width - | 16.7323 | inches
Branch area - | 4.1172 | sq.ft.
Branch flow rate - | 3604.2149 | cfm
Branch velocity - | 875.4053 | fpm
Branch velocity pressure - | 0.047776 | in.w.c.
C0 for main - | 0.05 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.023083 | in.w.c.
C0 for branch - | 1.38 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.065931 | in.w.c.
Straight duct
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Flow rate - | 43057.7605 | cfm
Duct velocity - | 2721.2223 | fpm
Velocity pressure - | 0.46166 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.03 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Junction - flow through main - | 0.023083 | in.w.c.
Straight duct - | 0.03 | in.w.c.
Total - | 0.053083 | in.w.c.
Level 8 to Level 7 take-off
Flow through main past branch tap
Duct height in - | 41.3386 | inches
Duct width in - | 55.1181 | inches
Duct area in - | 15.8229 | sq.ft.
Duct flow rate in - | 43057.7605 | cfm
Duct velocity in - | 2721.2223 | fpm
Velocity pressure in - | 0.46166 | in.w.c.
Duct height out - | 41.3386 | inches
Duct width out - | 55.1181 | inches
Duct area out - | 15.8229 | sq.ft.
Duct flow rate out - | 39398.4548 | cfm
Duct velocity out - | 2489.9566 | fpm
Velocity pressure out - | 0.38653 | in.w.c.
Branch height - | 27.5591 | inches
Branch width - | 21.6535 | inches
Branch area - | 4.1441 | sq.ft.
Branch flow rate - | 3659.3058 | cfm
Branch velocity - | 883.0146 | fpm
Branch velocity pressure - | 0.048611 | in.w.c.
C0 for main - | 0.06 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.023192 | in.w.c.
C0 for branch - | 1.51 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.073402 | in.w.c.
Straight duct
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Flow rate - | 39398.4548 | cfm
Duct velocity - | 2489.9566 | fpm
Velocity pressure - | 0.38653 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.03 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Junction - flow through main - | 0.023192 | in.w.c.
Straight duct - | 0.03 | in.w.c.
Total - | 0.053192 | in.w.c.
Level 7 to Level 6 take-off
Flow through main past branch tap
Duct height in - | 41.3386 | inches
Duct width in - | 55.1181 | inches
Duct area in - | 15.8229 | sq.ft.
Duct flow rate in - | 39398.4548 | cfm
Duct velocity in - | 2489.9566 | fpm
Velocity pressure in - | 0.38653 | in.w.c.
Duct height out - | 41.3386 | inches
Duct width out - | 55.1181 | inches
Duct area out - | 15.8229 | sq.ft.
Duct flow rate out - | 35775.17 | cfm
Duct velocity out - | 2260.9674 | fpm
Velocity pressure out - | 0.3187 | in.w.c.
Branch height - | 27.5591 | inches
Branch width - | 19.685 | inches
Branch area - | 3.7674 | sq.ft.
Branch flow rate - | 3623.2848 | cfm
Branch velocity - | 961.7548 | fpm
Branch velocity pressure - | 0.057667 | in.w.c.
C0 for main - | 0.06 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.019122 | in.w.c.
C0 for branch - | 1.08 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.06228 | in.w.c.
Straight duct
Duct height - | 41.3386 | inches
Duct width - | 55.1181 | inches
Duct area - | 15.8229 | sq.ft.
Flow rate - | 35775.17 | cfm
Duct velocity - | 2260.9674 | fpm
Velocity pressure - | 0.3187 | in.w.c.
Duct length - | 13.4514 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Junction - flow through main - | 0.019122 | in.w.c.
Straight duct - | 0.01 | in.w.c.
Total - | 0.029122 | in.w.c.
Level 6 to Level 4 take-off (Level 5 supply is taken off at level 6 then drops to level 5 outside the chase)
Flow through main past branch tap
Duct height in - | 41.3386 | inches
Duct width in - | 55.1181 | inches
Duct area in - | 15.8229 | sq.ft.
Duct flow rate in - | 35775.17 | cfm
Duct velocity in - | 2260.9674 | fpm
Velocity pressure in - | 0.3187 | in.w.c.
Duct height out - | 27.5591 | inches
Duct width out - | 55.1181 | inches
Duct area out - | 10.5486 | sq.ft.
Duct flow rate out - | 25089.6581 | cfm
Duct velocity out - | 2378.475 | fpm
Velocity pressure out - | 0.35269 | in.w.c.
Branch height - | 55.1181 | inches
Branch width - | 17.7165 | inches
Branch area - | 6.7813 | sq.ft.
Branch flow rate - | 10685.5119 | cfm
Branch velocity - | 1575.7405 | fpm
Branch velocity pressure - | 0.1548 | in.w.c.
C0 for main - | 0.04 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.014108 | in.w.c.
C0 for branch - | 1.62 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.25077 | in.w.c.
45° radiused elbow loss - first elbow
Duct height - | 55.1181 | inches
Duct width - | 27.5591 | inches
Duct area - | 10.5486 | sq.ft.
Duct flow rate - | 25089.6581 | cfm
Duct velocity - | 2378.475 | fpm
Velocity pressure - | 0.35269 | in.w.c.
C0 for fitting - | 0.08 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.028215 | in.w.c. per elbow
45° radiused elbow loss - second elbow
Duct height - | 55.1181 | inches
Duct width - | 27.5591 | inches
Duct area - | 10.5486 | sq.ft.
Duct flow rate - | 25089.6581 | cfm
Duct velocity - | 2378.475 | fpm
Velocity pressure - | 0.35269 | in.w.c.
C0 for fitting - | 0.08 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.028215 | in.w.c. per elbow
Fitting interaction - elbows (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.03668 | in.w.c. per elbow
Straight duct
Duct height - | 27.5591 | inches
Duct width - | 55.1181 | inches
Duct area - | 10.5486 | sq.ft.
Flow rate - | 25089.6581 | cfm
Duct velocity - | 2378.475 | fpm
Velocity pressure - | 0.35269 | in.w.c.
Duct length - | 20.1772 | ft.
Loss - | 0.03 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Junction - flow through main - | 0.014108 | in.w.c.
First 45° elbow - | 0.028215
Second 45° elbow - | 0.03668
Straight duct - | 0.03 | in.w.c.
Total - | 0.109 | in.w.c.
Level 4 to Level 3 take-off
Flow through main past branch tap
Duct height in - | 27.5591 | inches
Duct width in - | 55.1181 | inches
Duct area in - | 10.5486 | sq.ft.
Duct flow rate in - | 25089.6581 | cfm
Duct velocity in - | 2378.475 | fpm
Velocity pressure in - | 0.35269 | in.w.c.
Duct height out - | 27.5591 | inches
Duct width out - | 47.2441 | inches
Duct area out - | 9.0417 | sq.ft.
Duct flow rate out - | 22837.2887 | cfm
Duct velocity out - | 2525.778 | fpm
Velocity pressure out - | 0.39773 | in.w.c.
Branch height - | 27.5591 | inches
Branch width - | 19.685 | inches
Branch area - | 3.7674 | sq.ft.
Branch flow rate - | 2252.3694 | cfm
Branch velocity - | 597.8628 | fpm
Branch velocity pressure - | 0.022284 | in.w.c.
C0 for main - | 0.03 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.011932 | in.w.c.
C0 for branch - | 3.04 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.067744 | in.w.c.
Straight duct
Duct height - | 27.5591 | inches
Duct width - | 47.2441 | inches
Duct area - | 9.0417 | sq.ft.
Flow rate - | 22837.2887 | cfm
Duct velocity - | 2525.778 | fpm
Velocity pressure - | 0.39773 | in.w.c.
Duct length - | 13.4514 | ft.
Loss - | 0.02 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Junction - flow through main - | 0.011932 | in.w.c.
Straight duct - | 0.02 | in.w.c.
Total - | 0.031932 | in.w.c.
Level 3 to Level 2 take-off
Flow through main past branch tap
Duct height in - | 27.5591 | inches
Duct width in - | 47.2441 | inches
Duct area in - | 9.0417 | sq.ft.
Duct flow rate in - | 22837.2887 | cfm
Duct velocity in - | 2525.778 | fpm
Velocity pressure in - | 0.39773 | in.w.c.
Duct height out - | 27.5591 | inches
Duct width out - | 47.2441 | inches
Duct area out - | 9.0417 | sq.ft.
Duct flow rate out - | 16192.481 | cfm
Duct velocity out - | 1790.8699 | fpm
Velocity pressure out - | 0.19995 | in.w.c.
Branch height - | 27.5591 | inches
Branch width - | 19.685 | inches
Branch area - | 3.7674 | sq.ft.
Branch flow rate - | 6644.8077 | cfm
Branch velocity - | 1763.7795 | fpm
Branch velocity pressure - | 0.19395 | in.w.c.
C0 for main - | 0.23 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.045989 | in.w.c.
C0 for branch - | 1.67 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.32389 | in.w.c.
45° radiused elbow loss - first elbow
Duct height - | 47.2441 | inches
Duct width - | 27.5591 | inches
Duct area - | 9.0417 | sq.ft.
Duct flow rate - | 16192.481 | cfm
Duct velocity - | 1790.8699 | fpm
Velocity pressure - | 0.19995 | in.w.c.
C0 for fitting - | 0.09 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.017996 | in.w.c. per elbow
45° radiused elbow loss - second elbow
Duct height - | 47.2441 | inches
Duct width - | 27.5591 | inches
Duct area - | 9.0417 | sq.ft.
Duct flow rate - | 16192.481 | cfm
Duct velocity - | 1790.8699 | fpm
Velocity pressure - | 0.19995 | in.w.c.
C0 for fitting - | 0.09 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.017996 | in.w.c. per elbow
Fitting interaction - elbows (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.023394 | in.w.c. per elbow
Transition - Nozzel
Duct height - | 47 | inches
Duct width - in - | 27.5591 | inches
Duct area - in - | 8.995 | sq.ft.
Duct height - out - | 29.5276 | inches
Duct width - out - | 29.5276 | inches
Duct area - out - | 6.0547 | sq.ft.
Transition length - | 24 | inches
Duct flow rate - | 16192.481 | cfm
Duct velocity - in - | 1800.1708 | fpm
Velocity pressure - in - | 0.20203 | in.w.c.
Duct velocity - out - | 2674.3657 | fpm
Velocity pressure - out - | 0.4459 | in.w.c.
C0 for fitting - | 0.04 | (ASHRAE Duct Fitting Data Base; pyramidl transition, supply; SR4-2)
Fitting loss - | 0.0080813 | in.w.c. per elbow
45° radiused elbow loss - first elbow
Duct height - | 29.5276 | inches
Duct width - | 29.5276 | inches
Duct area - | 6.0547 | sq.ft.
Duct flow rate - | 16192.481 | cfm
Duct velocity - | 2674.3657 | fpm
Velocity pressure - | 0.4459 | in.w.c.
C0 for fitting - | 0.1 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.04459 | in.w.c. per elbow
45° radiused elbow loss - second elbow
Duct height - | 29.5276 | inches
Duct width - | 29.5276 | inches
Duct area - | 6.0547 | sq.ft.
Duct flow rate - | 16192.481 | cfm
Duct velocity - | 2674.3657 | fpm
Velocity pressure - | 0.4459 | in.w.c.
C0 for fitting - | 0.1 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.04459 | in.w.c. per elbow
Fitting interaction -elbows (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.057967 | in.w.c. per elbow
Assume fittings take up floor to floor height with no additional straight duct
Summary
Junction - flow through main - | 0.045989 | in.w.c.
First offset, first 45° elbow - | 0.017996 | in.w.c.
First offset - second 45° elbow - | 0.023394 | in.w.c.
Transition - | 0.0080813 | in.w.c.
Second offset, first 45° elbow - | 0.04459 | in.w.c.
Second offset - second 45° elbow - | 0.057967 | in.w.c.
Total - | 0.19802 | in.w.c.
Level 2 to Level 1 take-off
Flow through main past branch tap
Duct height in - | 29.5276 | inches
Duct width in - | 29.5276 | inches
Duct area in - | 6.0547 | sq.ft.
Duct flow rate in - | 16192.481 | cfm
Duct velocity in - | 2674.3657 | fpm
Velocity pressure in - | 0.4459 | in.w.c.
Duct height out - | 25.5906 | inches
Duct width out - | 21.6535 | inches
Duct area out - | 3.8481 | sq.ft.
Duct flow rate out - | 7261.4018 | cfm
Duct velocity out - | 1887.0106 | fpm
Velocity pressure out - | 0.222 | in.w.c.
Branch height - | 29.5276 | inches
Branch width - | 23.622 | inches
Branch area - | 4.8438 | sq.ft.
Branch flow rate - | 8931.0792 | cfm
Branch velocity - | 1843.832 | fpm
Branch velocity pressure - | 0.21195 | in.w.c.
C0 for main - | 0.28 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.062159 | in.w.c.
C0 for branch - | 1.58 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.33488 | in.w.c.
Straight duct
Duct height - | 25.5906 | inches
Duct width - | 21.6535 | inches
Duct area - | 3.8481 | sq.ft.
Flow rate - | 7261.4018 | cfm
Duct velocity - | 1887.0106 | fpm
Velocity pressure - | 0.222 | in.w.c.
Duct length - | 13.4514 | ft.
Loss - | 0.02 | in.w.c. (ASHRAE Fitting Data Base)
FSD loss
Duct height - | 25.5906 | inches
Duct width - | 21.6535 | inches
Duct area - | 3.8481 | sq.ft.
Duct flow rate - | 7261.4018 | cfm
Duct velocity - | 1887.0106 | fpm
Velocity pressure - | 0.222 | in.w.c.
C0 for fitting - | 0.18 | (ASHRAE Duct Fitting Data Base; Parallel or Opposed Blade Airfoil Damper; CR9-4)
Fitting loss - | 0.039959 | in.w.c.
90° mitered elbow loss
Duct height - | 25.5906 | inches
Duct width - | 21.6535 | inches
Duct area - | 3.8481 | sq.ft.
Duct flow rate - | 7261.4018 | cfm
Duct velocity - | 1887.0106 | fpm
Velocity pressure - | 0.222 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.024419 | in.w.c. per elbow
Fitting interaction - elbows to FSD (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.031745 | in.w.c. per elbow
Summary
Junction - flow through main - | 0.062159 | in.w.c.
Straight duct - | 0.02 | in.w.c.
FSD loss - | 0.039959 | in.w.c.
Mitered elbow loss - | 0.031745 | in.w.c.
Total - | 0.15386 | in.w.c.
Level 1 to Basement
Flow through main past branch tap
Duct height in - | 25.5906 | inches
Duct width in - | 21.6535 | inches
Duct area in - | 3.8481 | sq.ft.
Duct flow rate in - | 7261.4018 | cfm
Duct velocity in - | 1887.0106 | fpm
Velocity pressure in - | 0.222 | in.w.c.
Duct height out - | 25.5906 | inches
Duct width out - | 19.685 | inches
Duct area out - | 3.4983 | sq.ft.
Duct flow rate out - | 6371.4722 | cfm
Duct velocity out - | 1821.3204 | fpm
Velocity pressure out - | 0.20681 | in.w.c.
Branch height - | 9.8425 | inches
Branch width - | 11.811 | inches
Branch area - | 0.80729 | sq.ft.
Branch flow rate - | 889.9296 | cfm
Branch velocity - | 1102.3622 | fpm
Branch velocity pressure - | 0.075761 | in.w.c.
C0 for main - | 0.05 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.01034 | in.w.c.
C0 for branch - | 0.46 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.03485 | in.w.c.
90° mitered elbow loss
Duct height - | 19.685 | inches
Duct width - | 25.5906 | inches
Duct area - | 3.4983 | sq.ft.
Duct flow rate - | 6371.4722 | cfm
Duct velocity - | 1821.3204 | fpm
Velocity pressure - | 0.20681 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.022749 | in.w.c. per elbow
Fitting interaction - elbows to branch (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.029574 | in.w.c. per elbow
90° mitered elbow loss
Duct height - | 25.5906 | inches
Duct width - | 19.685 | inches
Duct area - | 3.4983 | sq.ft.
Duct flow rate - | 6371.4722 | cfm
Duct velocity - | 1821.3204 | fpm
Velocity pressure - | 0.20681 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.022749 | in.w.c. per elbow
Fitting interaction - elbows to elbow (See AMCA derived chart to the right)
Centerline distance between fittings - | 2 | ft.
Multiplier - | 1.75 | (AMCA Chart)
Modified loss - | 0.039811 | in.w.c. per elbow
45° radiused elbow loss - first elbow
Duct height - | 25.5906 | inches
Duct width - | 19.685 | inches
Duct area - | 3.4983 | sq.ft.
Duct flow rate - | 6371.4722 | cfm
Duct velocity - | 1821.3204 | fpm
Velocity pressure - | 0.20681 | in.w.c.
C0 for fitting - | 0.09 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.018613 | in.w.c. per elbow
Fitting interaction -elbows (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.024197 | in.w.c. per elbow
45° radiused elbow loss - second elbow
Duct height - | 25.5906 | inches
Duct width - | 19.685 | inches
Duct area - | 3.4983 | sq.ft.
Duct flow rate - | 6371.4722 | cfm
Duct velocity - | 1821.3204 | fpm
Velocity pressure - | 0.20681 | in.w.c.
C0 for fitting - | 0.09 | (ASHRAE Duct Fitting Data Base; smooth radius with out vanes; CR3-1)
Fitting loss - | 0.018613 | in.w.c. per elbow
Fitting interaction -elbows (See AMCA derived chart to the right)
Centerline distance between fittings - | 4.9213 | ft.
Multiplier - | 1.3 | (AMCA Chart)
Modified loss - | 0.024197 | in.w.c. per elbow
Straight duct
Duct height - | 25.5906 | inches
Duct width - | 19.685 | inches
Duct area - | 3.4983 | sq.ft.
Flow rate - | 6371.4722 | cfm
Duct velocity - | 1821.3204 | fpm
Velocity pressure - | 0.20681 | in.w.c.
Duct length - | 6.7421 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base)
FSD loss
Duct height - | 25.5906 | inches
Duct width - | 19.685 | inches
Duct area - | 3.4983 | sq.ft.
Duct flow rate - | 6371.4722 | cfm
Duct velocity - | 1821.3204 | fpm
Velocity pressure - | 0.20681 | in.w.c.
C0 for fitting - | 0.18 | (ASHRAE Duct Fitting Data Base; Parallel or Opposed Blade Airfoil Damper; CR9-4)
Fitting loss - | 0.037225 | in.w.c.
Summary
Junction - flow through main - | 0.01034 | in.w.c.
Mitered elbow loss - | 0.029574
Mitered elbow loss - | 0.039811
First 45° elbow - | 0.024197
Second 45° elbow - | 0.024197
Straight duct - | 0.01 | in.w.c.
FSD loss - | 0.037225 | in.w.c.
Total - | 0.17534 | in.w.c.
Floor Penetration to TU6-8-B (May serves TU 4, 5, 6, 7, 8, 9, and 10)
90° mitered elbow loss
Duct height - | 25.5906 | inches
Duct width - | 17.7165 | inches
Duct area - | 3.1484 | sq.ft.
Duct flow rate - | 4400.9138 | cfm
Duct velocity - | 1397.806 | fpm
Velocity pressure - | 0.12181 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.013399 | in.w.c. per elbow
Fitting interaction - elbows to FSD (See AMCA derived chart to the right)
Centerline distance between fittings - | 2 | ft.
Multiplier - | 1.75 | (AMCA Chart)
Modified loss - | 0.023449 | in.w.c. per elbow
Straight duct
Duct height - | 25.5906 | inches
Duct width - | 17.7165 | inches
Duct area - | 3.1484 | sq.ft.
Flow rate - | 4400.9138 | cfm
Duct velocity - | 1397.806 | fpm
Velocity pressure - | 0.12181 | in.w.c.
Duct length - | 13.1234 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base)
Flow through main past branch tap for TU-4
Duct height in - | 17.7165 | inches
Duct width in - | 25.5906 | inches
Duct area in - | 3.1484 | sq.ft.
Duct flow rate in - | 4400.9138 | cfm
Duct velocity in - | 1397.806 | fpm
Velocity pressure in - | 0.12181 | in.w.c.
Duct height out - | 9.8425 | inches
Duct width out - | 23.622 | inches
Duct area out - | 1.6146 | sq.ft.
Duct flow rate out - | 3506.7464 | cfm
Duct velocity out - | 2171.916 | fpm
Velocity pressure out - | 0.29409 | in.w.c.
Branch height - | 9.8425 | inches
Branch width - | 14.5669 | inches
Branch area - | 0.99566 | sq.ft.
Branch flow rate - | 894.1674 | cfm
Branch velocity - | 898.0634 | fpm
Branch velocity pressure - | 0.050282 | in.w.c.
C0 for main - | 0 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0 | in.w.c.
C0 for branch - | 1.91 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 0.096038 | in.w.c.
90° mitered elbow loss
Duct height - | 9.8425 | inches
Duct width - | 23.622 | inches
Duct area - | 1.6146 | sq.ft.
Duct flow rate - | 3506.7464 | cfm
Duct velocity - | 2171.916 | fpm
Velocity pressure - | 0.29409 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.03235 | in.w.c. per elbow
Flow through main past branch tap for TU-8, 9 and 10
Duct height in - | 9.8425 | inches
Duct width in - | 23.622 | inches
Duct area in - | 1.6146 | sq.ft.
Duct flow rate in - | 3506.7464 | cfm
Duct velocity in - | 2171.916 | fpm
Velocity pressure in - | 0.29409 | in.w.c.
Duct height out - | 9.8425 | inches
Duct width out - | 23.622 | inches
Duct area out - | 1.6146 | sq.ft.
Duct flow rate out - | 1574.3278 | cfm
Duct velocity out - | 975.0656 | fpm
Velocity pressure out - | 0.059274 | in.w.c.
Branch height - | 11.811 | inches
Branch width - | 16.7323 | inches
Branch area - | 1.3724 | sq.ft.
Branch flow rate - | 1932.4186 | cfm
Branch velocity - | 1408.0593 | fpm
Branch velocity pressure - | 0.12361 | in.w.c.
C0 for main - | 0.17 | (ASHRAE Duct Fitting Data Base; SR5-13)
Main loss - | 0.010077 | in.w.c.
C0 for branch - | 11.41 | (ASHRAE Duct Fitting Data Base; SR5-13)
Branch loss - | 1.4103 | in.w.c.
Fitting interaction - branch to elbow (See AMCA derived chart to the right)
Centerline distance between fittings - | 2 | ft.
Multiplier - | 1.75 | (AMCA Chart)
Modified loss - Main - | 0.017634 | in.w.c. per elbow
Modified loss - Branch - | 2.4681 | in.w.c. per elbow
Straight duct
Duct height - | 23.622 | inches
Duct width - | 9.8425 | inches
Duct area - | 1.6146 | sq.ft.
Flow rate - | 1574.3278 | cfm
Duct velocity - | 975.0656 | fpm
Velocity pressure - | 0.059274 | in.w.c.
Duct length - | 26.2467 | ft.
Loss - | 0.02 | in.w.c. (ASHRAE Fitting Data Base)
Transition - Diffusser
Duct height - | 23.622 | inches
Duct width - in - | 9.8425 | inches
Duct area - in - | 1.6146 | sq.ft.
Duct height - out - | 15.748 | inches
Duct width - out - | 13.7795 | inches
Duct area - out - | 1.5069 | sq.ft.
Transition length - | 24 | inches
Duct flow rate - | 1574.3278 | cfm
Duct velocity - in - | 975.0656 | fpm
Velocity pressure - in - | 0.059274 | in.w.c.
Duct velocity - out - | 1044.7132 | fpm
Velocity pressure - out - | 0.068044 | in.w.c.
C0 for main - | 0.01 | (ASHRAE Duct Fitting Data Base; SR4-2)
Main loss - | 0.00059274 | in.w.c.
Straight duct
Duct height - | 15.748 | inches
Duct width - | 13.7795 | inches
Duct area - | 1.5069 | sq.ft.
Flow rate - | 1574.3278 | cfm
Duct velocity - | 1044.7132 | fpm
Velocity pressure - | 0.068044 | in.w.c.
Duct length - | 26.2467 | ft.
Loss - | 0.02 | in.w.c. (ASHRAE Fitting Data Base)
90° mitered elbow loss
Duct height - | 15.748 | inches
Duct width - | 13.7795 | inches
Duct area - | 1.5069 | sq.ft.
Duct flow rate - | 1574.3278 | cfm
Duct velocity - | 1044.7132 | fpm
Velocity pressure - | 0.068044 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.0074848 | in.w.c. per elbow
Straight duct
Duct height - | 15.748 | inches
Duct width - | 13.7795 | inches
Duct area - | 1.5069 | sq.ft.
Flow rate - | 1574.3278 | cfm
Duct velocity - | 1044.7132 | fpm
Velocity pressure - | 0.068044 | in.w.c.
Duct length - | 32.8084 | ft.
Loss - | 0.04 | in.w.c. (ASHRAE Fitting Data Base)
90° mitered elbow loss
Duct height - | 9.8425 | inches
Duct width - | 11.811 | inches
Duct area - | 0.80729 | sq.ft.
Duct flow rate - | 886.3278 | cfm
Duct velocity - | 1097.9007 | fpm
Velocity pressure - | 0.075149 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.0082663 | in.w.c. per elbow
Transition - rectangular to round
Duct height - | 9.8425 | inches
Duct width - in - | 11.811 | inches
Duct area - in - | 0.80729 | sq.ft.
Duct diameter - out - | 11.811 | inches
Duct area - out - | 0.76086 | sq.ft.
Transition length - | 12 | inches
Duct flow rate - | 886.3278 | cfm
Duct velocity - in - | 1097.9007 | fpm
Velocity pressure - in - | 0.075149 | in.w.c.
Duct velocity - out - | 1164.9088 | fpm
Velocity pressure - out - | 0.084602 | in.w.c.
Fitting loss - | 0 | in.w.c. per (velocity conversion)
Straight duct (round)
Duct diameter - | 11.811 | inches
Duct area - | 0.76086 | sq.ft.
Flow rate - | 886.3278 | cfm
Duct velocity - | 1164.9088 | fpm
Velocity pressure - | 0.084602 | in.w.c.
Duct length - | 6.5617 | ft.
Loss - | 0 | in.w.c. (ASHRAE Fitting Data Base)
Flow through branch for TU-6 (round conical tee)
Duct diameter - in - | 11.811 | inches
Duct area - in - | 0.76086 | sq.ft.
Duct flow rate in - | 886.3278 | cfm
Duct velocity in - | 1164.9088 | fpm
Velocity pressure in - | 0.084602 | in.w.c.
Duct diameter - out - | 5.9055 | inches
Duct area - out - | 0.19021 | sq.ft.
Duct flow rate out - | 352.3701 | cfm
Duct velocity out - | 1852.4929 | fpm
Velocity pressure out - | 0.21395 | in.w.c.
Duct diameter - branch - | 9.8425 | inches
Duct area - branch - | 0.52837 | sq.ft.
Branch flow rate - | 533.9578 | cfm
Branch velocity - | 1010.5712 | fpm
Branch velocity pressure - | 0.063669 | in.w.c.
C0 for main - | 0.15 | (ASHRAE Duct Fitting Data Base; SR5-10)
Main loss - | 0.032092 | in.w.c.
C0 for branch - | 0.88 | (ASHRAE Duct Fitting Data Base; SR5-10)
Branch loss - | 0.056029 | in.w.c.
Straight duct (round)
Duct diameter - | 9.8425 | inches
Duct area - | 0.52837 | sq.ft.
Flow rate - | 533.9578 | cfm
Duct velocity - | 1010.5712 | fpm
Velocity pressure - | 0.063669 | in.w.c.
Duct length - | 16.4042 | ft.
Loss - | 0.02 | in.w.c. (ASHRAE Fitting Data Base)
Summary
Mitered elbow loss - | 0.023449 | in.w.c.
Straight duct - | 0.01 | in.w.c.
Flow through main past TU-4 branch - | 0 | in.w.c.
Mitered elbow loss - | 0.03235 | in.w.c.
Flow through main past branch for TU-8, 9, and 10 - | 0.017634 | in.w.c.
Straight duct | 0.02 | in.w.c.
Trasition - | 0.00059274 | in.w.c.
Straight duct - | 0.02 | in.w.c.
Mitered elbow loss - | 0.0074848 | in.w.c.
Straight duct - | 0.04 | in.w.c.
Mitered elbow loss - | 0.0082663 | in.w.c.
Rectangular to round transition - | 0 | in.w.c.
Straight duct - | 0 | in.w.c.
Flow through branch - | 0.056029 | in.w.c.
Straight duct - | 0.02 | in.w.c.
Total - | 0.25581 | in.w.c.
TU-6 Operating allowance
Maximum operating loss - | 0.20073 | in.w.c. (from equipment schedule)
TU-6 Low pressure duct system allowance
Maximum operating loss - | 0.1 | in.w.c. (from equipment schedule)
Level 5 Return Path (assumes 50% of the air flow from all but the public spaces on the floor goes up each of two ducts)
See analysis to the right for an assessment of the approximate total flow rate per floor
Straight duct from L5 ceiling plenum to L6 transfer duct
Duct height - | 25.5906 | inches
Duct width - | 78.7402 | inches
Duct area - | 13.9931 | sq.ft.
Flow rate - | 9774.438 | cfm
Duct velocity - | 698.5192 | fpm
Velocity pressure - | 0.030419 | in.w.c.
Duct length - | 13.4514 | ft.
Loss - | 0.004 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Flow into main from branch down to the 5th floor ceiling plenum
Duct height in - | 78.7402 | inches | Approximate floor area assessment above L9 for approximate flow assessment
Duct width in - | 25.5906 | inches |  | Main area E-W | 137.7953 | ft.
Duct area in - | 13.9931 | sq.ft. |  | Main area N-S | 177.1654 | ft.
Duct flow rate in - | 9774.438 | cfm |  | Main area sq.ft. | 24412.5488 | sq.ft.
Duct velocity in - | 698.5192 | fpm |  | West bump-out - E-W | 36.0892 | ft.
Velocity pressure in - | 0.030419 | in.w.c. |  | West bump-out - N-S | 52.4934 | ft.
Duct height out - | 78.7402 | inches |  | West bump out sq.ft. | 1894.4482 | sq.ft.
Duct width out - | 25.5906 | inches |  | South bump-out - E-W | 84.4816 | ft.
Duct area out - | 13.9931 | sq.ft. |  | South bump-out - N-S | 14.7638 | ft.
Duct flow rate out - | 19548.8759 | cfm |  | South bump-out sq.ft. | 1247.2681 | sq.ft.
Duct velocity out - | 1397.0385 | fpm |  | Total sq.ft. | 27554.2652 | sq.ft.
Velocity pressure out - | 0.12168 | in.w.c. | Based on the flow analysis in:
Branch height - | 78.7402 | inches |  | Building Airflow Tabulation and MOA Calcs.xls
Branch width - | 25.5906 | inches |  | : the building is served at about 1 cfm per square foot
Branch area - | 13.9931 | sq.ft. |  | Approximate air flow per floor - | 27554.2652 | cfm
Branch flow rate - | 9774.438 | cfm |  | MOA % (from analysis above) - | 20% | will assume this much goes out the exhaust system
Branch velocity - | 698.5192 | fpm |  | Approximate return air flow per floor - | 22043.4121 | cfm
Branch velocity pressure - | 0.030419 | in.w.c. |  | Approximate Lobby area - | 2494.5362 | sq.ft. (about twice the South bump-out number)
C0 for main - | 2.23 | (ASHRAE Duct Fitting Data Base; ER5-3) |  | Approximate lobby air flow - | 2494.5362 | cfm
Main loss - | 0.067835 | in.w.c. |  | Approximate return air up shafts 2 and 4 - | 19548.8759 | cfm (assumes lobby air flow goes up shafts 1 and 5)
C0 for branch - | 0.66 | (ASHRAE Duct Fitting Data Base; ER5-3)
Branch loss - | 0.020077 | in.w.c.
Transition - Diffusser
Duct height - | 25.5906 | inches
Duct width - in - | 78.7402 | inches
Duct area - in - | 13.9931 | sq.ft.
Duct height - out - | 43.3071 | inches
Duct width - out - | 78.7402 | inches
Duct area - out - | 23.6806 | sq.ft.
Transition length - | 24 | inches
Duct flow rate - | 19548.8759 | cfm
Duct velocity - in - | 1397.0385 | fpm
Velocity pressure - in - | 0.12168 | in.w.c.
Duct velocity - out - | 825.5227 | fpm
Velocity pressure - out - | 0.042487 | in.w.c.
C0 for main - | 0.24 | (ASHRAE Duct Fitting Data Base; SR4-2)
Main loss - | 0.029203 | in.w.c.
15° mitered offset loss
Duct height - | 25.5906 | inches
Duct width - | 78.7402 | inches
Duct area - | 13.9931 | sq.ft.
Duct flow rate - | 19548.8759 | cfm
Duct velocity - | 1397.0385 | fpm
Velocity pressure - | 0.12168 | in.w.c.
C0 for fitting - | 0.08 | (ASHRAE Duct Fitting Data Base; mitered elbow, no vanes; 25° angle; CR3-6)
Fitting loss - | 0.0097342 | in.w.c. per elbow
Straight duct between offsets
Duct height - | 25.5906 | inches
Duct width - | 78.7402 | inches
Duct area - | 13.9931 | sq.ft.
Flow rate - | 19548.8759 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 1397.0385 | fpm
Velocity pressure - | 0.12168 | in.w.c.
Duct length - | 9.8425 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
15° mitered offset loss
Duct height - | 25.5906 | inches
Duct width - | 78.7402 | inches
Duct area - | 13.9931 | sq.ft.
Duct flow rate - | 19548.8759 | cfm
Duct velocity - | 1397.0385 | fpm
Velocity pressure - | 0.12168 | in.w.c.
C0 for fitting - | 0.08 | (ASHRAE Duct Fitting Data Base; mitered elbow, no vanes; 25° angle; CR3-6)
Fitting loss - | 0.0097342 | in.w.c. per elbow
Fitting interaction - offset to offset (See AMCA derived chart to the right)
Centerline distance between fittings - | 9.8425 | ft.
Multiplier - | 1 | (AMCA Chart)
Modified loss - Main - | 0.0097342 | in.w.c. per elbow
Straight duct (assumes no loss due to the branch tap near the outlet of this section due to low velocity and small flows)
Duct height - | 25.5906 | inches
Duct width - | 78.7402 | inches
Duct area - | 13.9931 | sq.ft.
Flow rate - | 19548.8759 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 1397.0385 | fpm
Velocity pressure - | 0.12168 | in.w.c.
Duct length - | 11.811 | ft.
Loss - | 0.01 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Transition - Diffusser
Duct height - | 25.5906 | inches
Duct width - in - | 78.7402 | inches
Duct area - in - | 13.9931 | sq.ft.
Duct height - out - | 68.8976 | inches
Duct width - out - | 78.7402 | inches
Duct area - out - | 37.6737 | sq.ft.
Transition length - | 18 | inches
Duct flow rate - | 19548.8759 | cfm
Duct velocity - in - | 1397.0385 | fpm
Velocity pressure - in - | 0.12168 | in.w.c.
Duct velocity - out - | 518.9 | fpm
Velocity pressure - out - | 0.016787 | in.w.c.
C0 for fitting - | 0.48 | (ASHRAE Duct Fitting Data Base; pyramidl transition, supply; SR4-2)
Fitting loss - | 0.058405 | in.w.c. per elbow
FSD loss
Duct height - | 68.8976 | inches
Duct width - | 78.7402 | inches
Duct area - | 37.6737 | sq.ft.
Duct flow rate - | 19548.8759 | cfm
Duct velocity - | 518.9 | fpm
Velocity pressure - | 0.016787 | in.w.c.
C0 for fitting - | 0.18 | (ASHRAE Duct Fitting Data Base; Parallel or Opposed Blade Airfoil Damper; CR9-4)
Fitting loss - | 0.0030216 | in.w.c.
Fitting interaction - transition to FSD (See AMCA derived chart to the right)
Centerline distance between fittings - | 2 | ft.
Multiplier - | 1.75 | (AMCA Chart)
Modified loss - Main - | 0.0052878 | in.w.c. per elbow
Summary
Straight duct from L5 ceiling plenum to L6 transfer duct - | 0.004 | in.w.c.
Branch tap - | 0.020077 | in.w.c.
Transition - | 0.029203 | in.w.c.
Mitered offset - | 0.0097342 | in.w.c.
Straight duct - | 0.01 | in.w.c.
Mitered offset - | 0.0097342 | in.w.c.
Straight duct - | 0.01 | in.w.c.
Transition - | 0.058405 | in.w.c.
FSD - | 0.0052878 | in.w.c.
Total - | 0.15644 | in.w.c.
Mechancial Shaft 2 Through the FSD at the top of the shaft
Treats the shaft as a duct with the shaft dimensions and assumes half the flow for the each floor is carried by it
Straight duct from L6 to L7
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 19548.8759 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 157.9261 | fpm
Velocity pressure - | 0.0015549 | in.w.c.
Duct length - | 13.4514 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L7 to L8
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 29323.3139 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 236.8891 | fpm
Velocity pressure - | 0.0034985 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L8 to L9
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 39097.7518 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 315.8522 | fpm
Velocity pressure - | 0.0062196 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L9 to L10
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 48872.1898 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 394.8152 | fpm
Velocity pressure - | 0.0097181 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L10 to L11
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 58646.6277 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 473.7783 | fpm
Velocity pressure - | 0.013994 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L11 to L12
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 68421.0657 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 552.7413 | fpm
Velocity pressure - | 0.019048 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L12 to L13
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 78195.5036 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 631.7043 | fpm
Velocity pressure - | 0.024878 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L13 to L14
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 87969.9416 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 710.6674 | fpm
Velocity pressure - | 0.031487 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L14 to L15
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 97744.3795 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 789.6304 | fpm
Velocity pressure - | 0.038873 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L15 to L16
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 107518.8175 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 868.5935 | fpm
Velocity pressure - | 0.047036 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L16 to L17
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 117293.2554 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 947.5565 | fpm
Velocity pressure - | 0.055976 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L17 to L18
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 127067.6934 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 1026.5196 | fpm
Velocity pressure - | 0.065695 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L18 to L19
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 136842.1313 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 1105.4826 | fpm
Velocity pressure - | 0.07619 | in.w.c.
Duct length - | 20.3412 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Straight duct from L19 to L20A
Duct height - | 226.378 | inches
Duct width - | 78.7402 | inches
Duct area - | 123.785 | sq.ft.
Flow rate - | 146616.5693 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 1184.4457 | fpm
Velocity pressure - | 0.087463 | in.w.c.
Duct length - | 13.4514 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
FSD loss
Duct height - | 78.7402 | inches
Duct width - | 334.6457 | inches
Duct area - | 182.9865 | sq.ft.
Duct flow rate - | 146616.5693 | cfm
Duct velocity - | 801.2426 | fpm
Velocity pressure - | 0.040024 | in.w.c.
C0 for fitting - | 0.18 | (ASHRAE Duct Fitting Data Base; Parallel or Opposed Blade Airfoil Damper; CR9-4)
Fitting loss - | 0.0072044 | in.w.c.
Summary
L6 - L7 | 0.001 | in.w.c.
L7 - L8 | 0.001 | in.w.c.
L8 - L9 | 0.001 | in.w.c.
L9 - L10 | 0.001 | in.w.c.
L10 - L11 | 0.001 | in.w.c.
L11 - L12 | 0.001 | in.w.c.
L12 - L13 | 0.001 | in.w.c.
L13 - L14 | 0.001 | in.w.c.
L14 - L15 | 0.001 | in.w.c.
L15 - L16 | 0.001 | in.w.c.
L16 -L17 | 0.001 | in.w.c.
L17 - L18 | 0.001 | in.w.c.
L18 - L19 | 0.001 | in.w.c.
FDS - | 0.0072044 | in.w.c.
Total - | 0.020204 | in.w.c.
Mechancial Shaft 2 Through the FSD at the top of the shaft
Entry Loss
Duct height - | 47.2441 | in.
Duct width - | 78.7402 | in.
Duct area - | 25.8334 | sq.ft.
Extension past wall - | 0.1 | in.
Duct flow rate - | 31261.9556 | cfm
Duct velocity - | 1210.1378 | fpm
Velocity pressure - | 0.091299 | in.w.c.
C0 for fitting - | 0.56 | (ASHRAE Duct Fitting Data Base; Duct mounted in wall; ER1-1)
Fitting loss - | 0.051127 | in.w.c.
Straight duct from L19 to L20A
Duct height - | 47.2441 | inches
Duct width - | 78.7402 | inches
Duct area - | 25.8334 | sq.ft.
Flow rate - | 31261.9556 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 1210.1378 | fpm
Velocity pressure - | 0.091299 | in.w.c.
Duct length - | 18.8484 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Obstruction
Duct height - | 79 | in.
Duct width - | 47 | in.
Duct area - | 25.7847 | sq.ft.
Obstruction width/diameter - | 12 | in.
Obstruction distance from duct center line - | 12 | in
Duct flow rate - | 31261.9556 | cfm
Duct velocity - | 1212.4217 | fpm
Velocity pressure - | 0.091644 | in.w.c.
C0 for fitting - | 0.21 | (ASHRAE Duct Fitting Data Base; Parallel or Opposed Blade Airfoil Damper; ER1-1)
Fitting loss - | 0.019245 | in.w.c.
90° mitered elbow loss
Duct height - | 79 | inches
Duct width - | 47 | inches
Duct area - | 25.7847 | sq.ft.
Duct flow rate - | 31261.9556 | cfm
Duct velocity - | 1212.4217 | fpm
Velocity pressure - | 0.091644 | in.w.c.
C0 for fitting - | 0.11 | (ASHRAE Duct Fitting Data Base; mitered elbow 1-1/2" vane spacing; CR3-9)
Fitting loss - | 0.010081 | in.w.c. per elbow
Straight duct
Duct height - | 79 | inches
Duct width - | 47 | inches
Duct area - | 25.7847 | sq.ft.
Flow rate - | 31261.9556 | cfm (ignors air going out toilet exhaust; i.e. assumes all supply air goes back the return)
Duct velocity - | 1212.4217 | fpm
Velocity pressure - | 0.091644 | in.w.c.
Duct length - | 5.0853 | ft.
Loss - | 0.001 | in.w.c. (ASHRAE Fitting Data Base says 0 to two decimal places)
Exit Loss
Duct height - | 79 | in.
Duct width - | 47 | in.
Duct area - | 25.7847 | sq.ft.
Exit angle - | 90 | °
Duct flow rate - | 31261.9556 | cfm
Duct velocity - | 1212.4217 | fpm
Velocity pressure - | 0.091644 | in.w.c.
C0 for fitting - | 1 | (ASHRAE Duct Fitting Data Base; Discharge flush with wall; SR2-2)
Fitting loss - | 0.091644 | in.w.c.
Summary
Entry loss - | 0.051127 | in.w.c.
Straight duct - | 0.001 | in.w.c.
Obstruction - | 0.019245 | in.w.c.
Elbow - | 0.010081 | in.w.c.
Straight duct - | 0.001 | in.w.c.
Exit loss - | 0.091644 | in.w.c.
Total - | 0.1741 | in.w.c.
Relief damper
Entry Loss
Duct height - | 129.9213 | in.
Duct width - | 27.5591 | in.
Duct area - | 24.8646 | sq.ft.
Extension past wall - | 0.1 | in.
Duct flow rate - | 31261.9556 | cfm
Duct velocity - | 1257.286 | fpm
Velocity pressure - | 0.098551 | in.w.c.
C0 for fitting - | 0.57 | (ASHRAE Duct Fitting Data Base; Duct mounted in wall; ER1-1)
Fitting loss - | 0.056174 | in.w.c.
Damper loss
Duct height - | 129.9213 | inches
Duct width - | 27.5591 | inches
Duct area - | 24.8646 | sq.ft.
Duct flow rate - | 31261.9556 | cfm
Duct velocity - | 1257.286 | fpm
Velocity pressure - | 0.098551 | in.w.c.
C0 for fitting - | 0.18 | (ASHRAE Duct Fitting Data Base; Parallel or Opposed Blade Airfoil Damper; CR9-4)
Fitting loss - | 0.017739 | in.w.c.
Exit Loss
Duct height - | 129.9213 | in.
Duct width - | 27.5591 | in.
Duct area - | 24.8646 | sq.ft.
Exit angle - | 90 | °
Duct flow rate - | 31261.9556 | cfm
Duct velocity - | 1257.286 | fpm
Velocity pressure - | 0.098551 | in.w.c.
C0 for fitting - | 1 | (ASHRAE Duct Fitting Data Base; Discharge flush with wall; SR2-2)
Fitting loss - | 0.098551 | in.w.c.
Summary
Entry loss - | 0.056174 | in.w.c.
Damper - | 0.017739 | in.w.c.
Exit loss - | 0.098551 | in.w.c.
Total - | 0.17247 | in.w.c.
Relief Louver and Damper
Barometric Damper
Allowance - | 0.1 | in.w.c.
Louver
Allowance - | 0.1 | in.w.c.
Summary
Barometric Damper - | 0.1 | in.w.c.
Louver - | 0.1 | in.w.c.
Total - | 0.2 | in.w.c.