## Sheet1
Equipment | Full Load Tons | Full Load kW | Full Load kW/Ton | % of Full Load kW |  | Variation with Load | Nature of variation | David Illustration of How to Use
Chiller 1 | 550 | 286 | 0.52 | 79.32% | 38.11% | yes | TBD |  | Estimated preheat load - (from previous class - see slide 7) - | 83504 | Btu/hr
Chiller 2 | 550 | 309.2 | 0.56218 |  | 41.21% | yes | TBD |  | Btu/hr per ton - | 12000 | Btu/hr/ton
Evaporator Pump 1 |  | 10.1456 |  | 20.68% | 1.352% | no |  |  | Preheat false load as tons - | 6.9587 | tons
Evaporator Pump 2 |  | 10.1456 |  |  | 1.352% | no |  |  | Estimated kW per ton (full load) - | 0.68215 | kW/ton
Distribution Pump 1 |  | 25.8862 |  |  | 3.45% | yes | affinity law |  | Plant kW associated with the false load - | 4.7469 | kW
Distribution Pump 2 |  | 25.8862 |  |  | 3.45% | yes | affinity law |  | Electric rate - | 0.16 | $/kWH
Condenser Pump 1 |  | 30.3622 |  |  | 4.046% | no |  |  | Unnecessary cost per hour - | 0.7595 | per hour
Condenser Pump 2 |  | 30.3622 |  |  | 4.046% | no |  |  | Estimated annual hours the condition might exist - | 5000
Cooling Tower 1 |  | 11.19 |  |  | 1.491% | yes | TBD |  | Potential annual penalty at the chiller plant - | 3797.4988 | per year
Cooling Tower 2 |  | 11.19 |  |  | 1.491% | yes | TBD
Total | 1100 | 750.368 | 0.68215