## Design Point System Curve
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
This spreadsheet calculates a system curve based on a known flow and head determined by a pump test or by a design metric. You can add it as a tab in a digitized pump or fan curve spreadsheet and then use the results to plot the system curve on the pump curve, plot lines that intersect at the design point or other points on the system curve and plot a "dot" at the design point and other points.
Assumptions
1 | Known flow = | 1100 | gpm (design parameter)
2 | Head or static at known flow = | 90 | ft.w.c. (design parameter)
3 | Fixed static or open system lift = | 0 | Note 1
4 | System Curve Exponent = | 2 | Note 2
5 | Efficiency = | 72.25% | (From the curve)
6 | Bhp = | 34.6021 | Bhp (calculated)
7 | Largest impeller = | 7 | inches
8 | Closest known impeller size = | 6 | inches (enter the known impeller size closes to the design operating point)
9 | Smallest impeller = | 5.5 | inches
10 | DP set point = | 80 | ft.w.c. (at the remote load at discharge header)
11 | Published curve speed = | 3550 | rpm (from the published curve)
Note 1 - For closed systems that control for a fixed pressure, enter it here in ft.w.c., otherwise use 0.
Note 2 - The typical value for this is 2, but ASHRAE research indicates that generally, 1.85 - 1.89 may be more appropriate for systems were there are some portions with out fully developed turbulent flow.
System Curve Points
| Condition | Flow | Static
| 140% of known flow | 1540 | 176.4
| 120% of known flow | 1320 | 129.6
| Known | 1100 | 90
| 80% of known flow | 880 | 57.6
| 60% of known flow | 660 | 32.4
| 40% of known flow | 440 | 14.4
| 30% of known flow | 330 | 8.1
| 20% of known flow | 220 | 3.6
| 18% of known flow | 198 | 2.916
| 16% of known flow | 176 | 2.304
| 14% of known flow | 154 | 1.764
| 12% of known flow | 132 | 1.296
| 10% of known flow | 110 | 0.9
| 8% of known flow | 88 | 0.576
| 6% of known flow | 66 | 0.324
| 4% of known flow | 26.4 | 0.05184
| 2% of known flow | 13.2 | 0.01296
| No Flow | 0 | 0
Design Conditions
This table can be used to create lines that cross at the design point on a pump curve chart.
| Head Line | 1800 | 90 | Set the flow values in the yellow cells to match the range of the X axis
|  | 0 | 90
| Flow Line | 1100 | 200 | Set the head values in the orange cells to match the range of the Y axis
|  | 1100 | 0
Point on a Known Impeller Line
This table can be used to create lines that cross at a known point on a pump curve chart.
| Head Line | 1800 | 73.5 | Set the head value in the orange cell to the head value where the design system curve crosses the known impeller size line
|  | 0 | 73.5
| Flow Line | 1330 | 200 | Set the flow value in the yellow cell to the flow value where the design system curve crosses the known impeller size line
|  | 1330 | 0
You can also use these tables to create a "dot" at the design point or known operating point by plotting the numbers in the blue cells as a series, which gives you a line with only one point. When you do that, you probably will not see the "dot" on your chart because the markers for the line are turned off or are too small. But if you select the series by using the "Current Selection" area of "Format" tab associated with the "Chart Tools" you can format the marker to be larger, and have fill and color characteristics, just like you would if you wanted all of the markers on a line to show up.