## Slide 1
As Installed
Typical AHU
Typical AHU
SD
TDV
Chiller 2 VFD & HG
SD
TDV
Chiller 1 No VFD
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
550 tons (Typical)
EWT – 57°F
LWT – 45°F
550 tons (Typical)
EWT – 45°F
LWT – 57°F